## Allocation Summary
WPD Method | [5 empty] | Index
Catergory | % by network tier
| LV | LV/HV | HV | EHV | Unallocated
Opex and transmission exit charges | 47.06% | 7.86% | 18.88% | 26.2% | N/A
Depriciation | 13.6% | 5.975% | 27.2% | 53.23% | N/A
Return | 13.6% | 5.975% | 27.2% | 53.23% | N/A
Weighted Average | 24.83% | 6.607% | 24.41% | 44.16% | N/A
Weighted Average (after incentive and pencsion deficit costs removed and weighted by units flowing) | 29.36% | 7.814% | 19.41% | 34.3% | 9.124%
Direct cost % | 60.08% | 89.55% | 91.82% | 73.81% | N/A
| LV | HV/LV | HV | EHV/HV | EHV | 132kV/EHV | 132kV
Weighted by units flowing | 29.36% | 7.814% | 19.41% | 4.836% | 3.38% | 2.869% | 23.21%
Direct cost % | 60.08% | 89.55% | 91.82% | 73.81% | 73.81% | 73.81% | 73.81%
| LV | HV | 33kV | 132kV
Network length split | 9.9% | 46% | 100% | 100%
Options | DCP071
TRUE
Discount matrix
| Discounts |  |  |  | Network levels provided or bypassed by the DNO |  |  |  | Network levels bypassed by the DNO
Boundary category | LV demand end user | LV Sub demand or LV generation end user | HV demand or LV Sub generation end user | HV generation end user | EHV/HV | EHV | 132kV/EHV | 132kV | EHV/HV | EHV | 132kV/EHV | 132kV
Boundary 0000 | 90.88% | 87.08% | 85.48% | 78.99% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boundary 132kV | 73.74% | 62.83% | 58.21% | 39.53% | 0 | 0 | 0 | 0.73815 | 0 | 0 | 0 | 0
Boundary 132kV/EHV | 64.8% | 50.17% | 43.97% | 18.92% | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
Boundary EHV | 62.3% | 46.63% | 40% | 13.18% | 0 | 0.73815 | 1 | 1 | 0 | 0 | 0 | 0
Boundary HVplus | 56.58% | 38.53% | 30.89% | 0% | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Input data reconciliation check
Compare results to current CDCM Method M with DCP096
| No discount | LDNO LV: LV user | LDNO HV: LV user | LDNO HV: LV sub user | LDNO HV: HV user
LDNO discount using data in this model |  | 27.61% | 48.38% | 26.93% | 17.84%

## WPD - Final Allocation
Step 1. Format price control allowed revenue data
Index
|  | I) DPCR3 type presentation | [9 empty] | ii) DPCR4 type presentation
|  |  |  | 2005/06 | 2006/07 |  | 2007/08 | 2008/09 | 2009/10 | [5 empty] | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
[12 empty] | Opening asset value |  |  | 947.9 | 989.2 | 1030.2 | 1064.8 | 1093.2
|  | Allowed revenue |  | 241.2388 | 243.41 |  | 246.0636 | 249.1997 | 251.8533 |  |  | Total capex |  |  | 117.8 | 117.5 | 117 | 116.6 | 116.4
[12 empty] | Depreciation |  |  | -76.5 | -76.5 | -82.4 | -88.2 | -94.1
|  | Opex (incl pensions after 57.7% capitalized) |  | 80.699 | 83.2413 |  | 83.7413 | 82.4413 | 81.7413 |  |  | Closing asset value |  |  | 989.2 | 1030.2 | 1064.8 | 1093.2 | 1115.6
|  | Quality Reward | [9 empty] | Present value of opening/closing RAV |  |  | 947.9 |  | 0 |  | 851.7
|  | DPCR3 costs |  | 1.5 | [7 empty] | 5 year movement in closing RAV |  |  |  | 0 |  |  | 96.2
|  | Total Opex |  | 82.199 | 83.2413 |  | 83.7413 | 82.4413 | 81.7413
[12 empty] | Operating costs (excl pensions) |  |  | 75.2 | 77.7 | 78.2 | 76.9 | 76.2
|  | Capital elements | [9 empty] | Capex (excl pensions) |  |  | 110.3 | 109.9 | 109.4 | 109 | 108.8
|  | Depreciation |  | 76.5 | 76.5 |  | 82.4 | 88.2 | 94.1 |  |  | Pensions |  |  | 13 | 13.1 | 13.1 | 13.1 | 13.1
|  | Tax allowance |  | 27.2 | 26.3 |  | 26.4 | 26.8 | 26.8 |  |  | Tax allowance |  |  | 27.2 | 26.3 | 26.4 | 26.8 | 26.8
|  | Capital incentive |  | -0.8 | 0.6 |  | -0.6 | -0.6 | -0.2 |  |  | Capex incentive |  |  | -0.8 | 0.6 | -0.6 | -0.6 | -0.2
|  | Sliding scale |  | 1.4 | 1.4 |  | 1.5 | 1.5 | 1.6 |  |  | Sliding scale addn income |  |  | 1.4 | 1.4 | 1.5 | 1.5 | 1.6
|  | Return |  | 54.7398 | 55.3687 |  | 52.6223 | 50.8584 | 47.812 |  |  | Quality reward/Opex incentive & Other Adjustments
|  | Total capital |  | 159.0398 | 160.1687 |  | 162.3223 | 166.7584 | 170.112 |  |  | DPCR3 costs |  |  | 1.5 | - | - | - | -
|  | Total capital ex depreciation |  | 82.5398 | 83.6687 |  | 79.9223 | 78.5584 | 76.012 |  |  | Total allowed items |  |  | 227.7 | 229 | 228.1 | 226.8 | 226.3
[12 empty] | PV of allowed items |  |  | 221.6 | 211.2 | 199.3 | 187.7 | 177.5
|  | Allocation of allowed revenue to:- | [9 empty] | 5 year movement in closing RAV | [6 empty] | 96.2
[12 empty] | TOTAL PV OVER 5 YEARS | [6 empty] | 1093.5
|  | Opex |  | 82.199 | 83.2413 |  | 83.7413 | 82.4413 | 81.7413
|  | Depreciation |  | 76.5 | 76.5 |  | 82.4 | 88.2 | 94.1 |  |  | 5.545% |  |  | 0.94746 | 0.89769 | 0.85052 | 0.80584 | 0.7635
|  | Return |  | 54.7398 | 55.3687 |  | 52.6223 | 50.8584 | 47.812 | [5 empty] | 1 | 0.94746 | 0.89769 | 0.85052 | 0.80584
[15 empty] | 0.97338 | 0.92224 | 0.87379 | 0.82788 | 0.78439
[12 empty] | Revenue index |  |  | 1 | 1.009 | 1.02 | 1.033 | 1.044
[12 empty] | Discounted revenue index |  |  | 0.97338 | 0.93054 | 0.89126 | 0.8552 | 0.8189
[12 empty] | Price control revenue |  |  | 241.2388 | 243.41 | 246.0636 | 249.1997 | 251.8533
[12 empty] | Excluded services revenue |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
[12 empty] | Total revenue |  |  | 244.7388 | 246.91 | 249.5636 | 252.6997 | 255.3533
[12 empty] | PV of total revenue |  |  | 238.2232 | 227.71 | 218.0655 | 209.2054 | 200.2959
[12 empty] | TOTAL PV OVER 5 YEARS | [6 empty] | 1093.5
[12 empty] | PV of excluded service revenue |  | 15.3359 | 3.4068 | 3.2278 | 3.0583 | 2.8976 | 2.7454
Step 2. Allocate price control revenues to network tiers
|  | Hence DPCR4 revenue made up of | Total DPCR4 | Basis of allocation | % used | [5 empty] | £m
[5 empty] | EHV |  | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV
|  | Return | 400.7012 | Net Capex | 53.23% |  | 27.2% | 5.975% | 13.6% |  | 213.2797 | 108.9991 | 23.9417 | 54.4807
|  | Depreciation | 417.7 | Net Capex | 53.23% |  | 27.2% | 5.975% | 13.6% |  | 222.3276 | 113.6231 | 24.9574 | 56.7919
|  | Operating costs | 413.3642 | Overall Opex split | 26.2% |  | 18.88% | 7.86% | 47.06% |  | 108.2995 | 78.0419 | 32.4886 | 194.5343
|  | Total | 1231.7654 | [7 empty] | 543.9068 | 300.6641 | 81.3877 | 305.8068
[11 empty] | 44.16% | 24.41% | 6.607% | 24.83%
[5 empty] | 5 |  | 4 | 3 | 2
NET CAPEX SPLIT FROM "CALC -NET CAPEX" SHEET
OVERALL OPEX SPLIT FROM "CALC WPD OPEX ALLOCATYION" SHEET
Step 3. Remove incentive reveune and pension deficit payment from allocations
2007/08 allowed revenue source from page "summary allowed revenue"
| Base revenue |  |  |  |  | 276.4269 | 94.33% | [10 empty] | £m
| Allowed pass through items |  |  |  |  | -4.5983 | -1.569%
| Incentive revenue |  |  |  |  | 26.4079 | 9.011% |  |  | Total allowed income | [7 empty] | 293.0499 | From 2007/08 revenue summary
| Under/over revoery |  |  |  |  | -11.8565 | -4.046%
| Excluded |  |  |  |  | 6.67 | 2.276% |  |  | Less incentive revenue ? |  |  |  |  | y |  |  | -26.4079 | From 2007/08 revenue summary
| Total |  |  |  |  | 293.0499 | 100% |  |  | Less Pension deficit payment ? |  |  |  |  | n |  |  | 0 | From SEPD method A spreadsheet
[10 empty] | Less transmission exit charges ? |  |  |  |  | y |  |  | -4.4
| Input pension deficit payment |  |  |  |  | 0 | From SEPD method A spreadsheet
[10 empty] | Total revenue to share | [7 empty] | 262.242
|  |  |  | Step 3.a. Split out pension deficit and incentive payments | [7 empty] | Step 2.b. Divide cost by units flowing - effectively adjust the cost because of electricity lost as it flows thorugh the network meaning that there is more cost in the lower tiers
HENCE SPLIT OF TARIFFS
|  |  |  | £m | [7 empty] | p/kWh
|  |  |  | Total |  | EHV | HV | HV/LV | LV | Not to be split |  | EHV | HV | HV/LV | LV | Not to be split |  | Total
| Income |  |  | 293.0499 |  | 115.7974 | 64.0112 | 17.3274 | 65.1061 | 30.8079 |  | 0.39434 | 0.22315 | 0.089844 | 0.33758 | 0.10491
| All LV Tariffs | [10 empty] | 0.39434 | 0.22315 | 0.089844 | 0.33758 | 0.10491 |  | 1.1498
HV Tariffs
EHV Tariffs
| All LV Tariffs | [10 empty] | 34.3% | 19.41% | 7.814% | 29.36% | 9.124% |  | 100%
HV Tariffs
EHV Tariffs

## Calc - WPD Opex Allocation
Index
|  |  | Step 1 - extract total activity costs from cost report | [5 empty] | Step 2. Idnetify costs inlcuded in price control revenues to be allocated by MEAV | [5 empty] | Step 3. Allocate costs not directly atttibutable to network teirs to network tiers using MEAV |  |  |  |  | Step 4. Sum directly atttibuted and allocated costs | [5 empty] | Step 5. Divide cost by units flowing - effectively adjust the cost because of electricity lost as it flows thorugh the network meaning that there is more cost in the lower tiers |  |  |  | Step 6. Adjust costs so that they are aligned with the definition of opex in the allowed price control revenues
|  |  |  | Costs extracted from RRP Tables |  |  |  |  | Cost drivers - lookup from "Calc-Drivers" | [5 empty] | Allocation of "Unallocated" costs by cost driver to network tiers |  |  |  |  | Sum of allocated and "unallocted" costs | [5 empty] | Sum of allocated and "unallocted" costs expressed per unit throughput (p/kWh) |  |  |  | Propportion of costs allocated to Opex and Capex |  |  |  | Operating costs = sum of allocated and unallocated multplied by 1 minus capitalised proprtion |  |  |  |  | Opex only on p/kWh throughput
|  |  | Total activity cost - from RRP 1.3 | Costs allocated to netwrok tiers in RRP - from 2.2 amd 2.3 |  |  |  | Unallocated costs = Total - costs allocated to network tiers | Insert name of cost driver | Proportion of cost allocated to each network tier | [19 empty] | % Cost capitalised (from DCPR settlement - same for all DNOs) | Capex | Opex |  | EHV | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV
|  |  |  | EHV | HV | HV/LV | LV |  |  | EHV | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV |  |  | EHV | HV | HV/LV | LV
Cash typical costs (excluding disallowed related party margins) | Direct activities - From RRP 2.2 Detailed Cost Matrix | Load related new connections & reinforcement (net of contributions) | 46.4595 | 30.9257 | 36.86 | 0 | -21.4 | 0.073791 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.028592 | 0.0081397 | 0.0025092 | 0.03455 |  | 30.9543 | 36.8681 | 0.0025092 | -21.3654 |  |  | 0.10541 | 0.12853 | 1.3011e-05 | -0.11078 | 100% | 46.4595 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | Non-load new & replacement assets (net of contributions) | 62.5317 | 16.6927 | 16.9741 | 10.15 | 14.4502 | 4.2647 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 1.6525 | 0.47042 | 0.14502 | 1.9968 |  | 18.3452 | 17.4445 | 10.295 | 16.447 |  |  | 0.062473 | 0.060815 | 0.053381 | 0.08528 | 100% | 62.5317 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | Non-operational capex | 2.3969 | 0 | 0 | 0 | 0 | 2.3969 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.92875 | 0.2644 | 0.081506 | 1.1223 |  | 0.92875 | 0.2644 | 0.081506 | 1.1223 |  |  | 0.0031628 | 0.00092174 | 0.00042262 | 0.0058192 | 23.5% | 0.56328 | 1.8337 |  | 0.71049 | 0.20227 | 0.062352 | 0.85855 |  | 0.0024195 | 0.00070513 | 0.0003233 | 0.0044517
|  | Faults | 26.5144 | 1.5816 | 6.2658 | 0.5505 | 15.9459 | 2.1707 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.84108 | 0.23944 | 0.073812 | 1.0163 |  | 2.4226 | 6.5053 | 0.62431 | 16.9622 |  |  | 0.0082501 | 0.022679 | 0.0032371 | 0.087951 | 23.5% | 6.2309 | 20.2835 |  | 1.8533 | 4.9765 | 0.4776 | 12.9761 |  | 0.0063114 | 0.017349 | 0.0024764 | 0.067282
|  | Inspections, & Maintenance | 11.6067 | 4.3025 | 0.50909 | 4.2769 | 1.2192 | 1.299 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.50333 | 0.14329 | 0.044171 | 0.60821 |  | 4.8058 | 0.65238 | 4.3211 | 1.8274 |  |  | 0.016366 | 0.0022743 | 0.022405 | 0.0094752 | 23.5% | 2.7276 | 8.8791 |  | 3.6765 | 0.49907 | 3.3056 | 1.398 |  | 0.01252 | 0.0017398 | 0.01714 | 0.0072485
|  | Tree Cutting | 3.1209 | 0.81105 | 3.84 | 0 | 2.6698 | -4.2 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | -1.6274 | -0.46329 | -0.14282 | -1.9665 |  | -0.81634 | 3.3767 | -0.14282 | 0.70332 |  |  | -0.00278 | 0.011772 | -0.00074053 | 0.0036468 | 23.5% | 0.7334 | 2.3875 |  | -0.6245 | 2.5832 | -0.10926 | 0.53804 |  | -0.0021267 | 0.0090054 | -0.0005665 | 0.0027898
| Indirect activities - From RRP 2.2 Detailed Cost Matrix | Network Policy | 0.63889 | 0 | 0 | 0 | 0 | 0.63889 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.24755 | 0.070474 | 0.021725 | 0.29914 |  | 0.24755 | 0.070474 | 0.021725 | 0.29914 |  |  | 0.00084303 | 0.00024569 | 0.00011265 | 0.0015511 | 52.57% | 0.33587 | 0.30303 |  | 0.11741 | 0.033426 | 0.010304 | 0.14188 |  | 0.00039985 | 0.00011653 | 5.3428e-05 | 0.00073567
|  | Network Design & Engineering | 5.1306 | 0 | 0 | 0 | 0 | 5.1306 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 1.988 | 0.56594 | 0.17446 | 2.4022 |  | 1.988 | 0.56594 | 0.17446 | 2.4022 |  |  | 0.0067699 | 0.001973 | 0.0009046 | 0.012456 | 52.57% | 2.6971 | 2.4334 |  | 0.94289 | 0.26842 | 0.082747 | 1.1394 |  | 0.0032109 | 0.00093577 | 0.00042905 | 0.0059078
|  | Project Management | 2.2167 | 0 | 0 | 0 | 0 | 2.2167 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.85892 | 0.24452 | 0.075378 | 1.0379 |  | 0.85892 | 0.24452 | 0.075378 | 1.0379 |  |  | 0.002925 | 0.00085244 | 0.00039084 | 0.0053816 | 52.57% | 1.1653 | 1.0514 |  | 0.40739 | 0.11598 | 0.035752 | 0.49228 |  | 0.0013873 | 0.00040431 | 0.00018538 | 0.0025525
|  | Engineering Mgt & Clerical Support | 16.9396 | 0 | 0 | 0 | 0 | 16.9396 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 6.5636 | 1.8686 | 0.57602 | 7.9314 |  | 6.5636 | 1.8686 | 0.57602 | 7.9314 |  |  | 0.022352 | 0.0065141 | 0.0029867 | 0.041125 | 52.57% | 8.9052 | 8.0345 |  | 3.1131 | 0.88626 | 0.27321 | 3.7619 |  | 0.010602 | 0.0030896 | 0.0014166 | 0.019506
|  | Control Centre | 4.43 | 0 | 0 | 0 | 0 | 4.43 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 1.7165 | 0.48866 | 0.15064 | 2.0742 |  | 1.7165 | 0.48866 | 0.15064 | 2.0742 |  |  | 0.0058455 | 0.0017036 | 0.00078108 | 0.010755 | 52.57% | 2.3289 | 2.1012 |  | 0.81414 | 0.23177 | 0.071448 | 0.98379 |  | 0.0027725 | 0.000808 | 0.00037047 | 0.0051011
|  | System Mapping - Cartographical | 1.5095 | 0 | 0 | 0 | 0 | 1.5095 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.58488 | 0.1665 | 0.051328 | 0.70676 |  | 0.58488 | 0.1665 | 0.051328 | 0.70676 |  |  | 0.0019918 | 0.00058046 | 0.00026614 | 0.0036646 | 52.57% | 0.79353 | 0.71594 |  | 0.27741 | 0.078973 | 0.024345 | 0.33521 |  | 0.00094469 | 0.00027531 | 0.00012623 | 0.0017381
|  | Customer Call Centre | 1.3239 | 0 | 0 | 0 | 0 | 1.3239 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.51299 | 0.14604 | 0.04502 | 0.61989 |  | 0.51299 | 0.14604 | 0.04502 | 0.61989 |  |  | 0.001747 | 0.00050912 | 0.00023343 | 0.0032142 | 52.57% | 0.696 | 0.62794 |  | 0.24331 | 0.069267 | 0.021353 | 0.29401 |  | 0.00082858 | 0.00024148 | 0.00011072 | 0.0015245
|  | Stores | 1.5623 | 0 | 0 | 0 | 0 | 1.5623 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.60536 | 0.17234 | 0.053126 | 0.73151 |  | 0.60536 | 0.17234 | 0.053126 | 0.73151 |  |  | 0.0020615 | 0.00060079 | 0.00027546 | 0.0037929 | 52.57% | 0.82131 | 0.74101 |  | 0.28712 | 0.081739 | 0.025198 | 0.34695 |  | 0.00097777 | 0.00028496 | 0.00013065 | 0.001799
|  | Vehicles & Transport | 6.151 | 0 | 0 | 0 | 0 | 6.151 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 2.3834 | 0.6785 | 0.20916 | 2.88 |  | 2.3834 | 0.6785 | 0.20916 | 2.88 |  |  | 0.0081164 | 0.0023654 | 0.0010845 | 0.014933 | 52.57% | 3.2336 | 2.9174 |  | 1.1304 | 0.32181 | 0.099205 | 1.366 |  | 0.0038496 | 0.0011219 | 0.00051439 | 0.0070828
|  | IT & Telecoms | 10.2401 | 0 | 0 | 0 | 0 | 10.2401 | Do not allocate | [20 empty] | 52.57% | 5.3832 | 4.8569
|  | Property Mgt | 4.5836 | 0 | 0 | 0 | 0 | 4.5836 | Do not allocate | [20 empty] | 52.57% | 2.4096 | 2.174
|  | HR & Non-operational Training | 1.4398 | 0 | 0 | 0 | 0 | 1.4398 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.55788 | 0.15882 | 0.048959 | 0.67414 |  | 0.55788 | 0.15882 | 0.048959 | 0.67414 |  |  | 0.0018998 | 0.00055367 | 0.00025386 | 0.0034955 | 52.57% | 0.7569 | 0.6829 |  | 0.2646 | 0.075328 | 0.023221 | 0.31974 |  | 0.00090109 | 0.00026261 | 0.00012041 | 0.0016579
|  | Health & Safety & Operational Training | 2.0706 | 0 | 0 | 0 | 0 | 2.0706 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.80232 | 0.22841 | 0.070411 | 0.9695 |  | 0.80232 | 0.22841 | 0.070411 | 0.9695 |  |  | 0.0027322 | 0.00079626 | 0.00036509 | 0.005027 | 52.57% | 1.0885 | 0.9821 |  | 0.38054 | 0.10833 | 0.033396 | 0.45984 |  | 0.0012959 | 0.00037767 | 0.00017316 | 0.0023843
|  | Finance & Regulation | 7.5445 | 0 | 0 | 0 | 0 | 7.5445 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 2.9233 | 0.83221 | 0.25655 | 3.5324 |  | 2.9233 | 0.83221 | 0.25655 | 3.5324 |  |  | 0.009955 | 0.0029012 | 0.0013302 | 0.018316 | 52.57% | 3.9661 | 3.5784 |  | 1.3865 | 0.39472 | 0.12168 | 1.6754 |  | 0.0047217 | 0.0013761 | 0.00063092 | 0.0086873
|  | CEO etc | 1.6451 | 0 | 0 | 0 | 0 | 1.6451 | MEAV | 38.75% | 11.03% | 3.4% | 46.82% |  | 0.63744 | 0.18147 | 0.055941 | 0.77027 |  | 0.63744 | 0.18147 | 0.055941 | 0.77027 |  |  | 0.0021708 | 0.00063263 | 0.00029006 | 0.0039939 | 52.57% | 0.86484 | 0.78028 |  | 0.30234 | 0.08607 | 0.026533 | 0.36534 |  | 0.0010296 | 0.00030006 | 0.00013758 | 0.0018943
Other Costs from full activitty cost allocation |  | Atypical cash costs | 1.3215 | 0 | 0 | 0 | 0 | 1.3215 | Do not allocate | [20 empty] | 0% | 0 | 1.3215
|  | Pension deficit payments | 9.5 | 0 | 0 | 0 | 0 | 9.5 | Do not allocate | [20 empty] | 57.7% | 5.4815 | 4.0185
|  | Metering | 0.79378 | 0 | 0 | 0 | 0 | 0.79378 | Do not allocate | [20 empty] | 0% | 0 | 0.79378
|  | Excluded services & de minimis | 9.7514 | 0 | 0 | 0 | 0 | 9.7514 | Do not allocate | [20 empty] | 0% | 0 | 9.7514
|  | Relevant distributed generation (less contributions) | -8.3267e-16 | 0 | 0 | 0 | 0 | -8.3267e-16 | Do not allocate | [20 empty] | 0% | 0 | -8.3267e-16
|  | IFI | 1.0145 | 0 | 0 | 0 | 0 | 1.0145 | Do not allocate | [20 empty] | 0% | 0 | 1.0145
|  | Disallowed Related Party Margins | 4.3033 | 0 | 0 | 0 | 0 | 4.3033 | Do not allocate | [20 empty] | 0% | 0 | 4.3033
|  | Statutory Depreciation | 41.9128 | 0 | 0 | 0 | 0 | 41.9128 | Do not allocate | [20 empty] | 0% | 0 | 41.9128
|  | Network Rates | 27.092 | 0 | 0 | 0 | 0 | 27.092 | Do not allocate | [20 empty] | 0% | 0 | 27.092
|  | Transmission Exit Charges | 4.4 | 0 | 0 | 0 | 0 | 4.4 | Do not allocate | [20 empty] | 0% | 0 | 4.4
|  | Pension deficit repair payments by related parties (note 2) | -9.5 | 0 | 0 | 0 | 0 | -9.5 | Do not allocate | [20 empty] | 0% | 0 | -9.5
|  | Non activity costs and reconciling amounts (note 3) | 2.3543 | 0 | 0 | 0 | 0 | 2.3543 | Do not allocate | [20 empty] | 0% | 0 | 2.3543
|  | Total Annual Operating & Capital Expenditure per Regulatory Accounts | 313 | 54.3136 | 64.449 | 14.9774 | 12.8851 | 166.3749 | [5 empty] | Total | 22.7089 | 6.4648 | 1.9929 | 27.441 | Total all network tiers | 205.2328 |  |  |  |  | Total all network tiers | 0.8066 |  |  |  | Total | 160.1739 | 152.8261 | Total all network tiers | 58.3332 |  |  |  | Total all network tiers | 0.25655
[19 empty] | Total by network tiers | 77.0225 | 70.9138 | 16.9703 | 40.3261 |  | Total by network tiers | 0.26229 | 0.24722 | 0.087993 | 0.2091 |  |  |  | Total by network tiers | 15.283 | 11.0131 | 4.5847 | 27.4523 | Total by network tiers | 0.052045 | 0.038394 | 0.023772 | 0.14234
[19 empty] | % | 37.53% | 34.55% | 8.269% | 19.65% |  | % | 32.52% | 30.65% | 10.91% | 25.92% |  |  |  | % | 26.2% | 18.88% | 7.86% | 47.06% | % | 20.29% | 14.97% | 9.266% | 55.48%
[10 empty] | 5 | 4 | 3 | 2 | [20 empty] | THESE % ARE USED TO ALLOCATE PRICE CONTROL OPEX
Step 4.a. calculate proportion of cost classified as direct costs
[19 empty] | Total direct+other | 57.4567 | 65.1114 | 15.3244 | 37.0622 | Max of zero or total from each catergory
[19 empty] | Total indirect | 20.3821 | 5.8024 | 1.7887 | 24.6294 | Max of zero or total from each catergory
[19 empty] | % direct+other | 73.81% | 91.82% | 89.55% | 60.08%
[19 empty] | % indirect | 26.19% | 8.182% | 10.45% | 39.92%

## Calc-Units
103. Units distributed (GWh) from RRP table 5.1 |  |  | Index
Units distributed (GWh) from RRP table 5.1
Units distributed at LV | 19286
Units distributed at HV | 9669
Units distributed at EHV+ | 710
Losses | 1439
104. Estimated line loss adjustment factors relative to LV
| LV services | LV | HV | EHV | 132kV
Units distributed at LV | 1 | 1 | 1 | 1 | 1
Units distributed at HV | 0 | 0 | 0.97204 | 0.97204 | 0.97204
Units distributed at EHV+ | 0 | 0 | 0 | 0.95807 | 0.95807
| LV services | LV | HV | EHV | 132kV
Units (GWh) flowing through each level, loss-adjusted to LV | 19286 | 19286 | 28684.6948 | 29364.9218 | 29364.9218
Units (kWh) flowing through each level, loss-adjusted to LV | 19286000000 | 19286000000 | 28684694777.9461 | 29364921785.7559 | 29364921785.7559

## Calc-Drivers
Drivers - LV, HV, EHV split | [5 empty] | Index
| Catergory | LV | HV | EHV | Source
| Net Capex | 13.6% | 33.18% | 53.23% | FBPQ capex - see "Calc Net capex"
| Customers | 100% | 0% | 0% | Assumption
| Network Length | 53.65% | 36.48% | 9.875% | RRP table 5.1
| Substations | 0% | 99.03% | 0.9745% | RRP table 5.1
| Tranmission Exit Charges | 0% | 0% | 100% | Assumption
| MEAV | 46.82% | 14.43% | 38.75% | FBPQ capex - see "Calc MEAV"
| EHV only | 0% | 0% | 100% | Assumption
| LV only | 100% | 0% | 0% | Assumption
| HV only | 0% | 100% | 0% | Assumption
Drivers - LV, LV/HV, HV, EHV split
| Catergory | LV | LV/HV | HV | EHV | Source
| Net Capex | 13.6% | 5.975% | 27.2% | 53.23% | FBPQ capex - see "Calc Net capex"
| No Cutomers | 100% | 0% | 0% | 0% | Assumption
| Network Length | 53.65% | 0% | 36.48% | 9.875% | RRP table 5.1
| No. Substations | 0% | 0% | 99.03% | 0.9745% | RRP table 5.1
| Tranmission Exit Charges | 0% | 0% | 0% | 100% | Assumption
| MEAV | 46.82% | 3.4% | 11.03% | 38.75% | FBPQ capex - see "Calc MEAV"
| MEAV excl services | 31.58% | 6.249% | 12.32% | 49.86% | FBPQ capex - see "Calc MEAV"
| MEAV excl services and 50% LV network | 0% | 0% | % of Total | 26.17% | FBPQ capex - see "Calc MEAV"
| EHV only | 0% | 0% | 0% | 100% | Assumption
| LV only | 100% | 0% | 0% | 0% | Assumption
| HV only | 0% | 0% | 100% | 0% | Assumption

## Calc-MEAV
MEAV by Voltage Level |  |  |  |  | Index
| MEAV - LV, HV, EHV, 132kV split |  |  |  | MEAV - LV, LV/HV, HV, EHV, 132kV split |  |  |  | MEAV - LV (excl. services), LV/HV, HV, EHV, 132kV split |  |  |  |  | MEAV - LV (excl. services + 50%LV), LV/HV, HV, EHV, 132kV split
| Sum of MEAV of asset classified in voltage tier (as calculated below) |  |  |  | Sum of MEAV of asset classified in voltage tier |  |  |  | Sum of MEAV of asset classified in voltage tier (as calculated below) |  |  |  |  | Sum of MEAV of asset classified in voltage tier (as calculated below)
|  | £m | % of Total |  |  | £m | % of Total |  |  | £m | % of Total |  |  |  | £m | % of Total
| LV | 8538239.7639 | 46.82% |  | LV | 8538239.7639 | 46.82% |  | LV | 4475251.9348 | 31.58% |  |  | LV | 2237625.9674 | 18.75%
| HV | 2631614.162 | 14.43% |  | LV/HV | 620092.2593 | 3.4% |  | LV/HV | 885671.8521 | 6.249% |  |  | LV/HV | 885671.8521 | 7.421%
| EHV | 1708721.0755 | 9.37% |  | HV | 2011521.9027 | 11.03% |  | HV | 1745942.3098 | 12.32% |  |  | HV | 1745942.3098 | 14.63%
| 132 kV | 5357130.161 | 29.38% | Check | EHV | 1708721.0755 | 9.37% |  | EHV | 1708721.0755 | 12.06% |  |  | EHV | 1708721.0755 | 14.32%
| Total | 18235705.1624 | 100% | OK | 132 kV | 5357130.161 | 29.38% | Check | 132 kV | 5357130.161 | 37.8% | Check |  | 132 kV | 5357130.161 | 44.89% | Check
[5 empty] | Total | 18235705.1624 | 100% | OK | Total | 14172717.3334 | 100% | OK |  | Total | 11935091.366 | 100% | OK
MEAV Calculation = Replacement unit cost*FBPQ closing asset balance
|  | Asset categories | Units | DNO reported Unit Cost (£) |  | Unit cost used in MEAV calculation (£) | Closing DCPR asset Balance (units) | MEAV (£)
|  |  |  | Sum of direct and indriect replacement unit cost from FBPQ C2 | PB power numbers, if available | Is DNO Unit cost if avaliable, otherwise PB power unit cost | Closing asset balannce from FBPQ V4 | Unit cost used in MEAV calculation*Closing DCPR asset Balance (units) | Classification
LV Network | [10 empty] | LV | 8538239.7639 | 46.82%
| Overhead lines | [7 empty] | LV |  | HV/LV | 760542.3493 | 4.171%
|  | LV Main (OHL) | km | 39.5099 | DATA | 39.5099 | 5011.7 | 198011.8165 | LV |  | HV | 1624509.0141 | 8.908%
|  | LV Service (OHL) | Each | 0.48183 | DATA | 0.48183 | 124564 | 60018.4444 | LV |  | EHV/HV | 1031189.4535 | 5.655%
[6 empty] | 0 |  |  | LV |  | EHV | 720647.1728 | 3.952%
| Overhead lines - Support |  |  |  |  | 0 |  |  | LV |  | 132kV/EHV | 611697.0056 | 3.354%
|  | LV Support | Each | 0 | DATA | 0 | 121993 | 0 | LV |  | 132kV | 4948880.4032 | 27.14%
[6 empty] | 0 |  |  | LV |  | All | 18235705.1624 | 100%
| Underground cables |  |  |  |  | 0 |  |  | LV
|  | LV Main (UG Consac) | km | 120.457 | DATA | 120.457 | 11 | 1325.0275 | LV
|  | LV Main (UG Plastic) | km | 120.457 | DATA | 120.457 | 15211.5 | 1832332.3097 | LV |  | EHV/HV | 1031189.4535 | 14.1%
|  | LV Main (UG Paper) | km | 120.457 | DATA | 120.457 | 18317 | 2206411.6568 | LV |  | EHV | 720647.1728 | 9.855%
|  | LV Service (UG) | Each | 1.6108 | DATA | 1.6108 | 2485119.1 | 4002969.3846 | LV |  | 132kV/EHV | 611697.0056 | 8.365%
[6 empty] | 0 |  |  | LV |  | 132kV | 4948880.4032 | 67.68%
| Switchgear |  |  |  |  | 0 |  |  | LV |  | All EHV | 7312414.0352 | 100%
|  | LV Pillar (ID) | Each | 5.4206 | DATA | 5.4206 | 9596 | 52015.7603 | LV
|  | LV Pillar (OD) | Each | 5.4206 | DATA | 5.4206 | 7772 | 42128.6462 | LV
|  | LV Board (WM) | Each | 5.4206 | DATA | 5.4206 | 2299 | 12461.8834 | LV
|  | LV UGB | Each | 4.5774 | DATA | 4.5774 | 28524 | 130564.8344 | LV
|  | LV Fuses (PM) | Each | 0 | DATA | 0 | 22692 | 0 | LV
|  | LV Fuses (TM) | Each |  | DATA |  | 0 |  | LV
[6 empty] | 0 |  |  | LV
HV network | [5 empty] | 0
| Overhead lines |  |  |  |  | 0 |  |  | HV
|  | 6.6/11 kV OHL (Open) | km | 40.8349 | DATA | 40.8349 | 12473.2 | 509342.3434 | HV
|  | 6.6/11 kV OHL (Covered) | km | 40.8349 | DATA | 40.8349 | 20 | 816.6988 | HV
|  | 20 kV OHL (Open) | km | 0 | DATA | 0 | 0 | 0 | HV
|  | 20 kV OHL (Covered) | km | 0 | DATA | 0 | 0 | 0 | HV
[6 empty] | 0 |  |  | HV
| Overhead lines - Support |  |  |  |  | 0 |  |  | HV
|  | 6.6/11 kV Support | Each | 0 | DATA | 0 | 160773 | 0 | HV
|  | 20 kV Support | Each | 0 | DATA | 0 | 0 | 0 | HV
[5 empty] | DATA | DATA |  |  | HV
| Underground cables (kms) |  |  |  |  | 0 |  |  | HV
|  | 6.6/11kV UG Cable | km | 80.1039 | DATA | 80.1039 | 13673.9 | 1095333.1777 | HV
|  | 20kV UG Cable | km | 0 | DATA | 0 | 0 | 0 | HV
[6 empty] | 0 |  |  | HV
| Submarine cables (kms) |  |  |  |  | 0 |  |  | HV
|  | HV Sub Cable | km | 0 | DATA | 0 | 0 | 0 | HV
[5 empty] | DATA | DATA |  |  | HV
| Switchgear |  |  |  |  | 0 |  |  | HV
|  | 6.6/11 kV CB (PM) | Each | 13.2503 | DATA | 13.2503 | 1227 | 16258.0871 | EHV/HV
|  | 6.6/11 kV CB (GM) | Each | 29.2711 | DATA | 29.2711 | 7868 | 230304.7115 | EHV/HV
|  | 6.6/11 kV Switch (PM) | Each | 1.5659 | DATA | 1.5659 | 387 | 606.0194 | HV
|  | 6.6/11 kV Switch (GM) | Each | 4.9387 | DATA | 4.9387 | 10608 | 52390.1408 | HV/LV
|  | 6.6/11 kV RMU | Each | 15.539 | DATA | 15.539 | 17327 | 269243.5348 | HV/LV
|  | 6.6/11 kV Switchgear - Other (PM) | Each | 1.5659 | DATA | 1.5659 | 11757 | 18410.7749 | HV
|  | 6.6/11 kV Switchgear - Other (GM) | Each |  | DATA |  | 0 |  | HV
|  | 20 kV CB (PM) | Each | 0 | DATA | 0 | 0 | 0 | EHV/HV
|  | 20 kV CB (GM) | Each | 0 | DATA | 0 | 0 | 0 | EHV/HV
|  | 20 kV Switch (PM) | Each | 0 | DATA | 0 | 0 | 0 | HV
|  | 20 kV Switch (GM) | Each | 0 | DATA | 0 | 0 | 0 | HV/LV
|  | 20 kV RMU | Each | 0 | DATA | 0 | 0 | 0 | HV/LV
|  | 20 kV Switchgear - Other (PM) | Each |  | DATA |  | 0 |  | HV
|  | 20 kV Switchgear - Other (GM) | Each |  | DATA |  | 0 |  | HV
0
| Transformers |  |  |  |  | 0
|  | 6.6/11 kV Transformer (PM) | Each | 3.4933 | DATA | 3.4933 | 22854 | 79834.8326 | HV/LV
|  | 6.6/11 kV Transformer (GM) | Each | 11.323 | DATA | 11.323 | 19308 | 218623.7511 | HV/LV
|  | 20 kV Transformer (PM) | Each | 0 | DATA | 0 | 0 | 0 | HV/LV
|  | 20 kV Transformer (GM) | Each | 0 | DATA | 0 | 0 | 0 | HV/LV
0
EHV Network | [5 empty] | 0
| Overhead lines |  |  |  |  | 0
|  | 33kV OHL (Pole Line) | km | 93.2338 | DATA | 93.2338 | 1753.5 | 163485.3829 | EHV
|  | 33kV OHL (Tower Line) | km | 148.5235 | DATA | 148.5235 | 933 | 138572.4573 | EHV
|  | 66kV OHL (Pole Line) | km | 175.8673 | DATA | 175.8673 | 0 | 0 | EHV
|  | 66kV OHL (Tower Line) | km | 175.8673 | DATA | 175.8673 | 0 | 0 | EHV
0
| Overhead lines - Support |  |  |  |  | 0
|  | 33kV Pole | Each | 0 | DATA | 0 | 28125 | 0 | EHV
|  | 33kV Tower | Each | 0 | DATA | 0 | 1287 | 0 | EHV
|  | 66kV Pole | Each | 0 | DATA | 0 | 0 | 0 | EHV
|  | 66kV Tower | Each | 0 | DATA | 0 | 0 | 0 | EHV
0
| Underground cables (kms) |  |  |  |  | 0
|  | 33kV UG Cable (Non Pressurised) | km | 243.5641 | DATA | 243.5641 | 1562.6 | 380593.3267 | EHV
|  | 33kV UG Cable (Oil) | km | 243.5641 | DATA | 243.5641 | 156 | 37996.006 | EHV
|  | 33kV UG Cable (Gas) | km | 0 | DATA | 0 | 0 | 0 | EHV
|  | 66kV UG Cable (Non Pressurised) | km | 1143.1373 | DATA | 1143.1373 | 0 | 0 | EHV
|  | 66kV UG Cable (Oil) | km | 1143.1373 | DATA | 1143.1373 | 0 | 0 | EHV
|  | 66kV UG Cable (Gas) | km | 0 | DATA | 0 | 0 | 0 | EHV
0
| Submarine cables (kms) |  |  |  |  | 0
|  | EHV Sub Cable | km | 0 | DATA | 0 | 0 | 0 | EHV
0
| Switchgear |  |  |  |  | 0
|  | 33 KV CB (ID) | Each | 175.265 | DATA | 175.265 | 414 | 72559.709 | 132kV/EHV
|  | 33 kV CB (OD) | Each | 175.265 | DATA | 175.265 | 575 | 100777.3736 | 132kV/EHV
|  | 33 kV Switch (GM) | Each | 0 | DATA | 0 | 0 | 0 | 132kV/EHV
|  | 33 kV Switch (PM) | Each | 0 | DATA | 0 | 0 | 0 | 132kV/EHV
|  | 33 kV RMU | Each | 557.5957 | DATA | 557.5957 | 54 | 30110.1652 | 132kV/EHV
|  | 33 kV Switchgear - Other | Each | 175.265 | DATA | 175.265 | 2044 | 358241.6551 | EHV/HV
|  | 66 KV CB (ID & OD) | Each | 661.1887 | DATA | 661.1887 | 0 | 0 | 132kV/EHV
|  | 66 KV Switchgear - Other | Each |  | DATA |  | 0 |  | EHV/HV
0
| Transformers |  |  |  |  | 0
|  | 33 kV Transformer (PM) | Each | 504.5946 | DATA | 504.5946 | 0 | 0 | EHV/HV
|  | 33 kV Transformer (GM) | Each | 541.9362 | DATA | 541.9362 | 717 | 388568.2816 | EHV/HV
|  | 33 kV AuxiliaryTransfomer | Each | 11.323 | DATA | 11.323 | 651 | 7371.2483 | EHV/HV
|  | 66 kV Transformer | Each | 2117.5144 | DATA | 2117.5144 | 0 | 0 | EHV/HV
|  | 66 kV AuxiliaryTransfomer | Each |  | DATA |  | 0 |  | EHV/HV
0
132kV Network | [5 empty] | 0
| Overhead lines |  |  |  |  | 0
|  | 132kV OHL Conductor (Pole Line) | km | 677.33 | DATA | 677.33 | 138 | 93471.5335 | 132kV
|  | 132kV OHL Conductor (Tower Line) | km | 1163.9764 | DATA | 1163.9764 | 2246 | 2614291.0092 | 132kV
0
| Overhead lines - Support |  |  |  |  | 0
|  | 132kV Pole | Each | 0 | DATA | 0 | 56 | 0 | 132kV
|  | 132kV Tower | Each | 0 | DATA | 0 | 4562 | 0 | 132kV
|  | 132kV Fittings (Tower Line) | Each | 0 | DATA | 0 | 9124 | 0 | 132kV
0
| Underground cables (kms) |  |  |  |  | 0
|  | 132kV UG Cable (Non Pressurised) | km | 1174.4562 | DATA | 1174.4562 | 42 | 49327.1591 | 132kV
|  | 132kV UG Cable (Oil) | km | 1174.4562 | DATA | 1174.4562 | 164 | 192610.8118 | 132kV
|  | 132kV UG Cable (Gas) | km | 0 | DATA | 0 | 0 | 0 | 132kV
0
| Submarine cables (kms) |  |  |  |  | 0
|  | 132 kV Sub Cable | km | 0 | DATA | 0 | 0 | 0 | 132kV
0
| Switchgear |  |  |  |  | 0
|  | 132 kV CB (ID & OD) | Each | 1048.3376 | DATA | 1048.3376 | 245 | 256842.7231 | 132kV
|  | 132 kV Switchgear (other) | Each | 1048.3376 | DATA | 1048.3376 | 1662 | 1742337.1665 | 132kV
0
| Transformers |  |  |  |  | 0
|  | 132 kV Transformer | Each | 2117.5144 | DATA | 2117.5144 | 191 | 404445.2426 | 132kV/EHV
|  | 132 kV AuxiliaryTransfomer | Each | 11.323 | DATA | 11.323 | 336 | 3804.5152 | 132kV/EHV
0
Tele-control / SCADA | [5 empty] | 0
| Primary substation |  |  |  |  | 0
|  | 132 kV/EHV RTU (PM) | Each | 62.645 | DATA | 62.645 | 2 | 125.29 | EHV/HV
|  | 132 kV/EHV RTU (GM) | Each | 62.645 | DATA | 62.645 | 484 | 30320.18 | EHV/HV
0
| Secondary substation |  |  |  |  | 0
|  | HV RTU (PM) | Each | 62.645 | DATA | 62.645 | 1491 | 93403.695 | HV/LV
|  | HV RTU (GM) | Each | 62.645 | DATA | 62.645 | 751 | 47046.395 | HV/LV
0
0
HV network switchgear | [5 empty] | 0
|  | 6.6/11 kV CB (GM) |  |  |  | 0
|  | Primary | Each | 29.2711 | DATA | 29.2711
|  | Distribution | Each | 7.4683 | DATA | 7.4683
|  | 20 kV Switch (GM) |  |  | DATA | DATA
|  | Primary | Each | 0 | DATA | 0
|  | Distribution | Each | 0 | DATA | 0
[7 empty] | Total MEAV | 18235705.1624
Note on E24: George Moran: assume included in OHL cost
Note on E37: George Moran: assume £0
Note on E48: George Moran: assume included in OHL cost
Note on E64: George Moran: assume same as Switch (PM)
Note on E88: George Moran: assume included in OHL cost
Note on E89: George Moran: assume included in OHL cost
Note on E110: George Moran: assume same as CB
Note on E117: George Moran: assume cost of HV/LV Tx
Note on E127: George Moran: assume included in OHL cost
Note on E128: George Moran: assume included in OHL cost
Note on E129: George Moran: assume included in OHL cost
Note on E141: George Moran: assume same as CB
Note on E145: George Moran: assume cost of HV/LV Tx
Note on E149: George Moran: from Macro costs
Note on E150: George Moran: from Macro costs
Note on E153: George Moran: from Macro costs
Note on E154: George Moran: from Macro costs
Note on I153: George Moran: formula not dragged down!

## Calc-Net capex
Total Net Capex |  |  |  |  | Index
| Total Net Capex 2005/06 -2014/15 LV, HV, EHV, 132kV split |  |  |  | Total Net Capex 2005/06 -2014/15 LV, LV/HV, HV, EHV, 132kV split
| Sum connecions/reinforcement/replacement capex -see below |  |  |  | Sum connecions/reinforcement/replacement capex -see below
|  | £m | % of Total |  |  | £m | % of Total
| LV | 128.0394 | 13.6% |  | LV | 128.0394 | 13.6%
| HV | 312.435 | 33.18% |  | LV/HV | 56.2673 | 5.975%
| EHV | 201.1132 | 21.36% |  | HV | 256.1676 | 27.2%
| 132 kV | 300.1329 | 31.87% |  | EHV | 201.1132 | 21.36%
[5 empty] | 132 kV | 300.1329 | 31.87%
Connection/Reinfircement/Replacement Capex LV, HV, EHV, 132kV split
| Connections Capex 2005/06 -2014/15 (£m) |  |  | General reniforcement Capex 2005/06 -2014/15 (£m) |  |  | Fault reniforcement Capex 2005/06 -2014/15 (£m)
| Connections spend minus customer contrbutions (from FBPQ LR1) |  |  | (from FBPQ LR4) |  |  | (from FBPQ LR6)
| LV | 41.1326 |  | LV | 10.2948 |  | LV | 0
| HV | 100.3892 |  | HV | 41.5699 |  | HV | 2.0497
| EHV | 0.39676 |  | EHV | 95.0895 |  | EHV | 10.9284
| 132 kV | 0 |  | 132 kV | 157.4934 |  | 132 kV | 10.1373
Replacement Capex 2005/06 -2014/15 (£m)
(from FBPQ NL1)
| LV | 76.6121
| HV | 168.4262
| EHV | 94.6984
| 132 kV | 132.5022
Connection/Reinfircement/Replacement Capex LV, LV/HV, HV, EHV, 132kV split
| Connections Capex 2005/06 -2014/15 (£m) |  |  | General reniforcement Capex 2005/06 -2014/15 (£m) |  |  | Fault reniforcement Capex 2005/06 -2014/15 (£m)
| Connections spend minus customer contrbutions (from FBPQ LR1) |  |  | (from FBPQ LR4) |  |  | (from FBPQ LR6)
| LV | 41.1326 |  | LV | 10.2948 |  | LV | 0
| LV/HV | 19.8451 | allocated in proportion to repex | LV/HV | 8.2176 | allocated in proportion to repex | LV/HV | 0.4052 | allocated in proportion to repex
| HV | 80.544 |  | HV | 33.3523 |  | HV | 1.6446
| EHV | 0.39676 |  | EHV | 95.0895 |  | EHV | 10.9284
| 132 kV | 0 |  | 132 kV | 157.4934 |  | 132 kV | 10.1373
Replacement Capex 2005/06 -2014/15 (£m)
(from FBPQ NL1)
| LV | 76.6121
| LV/HV | 27.7994 | HV/LV sub/trans costs |  | LV/HV/(LV/HV+HV) % | 19.77%
| HV | 140.6268
| EHV | 94.6984
| 132 kV | 132.5022

## Summary of revenue
|  | Summary of Revenue |  |  |  | Index
Allowed Demand Revenue (ADt) |  |  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
|  |  |  | 16 | 17 | 18 | 19 | 20
| Base Demand Revenue (BRt) |  | £m | 257.6017 | 263.8363 | 276.4269
| Pass through Items (PTt) |  | £m | 2.1203 | -2.121 | -4.5983
| Incentive Revenue (Ipt) |  | £m | 9.4297 | 8.568 | 26.4079
| Correction Factor (KDt) |  | £m | 8.5621 | -5.3794 | -1.4801
| Allowed Demand Revenue (Adt) |  | £m | 260.5896 | 275.6626 | 299.7165
| Regulated Demand Revenue (RDt) |  | £m | 255.53 | 274.28 | 287.86
| Net Movement on Revenue Provisions |  | £m | 1.83 | -0.72 | -3.93
| Over/Under Recovery |  | £m | -5.0596 | -1.3826 | -11.8565
Allowed Network Generation Revenue (AGt)
| Incentivised Generation (IGt) |  | £m | 0 | 0.012823 | 0.042558
| Registered Power Zones (RPZt) |  | £m | 0 | 0 | 0
| Correction Factor (KGt) |  | £m | 0 | 0 | -0.003022
| Allowed Network Generation Revenue (AGt) |  | £m | 0 | 0.012823 | 0.04558
| Network Generation Revenue (RGt) |  | £m | 0 | 0.01 | 0.08
| Over/Under Recovery |  | £m | 0 | -0.002823 | 0.03442
Metering Revenue
| Legacy Basic Meter Asset Provision Revenue |  | £m | 9.06 | 8.98 | 9.85
| Basic Meter Operation Revenue |  | £m | 6.7382 | 4.3876 | 0
|  |  |  | 15.7982 | 13.3676 | 9.85
Excluded Services and Revenue Outside of Price Control
| Excluded Services |  | £m | 63.79 | 67.66 | 104.02
| Revenue Outside of Price Control |  | £m | 4.87 | 4.63 | 4.45
| Di-Minimis Revenue |  | £m | 2.89 | 2.57 | 2.22
|  |  |  | 71.55 | 74.86 | 110.69

## Allowed revenue -DPCR4
|  | 2004/05 | 2005/6 | 2006/7 | 2007/8 | 2008/9 | 2009/10 | Index
|  | (£M) | (£M) | (£M) | (£M) | (£M) | (£M)
1 | Opening asset value |  | 947.9 | 989.2 | 1030.2 | 1064.8 | 1093.2
2 | Total capex |  | 117.8 | 117.5 | 117 | 116.6 | 116.4
3 | Depreciation |  | -76.5 | -76.5 | -82.4 | -88.2 | -94.1
4 | Closing asset value |  | 989.2 | 1030.2 | 1064.8 | 1093.2 | 1115.6
5 | Present value of opening / closing RAV |  | 947.9 |  |  |  | 851.7
6 | 5 Year movement in closing RAV | [5 empty] | 96.2
ALLOWED ITEMS
7 | Operating costs (excluding pensions) |  | 75.2 | 77.7 | 78.2 | 76.9 | 76.2
8 | Capital expenditure (excluding pensions) |  | 110.3 | 109.9 | 109.4 | 109 | 108.8
9 | Pensions allowance |  | 13 | 13.1 | 13.1 | 13.1 | 13.1
10 | Tax allowance |  | 27.2 | 26.3 | 26.4 | 26.8 | 26.8
11 | Capex incentive scheme |  | -0.8 | 0.6 | -0.6 | -0.6 | -0.2
12 | Sliding scale additional income |  | 1.4 | 1.4 | 1.5 | 1.5 | 1.6
13 | Opex incentive / Other adjustments |  | - | - | - | - | -
14 | Quality award |  | - | - | - | - | -
15 | DPCR3 costs |  | 1.5 | - | - | - | -
16 | Total allowed items |  | 227.7 | 229 | 228.1 | 226.8 | 226.3
17 | Present value of allowed items |  | 221.6 | 211.2 | 199.3 | 187.7 | 177.5
18 | 5 year movement in closing RAV | [5 empty] | 96.2
19 | TOTAL PRESENT VALUE OVER 5 YEARS | [5 empty] | 1093.5
REVENUE
20 | Revenue index |  | 1 | 1.009 | 1.02 | 1.033 | 1.044
21 | Discounted revenue index |  | 0.973 | 0.931 | 0.891 | 0.855 | 0.819
22 | Price control revenue | 256.2 | 241.2 | 243.4 | 246.1 | 249.1 | 251.8
23 | Excluded service revenue |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
24 | Total revenue |  | 244.7 | 246.9 | 249.6 | 252.6 | 255.3
25 | Present value of total revenue |  | 238.2 | 227.7 | 218.1 | 209.2 | 200.3
26 | TOTAL PRESENT VALUE OVER 5 YEARS | [5 empty] | 1093.5
Take these data from the February 2005 Ofgem document (link below), not the November 2004 final proposals.
http://www.ofgem.gov.uk/Markets/RetMkts/Metrng/Metering/Documents1/9745-5405.pdf

## FBPQ T4
Main Forecast Business Plan DPCR5 | [5 empty] | Index
T4 - Volume Summary
Total Asset Register Movement
[6 empty] | 2005/06 |  |  |  |  | 2006/07 |  |  |  |  | 2007/08 |  |  |  |  | 2008/09 |  |  |  |  | 2009/10
|  |  |  | Asset categories | Opening Balance DCPR4 | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance DPCR4
[6 empty] | LRE | NLRE | LRE | NLRE | 2005/06 | LRE | NLRE | LRE | NLRE | 2006/07 | LRE | NLRE | LRE | NLRE | 2007/08 | LRE | NLRE | LRE | NLRE | 2008/09 | LRE | NLRE | LRE | NLRE | 2009/10
LV Network
Overhead lines - Conductor
|  |  |  | LV Main (OHL) | 4914 | 22 | 8 | 214 | 4 | 5102 | 62 | 20 | 9 | 10 | 5039 | 0 | 21 | 35 | 18 | 5071 | 0 | 45.7 | 27.6 | 17.3 | 5070.2 | 0 | 148.3 | 25.5 | 64.3 | 5011.7
|  |  |  | LV Service (OHL) | 135999 | 911 | 1556 | 48 | 1633 | 135213 | 97 | 1478 | 77 | 565 | 134280 | 2469 | 1419 | 437 | 732 | 131561 | 1942 | 2476 | 358 | 637 | 128138 | 1785 | 3377 | 371 | 1217 | 124564
Overhead lines - Support
|  |  |  | LV Support | 123846 | 134 | 0 | 61 | 0 | 123773 | 228 | 0 | 335 | 0 | 123880 | 1316 | 910 | 1127 | 910 | 123691 | 1035 | 570 | 902 | 142 | 123130 | 951 | 1458 | 872 | 400 | 121993
Underground cables
|  |  |  | LV Main (UG Consac) | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11
|  |  |  | LV Main (UG Plastic) | 13223 | 0 | 0 | 655 | 39 | 13917 | 0 | 2 | 310 | 75 | 14300 | 0 | 0 | 305 | 50 | 14655 | 0 | 1.4 | 210.3 | 74.6 | 14938.5 | 0 | 1 | 196 | 78 | 15211.5
|  |  |  | LV Main (UG Paper) | 18395 | 0 | 7 | 0 | 0 | 18388 | 0 | 31 | 0 | 0 | 18357 | 0 | 33 | 0 | 0 | 18324 | 0 | 4 | 0 | 0 | 18320 | 0 | 3 | 0 | 0 | 18317
|  |  |  | LV Service (UG) | 2361332 | 77 | 1230 | 27978 | 1230 | 2389233 | 0 | 1153 | 23378 | 2066 | 2413524 | 0 | 1684 | 27485 | 2371 | 2441696 | 0 | 108 | 20668.5 | 1787 | 2464043.5 | 0 | 262 | 18931.6 | 2406 | 2485119.1
Switchgear
|  |  |  | LV Pillar (ID) | 8541 | 12 | 49 | 210 | 49 | 8739 | 43 | 105 | 392 | 105 | 9088 | 0 | 94 | 259 | 103 | 9356 | 0 | 283 | 204 | 143 | 9420 | 0 | 116 | 188 | 104 | 9596
|  |  |  | LV Pillar (OD) | 7893 | 0 | 0 | 80 | 0 | 7973 | 3 | 36 | 0 | 36 | 7970 | 181 | 0 | 136 | 0 | 7925 | 142 | 0 | 63 | 0 | 7846 | 131 | 0 | 57 | 0 | 7772
|  |  |  | LV Board (WM) | 2425 | 0 | 0 | 0 | 0 | 2425 | 43 | 0 | 0 | 0 | 2382 | 33 | 0 | 0 | 0 | 2349 | 26 | 0 | 0 | 0 | 2323 | 24 | 0 | 0 | 0 | 2299
|  |  |  | LV UGB | 27050 | 0 | 1 | 63 | 9 | 27121 | 0 | 159 | 127 | 136 | 27225 | 0 | 330 | 484 | 155 | 27534 | 0 | 340 | 392 | 457 | 28043 | 0 | 33 | 391 | 123 | 28524
|  |  |  | LV Fuses (PM) | 22689 | 0 | 0 | 31 | 0 | 22720 | 109 | 0 | 88 | 0 | 22699 | 485 | 0 | 484 | 0 | 22698 | 382 | 0 | 380 | 0 | 22696 | 351 | 0 | 347 | 0 | 22692
|  |  |  | LV Fuses (TM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV network
Overhead lines - Conductor
|  |  |  | 6.6/11 kV OHL (Open) | 12571 | 23 | 22 | 13 | 22 | 12561 | 17 | 43 | 46 | 43 | 12590 | 78 | 57 | 60 | 57 | 12572 | 34.3 | 250.1 | 26.8 | 219.4 | 12533.8 | 49.4 | 167.5 | 26 | 130.3 | 12473.2
|  |  |  | 6.6/11 kV OHL (Covered) | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 1 | 0 | 0 | 0 | 21 | 0.4 | 0 | 0 | 0 | 20.6 | 0.6 | 0 | 0 | 0 | 20
|  |  |  | 20 kV OHL (Open) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV OHL (Covered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overhead lines - Support
|  |  |  | 6.6/11 kV Support | 163477 | 229 | 225 | 145 | 225 | 163393 | 0 | 233 | 697 | 506 | 164363 | 2217 | 1136 | 647 | 1136 | 162793 | 974 | 1765 | 525 | 1460 | 162039 | 1403 | 1533 | 509 | 1161 | 160773
|  |  |  | 20 kV Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Underground cables (kms)
|  |  |  | 6.6/11kV UG Cable | 12768 | 0 | 10 | 122 | 30 | 12910 | 1 | 55 | 184 | 55 | 13093 | 0 | 10 | 167 | 38 | 13288 | 0 | 10.8 | 133 | 77.3 | 13487.5 | 0 | 14.7 | 124.7 | 76.4 | 13673.9
|  |  |  | 20kV UG Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  |  | HV Sub Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0
Switchgear
|  |  |  | 6.6/11 kV CB (PM) | 1148 | 0 | 63 | 0 | 23 | 1108 | 0 | 25 | 0 | 24 | 1107 | 0 | 66 | 0 | 56 | 1097 | 0 | 0 | 0 | 27 | 1124 | 0 | 0 | 0 | 103 | 1227
|  |  |  | 6.6/11 kV CB (GM) | 7882 | 0 | 18 | 73 | 15 | 7952 | 0 | 321 | 35 | 37 | 7703 | 0 | 344 | 169 | 32 | 7560 | 0 | 8 | 135 | 36 | 7723 | 0 | 23 | 128 | 40 | 7868
|  |  |  | 6.6/11 kV Switch (PM) | 195 | 0 | 0 | 0 | 41 | 236 | 0 | 6 | 0 | 28 | 258 | 0 | 0 | 0 | 36 | 294 | 0 | 387 | 0 | 418 | 325 | 0 | 72 | 0 | 134 | 387
|  |  |  | 6.6/11 kV Switch (GM) | 11859 | 0 | 162 | 47 | 53 | 11797 | 0 | 355 | 4 | 1 | 11447 | 0 | 410 | 32 | 0 | 11069 | 0 | 236 | 25 | 1 | 10859 | 0 | 276 | 23 | 2 | 10608
|  |  |  | 6.6/11 kV RMU | 14442 | 0 | 13 | 297 | 47 | 14773 | 0 | 94 | 518 | 269 | 15466 | 4 | 243 | 552 | 243 | 16014 | 2 | 65 | 445 | 274 | 16666 | 3 | 94 | 428 | 330 | 17327
|  |  |  | 6.6/11 kV Switchgear - Other (PM) | 10690 | 0 | 1352 | 3 | 1405 | 10746 | 0 | 134 | 12 | 388 | 11012 | 0 | 150 | 192 | 352 | 11406 | 0 | 0 | 168 | 0 | 11574 | 0 | 0 | 183 | 0 | 11757
|  |  |  | 6.6/11 kV Switchgear - Other (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV CB (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV CB (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switch (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switch (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV RMU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switchgear - Other (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switchgear - Other (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformers
|  |  |  | 6.6/11 kV Transformer (PM) | 22676 | 279 | 54 | 323 | 54 | 22720 | 284 | 149 | 263 | 149 | 22699 | 356 | 129 | 352 | 129 | 22695 | 156 | 136 | 280 | 139 | 22822 | 225 | 237 | 262 | 232 | 22854
|  |  |  | 6.6/11 kV Transformer (GM) | 17685 | 0 | 73 | 392 | 74 | 18078 | 0 | 123 | 357 | 143 | 18455 | 50 | 199 | 357 | 199 | 18762 | 22 | 75 | 285 | 92 | 19042 | 32 | 102 | 269 | 131 | 19308
|  |  |  | 20 kV Transformer (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Transformer (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EHV Network
Overhead lines - Conductor
|  |  |  | 33kV OHL (Pole Line) | 1806 | 1 | 4 | 0 | 4 | 1805 | 11 | 9 | 0 | 9 | 1794 | 30 | 18 | 5 | 18 | 1769 | 5 | 3.3 | 4.3 | 1.8 | 1766.8 | 0.6 | 22 | 0.7 | 8.6 | 1753.5
|  |  |  | 33kV OHL (Tower Line) | 947 | 0 | 0 | 0 | 2 | 949 | 0 | 0 | 0 | 0 | 949 | 24 | 0 | 8 | 0 | 933 | 0 | 0 | 0 | 0 | 933 | 0 | 0 | 0 | 0 | 933
|  |  |  | 66kV OHL (Pole Line) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66kV OHL (Tower Line) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overhead lines - Support
|  |  |  | 33kV Pole | 28943 | 1 | 36 | 1 | 36 | 28943 | 276 | 0 | 6 | 0 | 28673 | 483 | 144 | 83 | 144 | 28273 | 50 | 32 | 43 | 20 | 28254 | 6 | 232 | 7 | 102 | 28125
|  |  |  | 33kV Tower | 1326 | 30 | 0 | 0 | 0 | 1296 | 0 | 0 | 10 | 7 | 1313 | 63 | 0 | 37 | 0 | 1287 | 0 | 0 | 0 | 0 | 1287 | 0 | 0 | 0 | 0 | 1287
|  |  |  | 66kV Pole | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66kV Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Underground cables (kms)
|  |  |  | 33kV UG Cable (Non Pressurised) | 1381 | 0 | 0 | 67 | 25 | 1473 | 2 | 8 | 55 | 8 | 1526 | 0 | 0 | 23 | 16 | 1565 | 1.9 | 19.2 | 11.9 | 4.2 | 1560 | 1.1 | 12.4 | 4.4 | 11.7 | 1562.6
|  |  |  | 33kV UG Cable (Oil) | 157 | 1 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 156
|  |  |  | 33kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66kV UG Cable (Oil) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  |  | EHV Sub Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0
Switchgear
|  |  |  | 33 KV CB (ID) | 365 | 0 | 0 | 5 | 0 | 370 | 1 | 0 | 12 | 0 | 381 | 0 | 0 | 15 | 15 | 411 | 0 | 6 | 0 | 6 | 411 | 0 | 7 | 3 | 7 | 414
|  |  |  | 33 kV CB (OD) | 569 | 0 | 0 | 17 | 1 | 587 | 0 | 0 | 0 | 0 | 587 | 12 | 12 | 1 | 12 | 576 | 0 | 9 | 0 | 8 | 575 | 0 | 9 | 0 | 9 | 575
|  |  |  | 33 kV Switch (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33 kV Switch (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33 kV RMU | 51 | 0 | 0 | 0 | 0 | 51 | 1 | 0 | 5 | 0 | 55 | 2 | 0 | 1 | 0 | 54 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 54
|  |  |  | 33 kV Switchgear - Other | 2013 | 0 | 0 | 2 | 0 | 2015 | 0 | 0 | 2 | 0 | 2017 | 0 | 17 | 2 | 42 | 2044 | 0 | 0 | 0 | 0 | 2044 | 0 | 0 | 0 | 0 | 2044
|  |  |  | 66 KV CB (ID & OD) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66 KV Switchgear - Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformers
|  |  |  | 33 kV Transformer (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33 kV Transformer (GM) | 702 | 0 | 0 | 11 | 0 | 713 | 3 | 3 | 6 | 3 | 716 | 0 | 0 | 0 | 1 | 717 | 0 | 5 | 0 | 5 | 717 | 2 | 0 | 2 | 0 | 717
|  |  |  | 33 kV AuxiliaryTransfomer | 645 | 0 | 0 | 5 | 0 | 650 | 2 | 0 | 0 | 0 | 648 | 0 | 13 | 0 | 16 | 651 | 0 | 0 | 0 | 0 | 651 | 0 | 0 | 0 | 0 | 651
|  |  |  | 66 kV Transformer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 66 kV AuxiliaryTransfomer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132kV Network
Overhead lines - Conductor
|  |  |  | 132kV OHL Conductor (Pole Line) | 143 | 0 | 1 | 0 | 1 | 143 | 5 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 138
|  |  |  | 132kV OHL Conductor (Tower Line) | 2233 | 0 | 0 | 0 | 0 | 2233 | 0 | 0 | 13 | 0 | 2246 | 4 | 8 | 4 | 8 | 2246 | 0 | 130 | 0 | 130 | 2246 | 0 | 130 | 0 | 130 | 2246
Overhead lines - Support
|  |  |  | 132kV Pole | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56
|  |  |  | 132kV Tower | 4569 | 0 | 7 | 0 | 7 | 4569 | 7 | 0 | 0 | 0 | 4562 | 0 | 0 | 0 | 0 | 4562 | 0 | 5 | 0 | 5 | 4562 | 0 | 4 | 0 | 4 | 4562
|  |  |  | 132kV Fittings (Tower Line) | 9138 | 0 | 0 | 0 | 0 | 9138 | 14 | 0 | 0 | 0 | 9124 | 0 | 0 | 0 | 0 | 9124 | 0 | 49 | 0 | 49 | 9124 | 0 | 45 | 0 | 45 | 9124
Underground cables (kms)
|  |  |  | 132kV UG Cable (Non Pressurised) | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 1 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 7 | 0 | 42 | 0 | 0 | 0 | 0 | 42
|  |  |  | 132kV UG Cable (Oil) | 164 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 164
|  |  |  | 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  |  | 132 kV Sub Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Switchgear
|  |  |  | 132 kV CB (ID & OD) | 264 | 44 | 0 | 4 | 0 | 224 | 0 | 0 | 12 | 0 | 236 | 0 | 3 | 0 | 12 | 245 | 0 | 0 | 0 | 0 | 245 | 0 | 10 | 0 | 10 | 245
|  |  |  | 132 kV Switchgear (other) | 1618 | 0 | 0 | 0 | 0 | 1618 | 0 | 0 | 0 | 0 | 1618 | 0 | 36 | 0 | 80 | 1662 | 0 | 0 | 0 | 0 | 1662 | 0 | 0 | 0 | 0 | 1662
Transformers
|  |  |  | 132 kV Transformer | 189 | 0 | 0 | 2 | 0 | 191 | 1 | 0 | 0 | 0 | 190 | 9 | 0 | 7 | 0 | 188 | 4 | 0 | 7 | 0 | 191 | 0 | 2 | 0 | 2 | 191
|  |  |  | 132 kV AuxiliaryTransfomer | 327 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 327 | 0 | 8 | 0 | 17 | 336 | 2 | 0 | 2 | 0 | 336 | 0 | 0 | 0 | 0 | 336
Tele-control / SCADA
Primary substation
|  |  |  | 132 kV/EHV RTU (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2
|  |  |  | 132 kV/EHV RTU (GM) | 462 | 0 | 0 | 0 | 0 | 462 | 0 | 0 | 0 | 5 | 467 | 0 | 0 | 0 | 17 | 484 | 0 | 0 | 0 | 0 | 484 | 0 | 0 | 0 | 0 | 484
Secondary substation
|  |  |  | HV RTU (PM) | 829 | 0 | 0 | 0 | 0 | 829 | 0 | 0 | 0 | 335 | 1164 | 0 | 0 | 0 | 327 | 1491 | 0 | 0 | 0 | 0 | 1491 | 0 | 0 | 0 | 0 | 1491
|  |  |  | HV RTU (GM) | 224 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 32 | 256 | 0 | 0 | 0 | 495 | 751 | 0 | 0 | 0 | 0 | 751 | 0 | 0 | 0 | 0 | 751

## FBPQ LR1
Main Forecast Business Plan DPCR5 |  |  |  |  | Index
LR1 - Demand
Demand Totals
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
| Gross direct costs | £m | 54.2306 | 38.8379 | 91.6745 | 60.6262 | 65.6828 | 67.8348 | 68.9569 | 73.5539 | 77.2727 | 81.3482 | 184.743 | 126.3089 | 311.052 | 368.9665 | 18.62%
| Customer contributions directs | £m | 47.9 | 34.2 | 74.4 | 47.7 | 49.6 | 50.6 | 53 | 56.9 | 60.2 | 63.6 | 156.5 | 97.3 | 253.8 | 284.3 | 12.02%
| Net (gross directs - customer contributions directs) | £m | 6.3306 | 4.6379 | 17.2745 | 12.9262 | 16.0828 | 17.2348 | 15.9569 | 16.6539 | 17.0727 | 17.7482 | 28.243 | 29.0089 | 57.252 | 84.6665 | 47.88%
| Customer contributions indirects | £m | 12.7 | 16.3 | 7.4 | 2.6 | 4.5 | 5.7 | 5.9 | 6.3 | 6.7 | 7 | 36.4 | 7.1 | 43.5 | 31.6 | -27.36%
| Net (gross directs - customer contributions directs and indirects) | £m | -6.3694 | -11.6621 | 9.8745 | 10.3262 | 11.5828 | 11.5348 | 10.0569 | 10.3539 | 10.3727 | 10.7482 | -8.157 | 21.9089 | 13.752 | 53.0665 | 285.9%
Demand trends
|  |  | DPCR4 |  |  |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
| Estimated system maximum demand | MW | 5142 | 5071.997 | 5165.0399 | 5268.9999 | 5307.953 | 5347.0146 | 5386.0264 | 5424.998 | 5464.0472 | 5503.0449
| Increase (reduction) in max demand | MW | 29.8836 | -70.003 | 93.043 | 103.9599 | 38.9531 | 39.0616 | 39.0118 | 38.9717 | 39.0492 | 38.9977
| Incremental increase in max demand due to new connections | MW | 61.2232 | 86.579 | 67.9341 | 50.4602 | 45.6834 | 47.1804 | 51.4786 | 56.8386 | 63.0161 | 70.0645
| Incremental reduction in max demand due to disconnections | MW | -31.3396 | -35.5821 | -23.6911 | -32.6003 | -34.2303 | -32.5188 | -29.2669 | -29.2669 | -29.2669 | -29.2669
| Net change in max demand (not due to connections/disconnections) | MW | 0 | -121 | 48.8 | 86.1 | 27.5 | 24.4 | 16.8 | 11.4 | 5.3 | -1.8
| Estimated units distributed | GWh | 30104.9 | 29508.8729 | 29665.4035 | 29133.7791 | 27786.1037 | 27637.5665 | 28143.0497 | 28347.7613 | 28504.6595 | 28539.0621
| Increase (reduction) in units distributed | GWh | 0 | -596.0271 | 156.5306 | -531.6244 | -1347.6754 | -148.5373 | 505.4833 | 204.7116 | 156.8982 | 34.4026
| Increase in units distributed due to generic background demand growth | GWh | 0 | -383.7 | 204.4 | 603.3 | -364.4901 | -76.9651 | 595.7583 | 321.9977 | 311.5937 | 227.4118
| Reduction in units distributed due to energy efficiency | GWh | 0 | -60.2097 | -59.0179 | -59.3307 | -58.2675 | -55.5722 | -55.2751 | -56.2861 | -56.6955 | -57.0093
| Units distributed offset by DG | GWh | 0 | 0 | 0 | 0 | -1 | -16 | -35 | -61 | -98 | -136
| Units distributed offset by DSM | GWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Price impact on units distributed | GWh | 0 | -152.1173 | 11.1485 | -176.7874 | 0 | 0 | 0 | 0 | 0 | 0
| Economic downturn effect on units distributed | GWh | 0 | 0 | 0 | -898.8063 | -923.9177 | 0 | 0 | 0 | 0 | 0
Estimated units distributed
| LV | GWh | 19523.2665 | 19016.9294 | 19286.2279 | 19229.0747 | 18354.6254 | 18249.2773 | 18625.9495 | 18839.1568 | 18968.9344 | 19043.0327
| HV | GWh | 9858.5455 | 9824.431 | 9669.4933 | 9284.3656 | 8814.1176 | 8770.9284 | 8899.7394 | 8891.2437 | 8918.3643 | 8878.6686
| EHV (inc. 132kV) | GWh | 723.0484 | 667.5866 | 709.6413 | 620.3173 | 617.3393 | 617.3393 | 617.3393 | 617.3393 | 617.3393 | 617.3393
| Total units distributed | GWh | 30104.8604 | 29508.947 | 29665.3625 | 29133.7576 | 27786.0822 | 27637.5449 | 28143.0282 | 28347.7398 | 28504.638 | 28539.0406
Incremental increase in units distributed attributable to new connections
| LV | MWh | 203209.9621 | 253590.3238 | 247138.8125 | 162407.1611 | 149722.5723 | 153294.5253 | 166488.8697 | 183276.6621 | 202079.7214 | 223108.7723
| HV | MWh | 196300.379 | 316771.3281 | 192019.6854 | 167619.7317 | 148778.5645 | 155157.1037 | 170132.0158 | 188455.36 | 210209.4127 | 235525.0061
| EHV (inc. 132kV) | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total increase in units distributed due to new connections | MWh | 399510.3411 | 570361.6519 | 439158.4978 | 330026.8928 | 298501.1367 | 308451.629 | 336620.8854 | 371732.0221 | 412289.1341 | 458633.7784
Connections/disconnections volume
|  |  | DPCR4 |  |  |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
Connections/Disconnections
Estimated number demand connections/disconnections at LV
| IDNO connections | # | 2 | 2 | 4 | 3.6 | 3.2 | 3.4 | 3.7 | 4.2 | 4.7 | 5.3
| Connections (excluding IDNOs) | # | 34184 | 34314.8 | 33331 | 27899.8 | 28372.2 | 30153.7 | 31706.1 | 34216.2 | 36957.8 | 39945.8
| Disconnections | # | 9236.7 | 10487.1 | 6982.5 | 9608.2 | 10088.7 | 9584.2 | 8625.8 | 8625.8 | 8625.8 | 8625.8
Estimated number demand connections/disconnections at HV
| IDNO connections | # | 0 | 6 | 10 | 9 | 8.1 | 8.5 | 9.4 | 10.4 | 11.6 | 13.1
| Connections (excluding IDNOs) | # | 81 | 396 | 196 | 174.7 | 156.6 | 164 | 180.3 | 200 | 223.7 | 252.1
| Disconnections | # | 93.3 | 105.9 | 70.5 | 97.1 | 101.9 | 96.8 | 87.1 | 87.1 | 87.1 | 87.1
Estimated number demand connections/disconnections at EHV
| IDNO connections | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Connections (excluding IDNOs) | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Disconnections | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Estimated number demand connections/disconnections at 132kV
| IDNO connections | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Connections (excluding IDNOs) | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Disconnections | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total number of demand connections | # | 34267 | 34718.8 | 33541 | 28087.1 | 28540.1 | 30329.6 | 31899.5 | 34430.8 | 37197.8 | 40216.3
| Total number of demand disconnections | # | 9330 | 10593 | 7053 | 9705.3 | 10190.6 | 9681 | 8712.9 | 8712.9 | 8712.9 | 8712.9
Customer specific demand investment
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
| Customer specific demand investment | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
New connections & customer specific reinforcement:
Connections provided at LV
| Sole use | £m | 0 | 0 | 0 | 27.9737 | 25.4384 | 25.227 | 26.9874 | 29.5405 | 31.6025 | 33.7467 | 0 | 53.4121 | 53.4121 | 147.1042 | 175.4%
| Shared | £m | 43.1652 | 30.9707 | 58.955 | 15.8285 | 12.2224 | 12.1169 | 12.9976 | 14.2746 | 15.2564 | 16.329 | 133.0909 | 28.0509 | 161.1418 | 70.9746 | -55.96%
| LV total | £m | 43.1652 | 30.9707 | 58.955 | 43.8022 | 37.6608 | 37.3439 | 39.9851 | 43.8151 | 46.8589 | 50.0757 | 133.0909 | 81.4629 | 214.5538 | 218.0787 | 1.643%
Connections provided at HV
| Sole use | £m | 0 | 0 | 0 | 5.6744 | 8.9432 | 9.7333 | 9.6242 | 9.9129 | 10.1049 | 10.3912 | 0 | 14.6176 | 14.6176 | 49.7665 | 240.5%
| Shared | £m | 10.7664 | 7.668 | 32.121 | 11.1496 | 19.0788 | 20.7576 | 19.3476 | 19.8259 | 20.3088 | 20.8814 | 50.5554 | 30.2284 | 80.7838 | 101.1213 | 25.18%
| HV total | £m | 10.7664 | 7.668 | 32.121 | 16.824 | 28.022 | 30.4909 | 28.9718 | 29.7388 | 30.4137 | 31.2726 | 50.5554 | 44.846 | 95.4014 | 150.8878 | 58.16%
Connections provided at EHV
| Sole use | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shared | £m | 0.29907 | 0.19917 | 0.59853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0968 | 0 | 1.0968 | 0 | -100%
| EHV total | £m | 0.29907 | 0.19917 | 0.59853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0968 | 0 | 1.0968 | 0 | -100%
Connections provided at 132kV
| Sole use | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shared | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV total | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expenditure on DSM to avoid customer spec investment | £m |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total inc. expenditure on DSM to avoid customer spec investment | £m | 54.2306 | 38.8379 | 91.6745 | 60.6262 | 65.6828 | 67.8348 | 68.9569 | 73.5539 | 77.2727 | 81.3482 | 184.743 | 126.3089 | 311.052 | 368.9665 | 18.62%
| Expenditure avoided due to DG | £m |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expenditure avoided due to DSM | £m |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Customer contributions - customer specific demand investment
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
| Customer contributions - customer specific demand investment | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
Customer contributions (directs) for connections at LV
| Sole use | £m | 0 | 0 | 0 | 28.1 | 25.6 | 25.4 | 27.2 | 29.8 | 31.9 | 34.1 | 0 | 53.7 | 53.7 | 148.4 | 176.4%
| Shared | £m | 38.1 | 27.4 | 49.1 | 10.4 | 9.5 | 9.4 | 10.1 | 11 | 11.8 | 12.6 | 114.6 | 19.9 | 134.5 | 54.9 | -59.18%
| LV total | £m | 38.1 | 27.4 | 49.1 | 38.5 | 35.1 | 34.8 | 37.3 | 40.8 | 43.7 | 46.7 | 114.6 | 73.6 | 188.2 | 203.3 | 8.023%
Customer contributions (directs) for connections at HV
| Sole use | £m | 0 | 0 | 0 | 5.7 | 9 | 9.8 | 9.7 | 10 | 10.2 | 10.5 | 0 | 14.7 | 14.7 | 50.2 | 241.5%
| Shared | £m | 9.5 | 6.8 | 24.9 | 3.5 | 5.5 | 6 | 6 | 6.1 | 6.3 | 6.4 | 41.2 | 9 | 50.2 | 30.8 | -38.65%
| HV total | £m | 9.5 | 6.8 | 24.9 | 9.2 | 14.5 | 15.8 | 15.7 | 16.1 | 16.5 | 16.9 | 41.2 | 23.7 | 64.9 | 81 | 24.81%
Customer contributions (directs) for connections at EHV
| Sole use | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shared | £m | 0.3 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0.7 | 0 | -100%
| EHV total | £m | 0.3 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0.7 | 0 | -100%
Customer contributions (directs) for connections at 132kV
| Sole use | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shared | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV total | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer contributions (directs) total | £m | 47.9 | 34.2 | 74.4 | 47.7 | 49.6 | 50.6 | 53 | 56.9 | 60.2 | 63.6 | 156.5 | 97.3 | 253.8 | 284.3 | 12.02%
| Customer contributions (indirects) | £m | 12.7 | 16.3 | 7.4 | 2.6 | 4.5 | 5.7 | 5.9 | 6.3 | 6.7 | 7 | 36.4 | 7.1 | 43.5 | 31.6 | -27.36%
| Customer contributions total | £m | 60.6 | 50.5 | 81.8 | 50.3 | 54.1 | 56.3 | 58.9 | 63.2 | 66.9 | 70.6 | 192.9 | 104.4 | 297.3 | 315.9 | 6.256%
| Total inc. exp on DSM to avoid customer spec investment (net of cust cont) | £m | -6.3694 | -11.6621 | 9.8745 | 10.3262 | 11.5828 | 11.5348 | 10.0569 | 10.3539 | 10.3727 | 10.7482 | -8.157 | 21.9089 | 13.752 | 53.0665 | 285.9%
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
| Unapportioned part of shared LV | £m | 5.0652 | 3.5707 | 9.855 | 5.4285 | 2.7224 | 2.7169 | 2.8976 | 3.2746 | 3.4564 | 3.729 | 18.4909 | 8.1509 | 26.6418 | 16.0746 | -39.66%
| Unapportioned part of shared HV | £m | 1.2664 | 0.868 | 7.221 | 7.6496 | 13.5788 | 14.7576 | 13.3476 | 13.7259 | 14.0088 | 14.4814 | 9.3554 | 21.2284 | 30.5838 | 70.3213 | 129.9%
| Unapportioned part of shared EHV | £m | -0.00093428 | 0.19917 | 0.19853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39676 | 0 | 0.39676 | 0 | -100%
| Unapportioned part of shared 132kV | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FBPQ LR4
Main Forecast Business Plan DPCR5 | [5 empty] | Index
LR4 - General reinforcement
General reinforcement expenditure
|  |  | DPCR4 |  |  |  |  | DPCR5 | [5 empty] | DPCR4 |  |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 |  | Actuals | Forecast | Total |  | Forecast | % change
|  |  | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) |  | (£m) | (£m) | (£m) |  | (£m) | (£m)
General reinforcement:
|  | LV System | 0.59788 | 1.493 | 1.2961 | 1.4502 | 0.77762 | 0.95352 | 0.93103 | 0.92934 | 0.92885 | 0.93731 |  | 3.387 | 2.2278 | 5.6148 |  | 4.6801 | -16.65%
|  | HV System | 4.1851 | 5.2754 | 3.8882 | 3.235 | 3.6659 | 4.3438 | 4.2414 | 4.2337 | 4.2314 | 4.27 |  | 13.3487 | 6.9009 | 20.2496 |  | 21.3203 | 5.287%
|  | EHV System | 10.8614 | 6.6689 | 3.1903 | 0.2231 | 3.4437 | 18.3288 | 13.7586 | 15.076 | 11.2494 | 12.2892 |  | 20.7207 | 3.6668 | 24.3875 |  | 70.702 | 189.9%
|  | 132kV System | 9.0678 | 12.2429 | 24.027 | 14.7247 | 1.1109 | 5.933 | 16.2414 | 22.2009 | 25.4918 | 26.4531 |  | 45.3377 | 15.8355 | 61.1733 |  | 96.3202 | 57.45%
|  | Expenditure on DSM to avoid gen reinf. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
|  | Total | 24.7123 | 25.6803 | 32.4015 | 19.6329 | 8.9982 | 29.5591 | 35.1724 | 42.4399 | 41.9015 | 43.9496 |  | 82.7941 | 28.631 | 111.4251 |  | 193.0225 | 73.23%
|  | Expenditure avoided due to DG |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
|  | Expenditure avoided due to DSM |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
General reinforcement projects
|  | Scheme details | DPCR5 2011/12: DPCR4 |  | DPCR5 |  |  |  |  | Scheme description
|  | Named scheme | Voltage | Limiting Factor | Forecast year in which substation demand will reach substation firm capacity | MVA of additional firm capacity to be installed | Total cost of project | Total cost of project in DPCR5 period | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Brief description of work involved, substations affected, assets installed/replaced etc.
|  | (Unique name) | (kV) | (a-j) | (Year) | (MVA) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (Description)
| 1 | Annesley - Hucknall 33kV | 33kV | b | 2011 | 14 | 2.0671 | 2.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0345 | 1.0326 | 0 | 0 | Uprating 33kV double circuit line to 40MVA and interconnection of cables via Linby (approx 10km of cable) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2 | Bainton - new GSP | 132kV | a | 2013 | 80 | 4.9811 | 4.9811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9609 | 3.0202 | Reconfiguration of the 132kV circuit between Bourne and Stamford | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 3 | Berkswell - Coventry South / Coventry West 132kV | 132kV | b | 2010 | 39 | 1.0345 | 1.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0345 | 0 | 0 | 0 | Installation of a third circuit from Berkswell. Alternatively for SCO only, re-energisation of Coventry South - Whitley 132kV circuits | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 4 | Billingborough 33/11kV Substation | 33kV | c | 2007 | 12 | 1.5892 | 1.5892 | 0 | 0 | 0 | 0 | 0 | 1.5892 | 0 | 0 | 0 | 0 | Installation of new 10km circuit from Great Hale to Billingborough and additional transformer at Billingborough | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 5 | Bourne 33/11kV Transformer Replacement | 33kV | a | 2007 | 9.5 | 0.83008 | 0.83008 | 0 | 0 | 0 | 0 | 0 | 0.10595 | 0.72414 | 0 | 0 | 0 | Uprating of 2 x 10/14.5MVA 33/11kV transformers with 12/24MVA units | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 6 | Brackley - Banbury group P2/6 SCO security | 132kV | c | 2013 | 189 | 0.41293 | 0.41293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20652 | 0.20641 | 0 | Installation of a third 132kV circuit. Costs split evenly across East and West. Wayleaves only in DPCR5, construction in DPCR6. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 7 | Brackley Town 33/11kV reinforcement | 33kV | a | 2011 | 16 | 2.581 | 2.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5489 | 1.0321 | 0 | Installation of Brackley local primary or strapping 33kV OHL circuits from Brackley Grid together. Installation of a new 33kV circuit (3km), uprating the existing transformers with 2 x 20/40MVA units and installation of a 2000A switchboard | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 8 | Bradwell Abbey 132/33kV reinforcement | 132kV | a | 2012 | 117 | 1.5508 | 1.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0345 | 0.5163 | 0 | 0 | Installation of a third grid transformer and third section of switchboard | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 9 | Braunstone, Jupiter & Groby Road 33/11kV reinforcement | 33kV | a | 2008 | 40 | 5.0111 | 5.0111 | 0 | 0 | 0 | 0 | 0 | 2.013 | 1.9655 | 1.0326 | 0 | 0 | Installation of new 40MVA 33/11kV primary on Hinckley Rd reserve site. Modification of 11kV circuits to enable load transfers. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 10 | Burton 132/33kV transformer change | 132kV | a | 2010 | 58.5 | 2.0647 | 2.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 1.0321 | 0 | Uprating the existing 132/33kV transformers with 2 x 90MVA units. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 11 | Cannon Street 33/11kV reinforcement | 33kV | a | 2012 | 39 | 4.9549 | 4.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9619 | 2.993 | 0 | Installation of a 132/11kV primary at Wellingborough Grid to transfer demand off Cannon Street. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 12 | Caythorpe 33/11kV | 33kV | a | 2012 | 13.15 | 0.20829 | 0.20829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20829 | Uprating transformer T1 (10.85MVA) with 24MVA transformer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 13 | Clifton 33/11kV reinforcement | 33kV | a | 2012 | 24 | 1.4454 | 1.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 0.41282 | 0 | Installation of a third 33kV circuit and a third 33/11kV 24MVA transformer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 14 | Coalville 33/11kV transformer change | 33kV | a | 2008 | 25 | 1.0595 | 1.0595 | 0 | 0 | 0 | 0 | 0 | 1.0595 | 0 | 0 | 0 | 0 | Uprating transformers for larger units. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 15 | Colwick 33/11kV reinforcement | 33kV | a | 2010 | 35.2 | 2.0671 | 2.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0345 | 1.0326 | 0 | 0 | Installation of a third 33kV circuit from Notts East and a third 33/11kV 40MVA transformer. Reconfiguration of Cotgrave 33kV interconnection. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 16 | Copsewood 33/11kv reinforcement | 33kV | a | 2012 | 16 | 4.0434 | 4.0434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 1.0321 | 1.9788 | Installation of 40MVA 33kV circuits, transformers and switchgear or installation of a 33/11kV 24MVA primary at Binley. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 17 | Coventry - Rugby 132kV cct reinforcement | 132kV | c | 2012 | 35 | 3.9275 | 3.9275 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9655 | 1.9619 | 0 | 0 | Transfer of Hinckley to Enderby GSP using the disconnected CA line. Refurbishment of CA1&2. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 18 | Coventry South 33/11kV Reinforcement | 33kV | a | 2010 | 16 | 1.5508 | 1.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0345 | 0.5163 | 0 | 0 | Uprating transformers with 20/40 33/11kV units or 30MVA 132/11kV units. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 19 | Dillotford Avenue 33/11kV Reinforcement | 33kV | a | 2013 | 18.6 | 2.5942 | 2.5942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0321 | 1.5622 | Uprating 33kV circuits with 40MVA rated cables and uprating transformers | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 20 | Farndon Road 33kV switchgear reconfiguration | 33kV | g | 2014 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switchgear reconfiguration | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 21 | Field Street T3 overload | 33kV | a | 2010 | 15 | 0.10345 | 0.10345 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10345 | 0 | 0 | 0 | Installation of auto opening scheme on the T2-T3 bus section for the loss of T1 or T2, or transfer load to Kettering North at 11kV or Uprate transformer T3. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 22 | Fiskerton 33/11kV reinforcement | 33kV | a | 2014 | 13.15 | 0.52073 | 0.52073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52073 | Uprating existing transformers with 2 x 12/24 MVA units. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 23 | Gresley - Moira - Ashby - Woodville - Willesley ccts | 33kV | b | 2014 | 27 | 1.0415 | 1.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0415 | Installation of additional circuits from Gresley & splitting existing circuits. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 24 | Hatton 33/11kV reinforcement | 33kV | a | 2010 | 16 | 1.5517 | 1.5517 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5517 | 0 | 0 | 0 | Uprating the existing 2 x 24MVA transformers with 40MVA units and changing the 11kV switchboard. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 25 | Hawton SCO Reinforcement and BSP reinforcement | 132kV | a | 2014 | 90 | 3.541 | 3.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.541 | Replacement of circuit breakers at Staythorpe, additional transformer capacity and 132kV busbars. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 26 | Heanor 33/11kV reinforcement | 33kV | a | 2008 | 12 | 1.5642 | 1.5642 | 0 | 0 | 0 | 0 | 0 | 0.52973 | 1.0345 | 0 | 0 | 0 | Uprating of existing transformers with 20/40 33/11kV units and replacement of circuits 2 x 85m | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 27 | Heanor BSP reinforcement | 132kV | a | 2013 | 39 | 6.0132 | 6.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.993 | 3.0202 | Uprating existing 132/33kV transformer with 120MVA units at Heanor. Looping the 132kV circuit (3km) into Stanton with two new CBs. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 28 | Kenilworth 33/11kV Reinforcement | 33kV | a | 2010 | 24 | 1.047 | 1.047 | 0 | 0 | 0 | 0 | 0 | 0.52973 | 0.51724 | 0 | 0 | 0 | Installation of a new 33/11kV primary (North Kenilworth) to offload Kenilworth. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 29 | Kibworth 33/11kV transformer replacement | 33kV | a | 2008 | 13.1 | 1.047 | 1.047 | 0 | 0 | 0 | 0 | 0 | 0.52973 | 0.51724 | 0 | 0 | 0 | Uprating 33/11kV transformers with 24MVA units. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 30 | Leicester East - Salutation - Thurmaston 33kV circuit | 33kV | b | 2007 | 40 | 1.0326 | 1.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 0 | 0 | Installation of third and fourth circuits to remove tee-off radial circuits. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 31 | Lincoln 132/33kV reinforcement | 132kV | a | 2007 | 117 | 0.74163 | 0.74163 | 0 | 0 | 0 | 0 | 0 | 0.74163 | 0 | 0 | 0 | 0 | Installation of new third 132/33kV 90MVA transformer | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 32 | Lincoln BSP | 132kV | c | 2014 | 117 | 2.0735 | 2.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0321 | 1.0415 | Creation of 132kV cross bay | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 33 | Mackworth 33/11kV reinforcement | 33kV | a | 2012 | 24 | 1.239 | 1.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 0.20641 | 0 | Installation of a third 33kV circuit (3.5km) and a third transformer (12/24MVA). | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 34 | Middlefield/Barwell 33kV circuit reinforcement | 33kV | b | 2008 | 16 | 0.52973 | 0.52973 | 0 | 0 | 0 | 0 | 0 | 0.52973 | 0 | 0 | 0 | 0 | Overlaying short lower rated sections of 33kV circuits increasing the rating to 40MVA. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 35 | Millclose transformer and switchboard replacement | 33kV | a | 2008 | 7.5 | 0.84757 | 0.84757 | 0 | 0 | 0 | 0 | 0 | 0.84757 | 0 | 0 | 0 | 0 | Uprating 33/11kV transformer and 11kV switchboard | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 36 | Milton Keynes additional BSP - acquire site and 132kV route | 132kV | a | 2015 | 117 | 0.52073 | 0.52073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52073 | Phase 1 - Acquisition of a reserved BSP site on the north eastern edge of the city and a route to an appropriate GSP. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 37 | Mountsorrel / Syston 33kV ccts | 33kV | b | 2011 | 31 | 0.5163 | 0.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5163 | 0 | 0 | Extension of Syston - Mountsorrel 33kV circuit into mid point at Mountsorrel and Syston, installation of RMU and changeover scheme at each end | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 38 | Normanton 33/11kV reinforcement | 33kV | a | 2011 | 16 | 1.0335 | 1.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51724 | 0.5163 | 0 | 0 | Uprating 33/11kV transformers with 40MVA units. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 39 | Northampton 132kV reinforcement | 132kV | c | 2014 | 190 | 15.1341 | 15.1341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0271 | 4.025 | 7.0819 | Installation of fourth 132kV circuit from Grendon to Northampton. Reconfiguration of 132kV running arrangement. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 40 | Northampton West - Kingsthorpe 33kV circuit reinforcement | 33kV | b | 2008 | 10 | 0.2069 | 0.2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2069 | 0 | 0 | 0 | Installation of 33kV and 11kV switchgear to accommodate all the potential 33kV circuit outages | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 41 | Nottingham North BSP | 132kV | a | 2014 | 40 | 3.0202 | 3.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0202 | Installation of new 33/11kV substation in vicinity of BSP site (5km double circuit 33kV cable assumed) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 42 | Nott'm East - Colwick 33kV cct | 33kV | b | 2010 | 40 | 1.2498 | 1.2498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2498 | Installation of two new 40MVA cable circuits to tee point to create two direct circuits to Colwick (3km) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 43 | Olney 33/11kV reinforcement | 33kV | a | 2014 | 9.5 | 1.3539 | 1.3539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3539 | Uprating the existing 33/11kV transformer with 24MVA units and reinforcement of 33kV circuits | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 44 | Raunds 33/11kV reinforcement | 33kV | c | 2008 | 16 | 1.5892 | 1.5892 | 0 | 0 | 0 | 0 | 0 | 1.5892 | 0 | 0 | 0 | 0 | Installation of a new 40MVA 33kV circuit from Irthlingborough Grid. Uprate transformer with a 12/24MVA unit and install a 2nd 12/24MVA unit. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 45 | Raynesway 33/11kV Substation | 33kV | a | 2007 | 40 | 2.3308 | 2.3308 | 0 | 0 | 0 | 0 | 0 | 2.3308 | 0 | 0 | 0 | 0 | Installation of a new 33/11kV primary substation | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 46 | Ripley 33/11kV reinforcement | 33kV | a | 2011 | 21.75 | 2.4901 | 2.4901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0321 | 1.458 | Installation of a third 33kV circuit (6.4km) and a third transformer (12/24MVA). | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 47 | Rugby - Harbury 132kV circuit (Warwick & Harbury Security) | 132kV | c | 2008 | 190 | 4.1319 | 4.1319 | 0 | 0 | 0 | 0 | 0 | 4.1319 | 0 | 0 | 0 | 0 | Installation of a 132kV interconnector between Harbury and Rugby. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 48 | Rugby 132/33kV reinforcement | 132kV | a | 2010 | 117 | 1.9655 | 1.9655 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9655 | 0 | 0 | 0 | Installation of a third 132/33kV transformer or alternatively a 132/11kV double wound transformer at Rugby BSP. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 49 | Rushden 33/11kV reinforcement | 33kV | a | 2008 | 16 | 2.3993 | 2.3993 | 0 | 0 | 0 | 0 | 0 | 0.84757 | 1.5517 | 0 | 0 | 0 | Installation of 2 x 40MVA 33kV circuits from Irthlingborough Grid to Rushden and 2 x 20/40MVA 33/11kV transformers at Rushden OR Installation of a 40MVA 33kV cable circuit from Wellingborough - Little Irchester to pick up existing Little Irchester - Rushden 33kV line and uprating Little Irchester. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 50 | Salutation 33/6.6kV reinforcement | 33kV | a | 2013 | 0 | 0.20829 | 0.20829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20829 | Uprating 6.6kV network to 11kV to reduce demand on Salutation s/s. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 51 | Spondon - Stanton - Heanor - Annesley 132kV reinforcement | 132kV | j | 2015 | 99.8 | 4.3544 | 4.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1673 | 2.1871 | Looping 132kV circuit through Heanor, installation of 2 x 132kV circuit breakers at Heanor | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 52 | Spondon 33/11kV reinforcement | 33kV | a | 2010 | 24 | 0.52073 | 0.52073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52073 | Installation of a third transformer (20/40MVA). Co-ordination with 11kV and 33kV switchgear replacements. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 53 | Stamford 132/33/11kV reinforcement | 33kV | a | 2010 | 16 | 1.047 | 1.047 | 0 | 0 | 0 | 0 | 0 | 0.52973 | 0.51724 | 0 | 0 | 0 | Uprating 33/11kV transformers with 40MVA units | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 54 | Stoke Bardolph - New GSP | 132kV | b | 2011 | 117 | 30.6576 | 30.0901 | 0 | 0 | 0 | 0 | 0.5675 | 1.0595 | 10.0345 | 11.9782 | 7.018 | 0 | Installation of new GSP to support Ratcliffe picking up Nottingham East on new 132kV cable and new OHL for new BSP to pick up Notts North. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 55 | Stony Stratford - Buckingham - Wicken - Towcester circuit reinforcement | 33kV | b | 2013 | 15 | 0.72244 | 0.72244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72244 | 0 | Reinforcement/rebuild/reconfiguration of the network required to increase the thermal rating. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 56 | Stony Stratford - Shenley Wood - Eldergate circuit reinforcement | 33kV | b | 2008 | 24 | 0.63568 | 0.63568 | 0 | 0 | 0 | 0 | 0 | 0.63568 | 0 | 0 | 0 | 0 | Installation of a new 40 MVA circuit from Stony Stratford to split the Shenley Wood / Eldergate circuits | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 57 | Syston 33/11kV reinforcement | 33kV | f | 2012 | 0 | 1.239 | 1.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 0.20641 | 0 | Installation of capacitors | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 58 | Talbot Street 33/11kV reinforcement | 33kV | a | 2010 | 24 | 1.4473 | 1.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93103 | 0.5163 | 0 | 0 | Installation of third 33/11kV 24MVA transformer and new 33kV circuit to Nottingham (4km) BSP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 59 | Tamworth Grid 132/33kV Tamworth Town 132/33kV reinforcement | 132kV | c | 2010 | 40 | 0.2069 | 0.2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2069 | 0 | 0 | 0 | Extension of 40MVA interconnector to be selectable to both sections of the 33kV switchboard at Tamworth Grid, connection to spare CB. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 60 | Walton 33/11kV | 33kV | C | 2009 | 10 | 0.52973 | 0.52973 | 0 | 0 | 0 | 0 | 0 | 0.52973 | 0 | 0 | 0 | 0 | Installation of additional 33/11kV 10MVA transformer and associated switchgear | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 61 | Warwick - Campion Hills - Tee Princethorpe 33kV circuit Reinforcement | 33kV | b | 2014 | 4 | 0.20829 | 0.20829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20829 | Increasing 11kV interconnection and application of sequence scheme to transfer demand away. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 62 | Watnall / Kimberley New Primary Substation | 33kV | a | 2007 | 40 | 4.2075 | 3.0725 | 0 | 0 | 0 | 0 | 1.135 | 3.0725 | 0 | 0 | 0 | 0 | Installation of new 33/11kV substation and 33kV circuits | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 63 | Wellesbourne 33/11kV New Primary Substation | 33kV | b | 2014 | 24 | 1.9788 | 1.9788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9788 | Following installation of Warwick West, decommissioning Banbury Rd and extending existing dual 33kV circuits to a reserve site at Wellesbourne. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 64 | West Burton - Lincoln 132kV DC OHL | 132kV | b | 2012 | 75 | 6.0132 | 6.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.993 | 3.0202 | Uprating 132kV overhead line | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 65 | West Burton GSP - 3rd SGT | 132kV | c | 2013 | 240 | 1.0321 | 1.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0321 | 0 | Installation of a third SGT and a bus-section at West Burton GSP. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 66 | Westville 33/11kV | 33kV | a | 2013 | 24 | 3.6127 | 3.6127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0326 | 2.5801 | 0 | Installation of a new 33/11kV substation and 33kV single circuit to Hucknall (3km) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 67 | Wigston Magna 33/11kV reinforcement | 33kV | a | 2008 | 32 | 1.5767 | 1.5767 | 0 | 0 | 0 | 0 | 0 | 1.0595 | 0.51724 | 0 | 0 | 0 | Installation of a third 33kV circuit and third 33/11kV 40MVA transformer. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 68 | Willington - Winster - Uttoxeter 132kV reinforcement | 132kV | c | 2010 | 181 | 3.5103 | 3.5103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4782 | 1.0321 | 0 | Unstitching tee (by cabling to Willington GSP) and refurbishment of both circuits (23km Uttoxeter & 35km Winster). | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 69 | Winster - Longcliffe | 33kV | b | 2011 | 27 | 0.20652 | 0.20652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20652 | 0 | 0 | Installation of new single 40MVA, 33kV circuit (4km ohl) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total |  |  |  | 3262.75 | 168.7247 | 167.0222 | 0 | 0 | 0 | 0 | 1.7025 | 24.2618 | 30 | 37.2769 | 36.7412 | 38.7423

## FBPQ LR6
Main Forecast Business Plan DPCR5 |  |  |  |  | Index
LR6 - Fault levels
Fault level system measures
|  |  | As at 31st March 2010 |  |  | As at 31st March 2015
|  |  | 132kV | EHV | HV | 132kV | EHV | HV
| No. of switchboards |  | 50 | 175 | 411 | 51 | 177 | 420
| No. of switchboards @ >95% of F.L. |  | 5 | 12 | 32 | 5 | 10 | 30
| No. of switchboards having fault level 'operational restrictions' |  | 5 | 12 | 32 | 5 | 10 | 30
Number of fault level schemes
| No. of schemes |  | DPCR4 |  |  | DPCR5
|  |  | 132kV | EHV | HV | 132kV | EHV | HV
| Switchboards |  | 0 | 0 | 0 | 1 | 3 | 3
| Transformers |  | 0 | 0 | 0 | 0 | 0 | 0
| Other |  | 0 | 0 | 0 | 0 | 0 | 0
Fault level reinforcement
|  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m)
Fault level reinforcement:
| LV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV | 0 | 0 | 0.79758 | 0 | 0 | 0.52973 | 0 | 0 | 0.72244 | 0 | 0.79758 | 0 | 0.79758 | 1.2522 | 57%
| EHV | 0 | 0 | 0.79758 | 2.4541 | 0.66653 | 3.6022 | 0.72414 | 1.0326 | 1.6513 | 0 | 0.79758 | 3.1206 | 3.9182 | 7.0102 | 78.91%
| 132kV | 0 | 0 | 2.0936 | 2.7888 | 4.2214 | 0 | 0.51724 | 0.5163 | 0 | 0 | 2.0936 | 7.0101 | 9.1038 | 1.0335 | -88.65%
| Total expenditure | 0 | 0 | 3.6888 | 5.2429 | 4.8879 | 4.1319 | 1.2414 | 1.5489 | 2.3737 | 0 | 3.6888 | 10.1308 | 13.8195 | 9.2959 | -32.73%

## FBPQ NL1
Main Forecast Business Plan DPCR5 |  |  |  |  | Index
NL1 - Condition based expenditure
Total condition based replacement
| Asset Categories |  | DPCR 4 |  |  |  |  | DPCR 5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| Metered LV Services | Overhead | 0.29921 | 0.29908 | 1.0977 | 4.021 | 2.337 | 1.9104 | 1.8662 | 1.863 | 1.9659 | 1.9833 | 1.696 | 6.358 | 8.054 | 9.5887 | 19.06%
|  | Underground | 1.6955 | 2.3926 | 3.5924 | 0.33509 | 0.77899 | 1.2736 | 1.3478 | 1.449 | 1.6555 | 1.7745 | 7.6805 | 1.1141 | 8.7946 | 7.5003 | -14.72%
| Un-metered LV Services | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV System | Overhead mains | 0.39894 | 0.49846 | 0.69852 | 4.9146 | 4.7853 | 1.2736 | 1.2441 | 1.3455 | 1.3451 | 1.357 | 1.5959 | 9.6998 | 11.2958 | 6.5652 | -41.88%
|  | Underground mains | 1.3963 | 2.4923 | 3.9916 | 0.33509 | 0.77899 | 0.84905 | 0.82942 | 1.242 | 1.552 | 1.7745 | 7.8802 | 1.1141 | 8.9942 | 6.247 | -30.54%
|  | Switchgear (incl other plant & equipment) | 0.59842 | 0.89723 | 1.1975 | 0.55848 | 1.1128 | 0.84905 | 0.93309 | 1.035 | 1.1381 | 1.2526 | 2.6931 | 1.6713 | 4.3644 | 5.2079 | 19.32%
| HV | Overhead lines | 2.7926 | 2.7914 | 2.7941 | 11.728 | 10.2382 | 6.474 | 5.9096 | 5.5889 | 5.2768 | 5.2192 | 8.3781 | 21.9662 | 30.3443 | 28.4684 | -6.182%
|  | Underground cables | 1.496 | 1.9938 | 3.0935 | 0.55848 | 1.0016 | 1.0613 | 1.1404 | 1.242 | 1.2416 | 1.4614 | 6.5833 | 1.56 | 8.1434 | 6.1467 | -24.52%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 3.8897 | 6.48 | 6.5861 | 4.3561 | 6.0094 | 6.8985 | 7.6721 | 8.1763 | 9.1051 | 8.3508 | 16.9558 | 10.3655 | 27.3213 | 40.2027 | 47.15%
|  | Transformers | 0 | 0.89723 | 1.1975 | 0.67017 | 1.7806 | 1.1674 | 1.2441 | 1.3455 | 1.6555 | 1.8789 | 2.0947 | 2.4507 | 4.5454 | 7.2914 | 60.41%
|  | Substation | 0.89762 | 2.3926 | 2.2951 | 1.5637 | 2.5596 | 1.2736 | 1.2441 | 1.242 | 1.2416 | 1.2526 | 5.5854 | 4.1233 | 9.7087 | 6.2539 | -35.58%
| EHV | Overhead lines | 0.099736 | 0.49846 | 0.99789 | 3.4625 | 0.89028 | 2.0165 | 6.428 | 2.3804 | 12.209 | 7.4113 | 1.5961 | 4.3528 | 5.9489 | 30.4453 | 411.8%
|  | Underground cables | 1.496 | 1.3957 | 1.896 | 0 | 1.1128 | 0 | 0 | 5.0714 | 3.104 | 0 | 4.7877 | 1.1128 | 5.9006 | 8.1754 | 38.55%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.29921 | 0.89723 | 1.1975 | 1.117 | 1.0016 | 1.6981 | 2.6956 | 4.8644 | 3.9317 | 6.8894 | 2.3939 | 2.1185 | 4.5124 | 20.0792 | 345%
|  | Transformers | 0.19947 | 0.89723 | 0.49894 | 0.67017 | 0.55642 | 0.74291 | 1.8662 | 2.6909 | 2.6901 | 0.73069 | 1.5956 | 1.2266 | 2.8222 | 8.7209 | 209%
|  | Substation | 0.19947 | 1.4954 | 0.99789 | 2.2339 | 2.2257 | 0.31839 | 0.10368 | 0.20699 | 0.10347 | 0.20877 | 2.6927 | 4.4596 | 7.1523 | 0.9413 | -86.84%
| 132kV | Overhead lines | 0.79789 | 0.89723 | 7.7835 | 8.3771 | 6.8997 | 2.7594 | 0 | 0.72448 | 0 | 4.3842 | 9.4787 | 15.2768 | 24.7555 | 7.868 | -68.22%
|  | Underground cables | 2.9921 | 0.29908 | 0 | 0 | 0.55642 | 1.2736 | 5.7022 | 6.8308 | 9.8293 | 9.9165 | 3.2912 | 0.55642 | 3.8476 | 33.5525 | 772%
|  | Submarine cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 2.8923 | 1.8942 | 0.19958 | 0 | 4.674 | 12.7357 | 11.9229 | 6.8308 | 3.8283 | 3.8622 | 4.9861 | 4.674 | 9.66 | 39.1799 | 305.6%
|  | Transformers | 2.0945 | 0.79754 | 0 | 0 | 2.1144 | 2.0165 | 2.4883 | 1.9664 | 1.9659 | 0 | 2.892 | 2.1144 | 5.0064 | 8.437 | 68.53%
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0.19526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19526 | 0
| Total non-load replacement (£m) |  | 24.535 | 30.2067 | 40.1152 | 44.9014 | 51.4137 | 46.7866 | 54.6379 | 56.0955 | 63.8388 | 59.708 | 94.8569 | 96.3151 | 191.172 | 281.0668 | 47.02%
Proactive condition based replacement (non fault)
| Asset Categories |  | DPCR 4 2005/06: DPCR 4; DPCR 5 2010/11: DPCR 5 | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| Metered LV Services | Overhead | 0.29921 | 0.29908 | 1.0977 | 4.021 | 2.337 | 1.9104 | 1.8662 | 1.863 | 1.9659 | 1.9833 | 1.696 | 6.358 | 8.054 | 9.5887 | 19.06%
|  | Underground | 1.6955 | 2.2929 | 3.4926 | 0.22339 | 0.66771 | 1.2736 | 1.3478 | 1.449 | 1.6555 | 1.7745 | 7.481 | 0.8911 | 8.3721 | 7.5003 | -10.41%
| Un-metered LV Services | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV System | Overhead mains | 0.39894 | 0.49846 | 0.69852 | 4.9146 | 4.7853 | 1.2736 | 1.2441 | 1.3455 | 1.3451 | 1.357 | 1.5959 | 9.6998 | 11.2958 | 6.5652 | -41.88%
|  | Underground mains | 1.3963 | 2.3926 | 3.8918 | 0.22339 | 0.66771 | 0.84905 | 0.82942 | 1.1385 | 1.4485 | 1.6702 | 7.6807 | 0.8911 | 8.5718 | 5.9356 | -30.75%
|  | Switchgear (incl other plant & equipment) | 0.19947 | 0.29908 | 0.39916 | 0.1117 | 0.66771 | 0.42452 | 0.51839 | 0.62098 | 0.72427 | 0.83508 | 0.8977 | 0.7794 | 1.6771 | 3.1232 | 86.23%
| HV | Overhead lines | 2.6929 | 2.6917 | 2.6943 | 11.6163 | 10.1269 | 6.3678 | 5.8059 | 5.4854 | 5.1733 | 5.1148 | 8.0789 | 21.7432 | 29.8221 | 27.9473 | -6.287%
|  | Underground cables | 1.496 | 1.9938 | 3.0935 | 0.55848 | 1.0016 | 1.0613 | 1.1404 | 1.242 | 1.2416 | 1.4614 | 6.5833 | 1.56 | 8.1434 | 6.1467 | -24.52%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 3.2913 | 5.4831 | 5.5882 | 3.4625 | 5.1191 | 6.1556 | 6.9464 | 7.4518 | 8.3808 | 7.6201 | 14.3625 | 8.5817 | 22.9442 | 36.5546 | 59.32%
|  | Transformers | 0 | 0.39877 | 0.49894 | 0.33509 | 1.4467 | 0.84905 | 0.93309 | 1.035 | 1.2416 | 1.4614 | 0.89771 | 1.7818 | 2.6795 | 5.5201 | 106%
|  | Substation | 0.69815 | 1.9938 | 1.896 | 1.2286 | 2.2257 | 0.95518 | 0.93309 | 0.93148 | 0.9312 | 0.93946 | 4.588 | 3.4543 | 8.0423 | 4.6904 | -41.68%
| EHV | Overhead lines | 0.099736 | 0.49846 | 0.99789 | 3.4625 | 0.89028 | 2.0165 | 6.428 | 2.3804 | 12.209 | 7.4113 | 1.5961 | 4.3528 | 5.9489 | 30.4453 | 411.8%
|  | Underground cables | 1.496 | 1.3957 | 1.896 | 0 | 1.1128 | 0 | 0 | 5.0714 | 3.104 | 0 | 4.7877 | 1.1128 | 5.9006 | 8.1754 | 38.55%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.29921 | 0.79754 | 1.0977 | 1.0053 | 0.89028 | 1.592 | 2.5919 | 4.7609 | 3.8283 | 6.785 | 2.1944 | 1.8955 | 4.09 | 19.558 | 378.2%
|  | Transformers | 0.099736 | 0.39877 | 0.19958 | 0.33509 | 0.22257 | 0.53065 | 1.6588 | 2.4839 | 2.4832 | 0.52192 | 0.69808 | 0.55766 | 1.2557 | 7.6785 | 511.5%
|  | Substation | 0.19947 | 1.4954 | 0.99789 | 2.2339 | 2.2257 | 0.31839 | 0.10368 | 0.20699 | 0.10347 | 0.20877 | 2.6927 | 4.4596 | 7.1523 | 0.9413 | -86.84%
| 132kV | Overhead lines | 0.79789 | 0.89723 | 7.7835 | 8.3771 | 6.8997 | 2.7594 | 0 | 0.72448 | 0 | 4.3842 | 9.4787 | 15.2768 | 24.7555 | 7.868 | -68.22%
|  | Underground cables | 2.9921 | 0.29908 | 0 | 0 | 0.55642 | 1.2736 | 5.7022 | 6.8308 | 9.8293 | 9.9165 | 3.2912 | 0.55642 | 3.8476 | 33.5525 | 772%
|  | Submarine cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 2.8923 | 1.8942 | 0.19958 | 0 | 4.674 | 12.7357 | 11.9229 | 6.8308 | 3.8283 | 3.8622 | 4.9861 | 4.674 | 9.66 | 39.1799 | 305.6%
|  | Transformers | 2.0945 | 0.79754 | 0 | 0 | 2.1144 | 2.0165 | 2.4883 | 1.9664 | 1.9659 | 0 | 2.892 | 2.1144 | 5.0064 | 8.437 | 68.53%
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0.19526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19526 | 0
| Total proactive condition based replacement (£m) |  | 23.1387 | 26.8172 | 36.5228 | 42.109 | 48.6315 | 44.5579 | 52.4607 | 53.8186 | 61.4591 | 57.3071 | 86.4787 | 90.7406 | 177.2193 | 269.6034 | 52.13%
Reactive condition-based replacement (fault)
| Asset Categories |  | DPCR 4 2005/06: DPCR 4; DPCR 5 2010/11: DPCR 5 | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| Metered LV Services | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground | 0 | 0.099692 | 0.099789 | 0.1117 | 0.11128 | 0 | 0 | 0 | 0 | 0 | 0.19948 | 0.22298 | 0.42246 | 0 | -100%
| Un-metered LV Services | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV System | Overhead mains | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground mains | 0 | 0.099692 | 0.099789 | 0.1117 | 0.11128 | 0 | 0 | 0.1035 | 0.10347 | 0.10438 | 0.19948 | 0.22298 | 0.42246 | 0.31135 | -26.3%
|  | Switchgear (incl other plant & equipment) | 0.39894 | 0.59815 | 0.79831 | 0.44678 | 0.44514 | 0.42452 | 0.41471 | 0.41399 | 0.41387 | 0.41754 | 1.7954 | 0.89192 | 2.6873 | 2.0846 | -22.43%
| HV | Overhead lines | 0.099736 | 0.099692 | 0.099789 | 0.1117 | 0.11128 | 0.10613 | 0.10368 | 0.1035 | 0.10347 | 0.10438 | 0.29922 | 0.22298 | 0.5222 | 0.52116 | -0.1993%
|  | Underground cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.59842 | 0.99692 | 0.99789 | 0.89356 | 0.89028 | 0.74291 | 0.72574 | 0.72448 | 0.72427 | 0.73069 | 2.5932 | 1.7838 | 4.3771 | 3.6481 | -16.65%
|  | Transformers | 0 | 0.49846 | 0.69852 | 0.33509 | 0.33385 | 0.31839 | 0.31103 | 0.31049 | 0.41387 | 0.41754 | 1.197 | 0.66894 | 1.8659 | 1.7713 | -5.07%
|  | Substation | 0.19947 | 0.39877 | 0.39916 | 0.33509 | 0.33385 | 0.31839 | 0.31103 | 0.31049 | 0.3104 | 0.31315 | 0.9974 | 0.66894 | 1.6663 | 1.5635 | -6.173%
| EHV | Overhead lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0 | 0.099692 | 0.099789 | 0.1117 | 0.11128 | 0.10613 | 0.10368 | 0.1035 | 0.10347 | 0.10438 | 0.19948 | 0.22298 | 0.42246 | 0.52116 | 23.36%
|  | Transformers | 0.099736 | 0.49846 | 0.29937 | 0.33509 | 0.33385 | 0.21226 | 0.20735 | 0.20699 | 0.20693 | 0.20877 | 0.89756 | 0.66894 | 1.5665 | 1.0423 | -33.46%
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV | Overhead lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Submarine cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total reactive condition based replacement (£m) |  | 1.3963 | 3.3895 | 3.5924 | 2.7924 | 2.7821 | 2.2287 | 2.1772 | 2.2769 | 2.3797 | 2.4008 | 8.3782 | 5.5745 | 13.9527 | 11.4635 | -17.84%
Overhead line refurbishment / replacement
| Asset Categories |  | DPCR 4 2005/06: DPCR 4; DPCR 5 2010/11: DPCR 5 | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/015 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| LV Mains | Refurbishment | 0 | 0 | 0 | 0.22339 | 1.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5588 | 1.5588 | 0 | -100%
|  | Full rebuild | 0.099736 | 0.099692 | 0.099789 | 0.89356 | 0.55642 | 0.74291 | 0.72574 | 0.82798 | 0.82773 | 0.83508 | 0.29922 | 1.45 | 1.7492 | 3.9594 | 126.4%
|  | Undergrounding | 0.29921 | 0.39877 | 0.59873 | 3.7976 | 2.8934 | 0.53065 | 0.51839 | 0.51749 | 0.51733 | 0.52192
|  | Covered Conductor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total OHL expenditure (£m) | 0.39894 | 0.49846 | 0.69852 | 4.9146 | 4.7853 | 1.2736 | 1.2441 | 1.3455 | 1.3451 | 1.357 | 1.5959 | 9.6998 | 11.2958 | 6.5652 | -41.88%
| HV | Refurbishment | 1.2966 | 1.296 | 1.2973 | 5.5848 | 5.1191 | 2.2287 | 1.9699 | 1.863 | 1.7589 | 1.7745 | 3.8898 | 10.7039 | 14.5937 | 9.595 | -34.25%
|  | Full rebuild | 0.59842 | 0.59815 | 0.59873 | 2.4573 | 3.5611 | 4.1391 | 3.8361 | 3.6224 | 3.4144 | 3.3403 | 1.7953 | 6.0184 | 7.8137 | 18.3523 | 134.9%
|  | Undergrounding | 0.79789 | 0.79754 | 0.79831 | 3.5742 | 1.4467 | 0 | 0 | 0 | 0 | 0
|  | Covered Conductor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total OHL expenditure (£m) | 2.6929 | 2.6917 | 2.6943 | 11.6163 | 10.1269 | 6.3678 | 5.8059 | 5.4854 | 5.1733 | 5.1148 | 8.0789 | 21.7432 | 29.8221 | 27.9473 | -6.287%
| EHV - Pole line | Refurbishment | 0.099736 | 0.49846 | 0.99789 | 3.4625 | 0.66771 | 0 | 0.10368 | 0.41399 | 0 | 0.20877 | 1.5961 | 4.1303 | 5.7263 | 0.72644 | -87.31%
|  | Full rebuild | 0 | 0 | 0 | 0 | 0 | 1.8042 | 5.9096 | 1.9664 | 11.0709 | 6.8894 | 0 | 0 | 0 | 27.6406 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0.22257 | 0 | 0.41471 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV - Tower line | Fittings only | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Reconductoring | 0 | 0 | 0 | 0 | 0 | 0.21226 | 0 | 0 | 0.10347 | 0.31315 | 0 | 0 | 0 | 0.62888 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20693 | 0
|  | Tower Refurbishment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82773 | 0
| EHV Total | Total OHL expenditure (£m) | 0.099736 | 0.49846 | 0.99789 | 3.4625 | 0.89028 | 2.0165 | 6.428 | 2.3804 | 12.209 | 7.4113 | 1.5961 | 4.3528 | 5.9489 | 30.4453 | 411.8%
| 132kV - Pole Line | Refurbishment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Full rebuild | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV - Tower line | Fittings only | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Reconductoring | 0.79789 | 0.89723 | 7.7835 | 8.3771 | 3.7837 | 2.1226 | 0 | 0.72448 | 0 | 4.3842 | 9.4787 | 12.1608 | 21.6395 | 7.2312 | -66.58%
|  | Undergrounding | 0 | 0 | 0 | 0 | 3.116 | 0 | 0 | 0 | 0 | 0
|  | Tower Refurbishment | 0 | 0 | 0 | 0 | 0 | 0.63678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63678 | 0
| 132 kV Total | Total OHL expenditure (£m) | 0.79789 | 0.89723 | 7.7835 | 8.3771 | 6.8997 | 2.7594 | 0 | 0.72448 | 0 | 4.3842 | 9.4787 | 15.2768 | 24.7555 | 7.868 | -68.22%

## FBPQ C2
Main Forecast Business Plan DPCR5 |  |  |  | Index
C2 - Unit costs
|  |  | Asset categories | Units | New build |  | Replacement
[5 empty] | Direct costs | Cost including indirects (absorbed costs in T2A) | Direct costs | Cost including indirects (absorbed costs in T2A) | TOTAL
[5 empty] | (£k) | (£k) | (£k) | (£k) | (£k)
LV Network
Overhead lines
|  |  | LV Main (OHL) | km | 26.001 | 2.7995 | 35.096 | 4.4139 | 39.5099
|  |  | LV Service (OHL) | Each | 0.214 | 0.023041 | 0.428 | 0.053828 | 0.48183
Overhead lines - Support
|  |  | LV Support | Each | 0 | 0 | 0 | 0 | 0
Underground cables
|  |  | LV Main (UG Consac) | km | 103.469 | 11.1404 | 107 | 13.457 | 120.457
|  |  | LV Main (UG Plastic) | km | 103.469 | 11.1404 | 107 | 13.457 | 120.457
|  |  | LV Main (UG Paper) | km | 103.469 | 11.1404 | 107 | 13.457 | 120.457
|  |  | LV Service (UG) | Each | 1.0598 | 0.11411 | 1.4308 | 0.17995 | 1.6108
Switchgear
|  |  | LV Pillar (ID) | Each | 3.424 | 0.36866 | 4.815 | 0.60557 | 5.4206
|  |  | LV Pillar (OD) | Each | 3.424 | 0.36866 | 4.815 | 0.60557 | 5.4206
|  |  | LV Board (WM) | Each | 3.424 | 0.36866 | 4.815 | 0.60557 | 5.4206
|  |  | LV UGB | Each | 3.103 | 0.3341 | 4.066 | 0.51137 | 4.5774
|  |  | LV Fuses (PM) | Each
|  |  | LV Fuses (TM) | Each
HV network
Overhead lines
|  |  | 6.6/11 kV OHL (Open) | km | 30.388 | 3.2719 | 36.273 | 4.5619 | 40.8349
|  |  | 6.6/11 kV OHL (Covered) | km | 30.388 | 3.2719 | 36.273 | 4.5619 | 40.8349
|  |  | 20 kV OHL (Open) | km | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV OHL (Covered) | km | 0 | 0 | 0 | 0 | 0
Overhead lines - Support
|  |  | 6.6/11 kV Support | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV Support | Each | 0 | 0 | 0 | 0 | 0
Underground cables (kms)
|  |  | 6.6/11kV UG Cable | km | 66.768 | 7.1889 | 71.155 | 8.9489 | 80.1039
|  |  | 20kV UG Cable | km | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  | HV Sub Cable | km | 0 | 0 | 0 | 0 | 0
Switchgear
|  |  | 6.6/11 kV CB (PM) | Each | 11.235 | 1.2097 | 11.77 | 1.4803 | 13.2503
|  |  | 6.6/11 kV CB (GM) | Each | 24.182 | 2.6037 | 26.001 | 3.2701 | 29.2711
|  |  | 6.6/11 kV Switch (PM) | Each | 0.963 | 0.10369 | 1.391 | 0.17494 | 1.5659
|  |  | 6.6/11 kV Switch (GM) | Each | 3.852 | 0.41474 | 4.387 | 0.55174 | 4.9387
|  |  | 6.6/11 kV RMU | Each | 12.947 | 1.394 | 13.803 | 1.736 | 15.539
|  |  | 6.6/11 kV Switchgear - Other (PM) | Each
|  |  | 6.6/11 kV Switchgear - Other (GM) | Each
|  |  | 20 kV CB (PM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV CB (GM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV Switch (PM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV Switch (GM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV RMU | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV Switchgear - Other (PM) | Each
|  |  | 20 kV Switchgear - Other (GM) | Each
Transformers
|  |  | 6.6/11 kV Transformer (PM) | Each | 3.103 | 0.3341 | 3.103 | 0.39025 | 3.4933
|  |  | 6.6/11 kV Transformer (GM) | Each | 9.309 | 1.0023 | 10.058 | 1.265 | 11.323
|  |  | 20 kV Transformer (PM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 20 kV Transformer (GM) | Each | 0 | 0 | 0 | 0 | 0
EHV Network
Overhead lines
|  |  | 33kV OHL (Pole Line) | km | 73.723 | 7.9377 | 82.818 | 10.4158 | 93.2338
|  |  | 33kV OHL (Tower Line) | km | 116.416 | 12.5344 | 131.931 | 16.5925 | 148.5235
|  |  | 66kV OHL (Pole Line) | km | 147.125 | 15.8408 | 156.22 | 19.6473 | 175.8673
|  |  | 66kV OHL (Tower Line) | km | 147.125 | 15.8408 | 156.22 | 19.6473 | 175.8673
Overhead lines - Support
|  |  | 33kV Pole | Each | 0 | 0 | 0 | 0 | 0
|  |  | 33kV Tower | Each | 0 | 0 | 0 | 0 | 0
|  |  | 66kV Pole | Each | 0 | 0 | 0 | 0 | 0
|  |  | 66kV Tower | Each | 0 | 0 | 0 | 0 | 0
Underground cables (kms)
|  |  | 33kV UG Cable (Non Pressurised) | km | 210.576 | 22.6725 | 216.354 | 27.2101 | 243.5641
|  |  | 33kV UG Cable (Oil) | km | 210.576 | 22.6725 | 216.354 | 27.2101 | 243.5641
|  |  | 33kV UG Cable (Gas) | km | 0 | 0 | 0 | 0 | 0
|  |  | 66kV UG Cable (Non Pressurised) | km | 1003.874 | 108.0863 | 1015.43 | 127.7073 | 1143.1373
|  |  | 66kV UG Cable (Oil) | km | 1003.874 | 108.0863 | 1015.43 | 127.7073 | 1143.1373
|  |  | 66kV UG Cable (Gas) | km | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  | EHV Sub Cable | km | 0 | 0 | 0 | 0 | 0
Switchgear
|  |  | 33 KV CB (ID) | Each | 152.796 | 16.4514 | 155.685 | 19.58 | 175.265
|  |  | 33 kV CB (OD) | Each | 152.796 | 16.4514 | 155.685 | 19.58 | 175.265
|  |  | 33 kV Switch (GM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 33 kV Switch (PM) | Each | 0 | 0 | 0 | 0 | 0
|  |  | 33 kV RMU | Each | 488.776 | 52.6261 | 495.303 | 62.2927 | 557.5957
|  |  | 33 kV Switchgear - Other | Each
|  |  | 66 KV CB (ID & OD) | Each | 575.981 | 62.0154 | 587.323 | 73.8657 | 661.1887
|  |  | 66 KV Switchgear - Other | Each
Transformers
|  |  | 33 kV Transformer (PM) | Each | 433.457 | 46.67 | 448.223 | 56.3716 | 504.5946
|  |  | 33 kV Transformer (GM) | Each | 446.404 | 48.0639 | 481.393 | 60.5432 | 541.9362
|  |  | 33 kV AuxiliaryTransfomer | Each
|  |  | 66 kV Transformer | Each | 1778.554 | 191.4954 | 1880.953 | 236.5614 | 2117.5144
|  |  | 66 kV AuxiliaryTransfomer | Each
132kV Network
Overhead lines
|  |  | 132kV OHL Conductor (Pole Line) | km | 549.552 | 59.1698 | 601.661 | 75.669 | 677.33
|  |  | 132kV OHL Conductor (Tower Line) | km | 929.83 | 100.114 | 1033.941 | 130.0354 | 1163.9764
Overhead lines - Support
|  |  | 132kV Pole | Each | 0 | 0 | 0 | 0 | 0
|  |  | 132kV Tower | Each | 0 | 0 | 0 | 0 | 0
|  |  | 132kV Fittings (Tower Line) | Each | 0 | 0 | 0 | 0 | 0
Underground cables (kms)
|  |  | 132kV UG Cable (Non Pressurised) | km | 1031.587 | 111.0701 | 1043.25 | 131.2062 | 1174.4562
|  |  | 132kV UG Cable (Oil) | km | 1031.587 | 111.0701 | 1043.25 | 131.2062 | 1174.4562
|  |  | 132kV UG Cable (Gas) | km | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  | 132 kV Sub Cable | km | 0 | 0 | 0 | 0 | 0
Switchgear
|  |  | 132 kV CB (ID & OD) | Each | 919.986 | 99.0541 | 931.221 | 117.1166 | 1048.3376
|  |  | 132 kV Switchgear (other) | Each
Transformers
|  |  | 132 kV Transformer | Each | 1796.53 | 193.4309 | 1880.953 | 236.5614 | 2117.5144
|  |  | 132 kV AuxiliaryTransfomer | Each
Tele-control / SCADA
Primary substation
|  |  | 132 kV/EHV RTU (PM) | Each
|  |  | 132 kV/EHV RTU (GM) | Each
Secondary substation
|  |  | HV RTU (PM) | Each
|  |  | HV RTU (GM) | Each
HV network switchgear
6.6/11 kV CB (GM)
|  |  | Primary | Each | 24.182 | 2.6037 | 26.001 | 3.2701 | 29.2711
|  |  | Distribution | Each | 6.099 | 0.65667 | 6.634 | 0.83434 | 7.4683
20 kV Switch (GM)
|  |  | Primary | Each | 0 | 0 | 0 | 0 | 0
|  |  | Distribution | Each | 0 | 0 | 0 | 0 | 0

## RRP 1.3
Regulatory Reporting Pack (RRP) |  |  |  | Index |  | CAUTION - THIS PACK DOES NOT BALANCE
2007/08
Electricity Distribution Industry Activity Costs - individual DNO input
|  | Cash typical costs (excluding disallowed related party margins) | [20 empty] | Atypical cash costs | Pension deficit payments | Metering | Excluded services & de minimis | Relevant distributed generation (less contributions) | IFI | Disallowed Related Party Margins | Statutory Depreciation | Network Rates | Transmission Exit Charges | Pension deficit repair payments by related parties (note 2) | Non activity costs and reconciling amounts (note 3) | Total Annual Operating & Capital Expenditure per Regulatory Accounts
|  | Direct activities | [5 empty] | Indirect activities
| Year ended | Load related new connections & reinforcement (net of contributions) | Non-load new & replacement assets (net of contributions) | Non-operational capex | Faults | Inspections, & Maintenance | Tree Cutting | Network Policy | Network Design & Engineering | Project Management | Engineering Mgt & Clerical Support | Control Centre | System Mapping - Cartographical | Customer Call Centre | Stores | Vehicles & Transport | IT & Telecoms | Property Mgt | HR & Non-operational Training | Health & Safety & Operational Training | Finance & Regulation | CEO etc
|  | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m
| 31 March 2008 | 46.4595 | 62.5317 | 2.3969 | 26.5144 | 11.6067 | 3.1209 | 0.63889 | 5.1306 | 2.2167 | 16.9396 | 4.43 | 1.5095 | 1.3239 | 1.5623 | 6.151 | 10.2401 | 4.5836 | 1.4398 | 2.0706 | 7.5445 | 1.6451 | 1.3215 | 9.5 | 0.79378 | 9.7514 | -8.3267e-16 | 1.0145 | 4.3033 | 41.9128 | 27.092 | 4.4 | -9.5 | 2.3543 | 313
| Adjustments on T4.3 | [33 empty] | 0
| 31 March 2008 | 46.4595 | 62.5317 | 2.3969 | 26.5144 | 11.6067 | 3.1209 | 0.63889 | 5.1306 | 2.2167 | 16.9396 | 4.43 | 1.5095 | 1.3239 | 1.5623 | 6.151 | 10.2401 | 4.5836 | 1.4398 | 2.0706 | 7.5445 | 1.6451 | 1.3215 | 9.5 | 0.79378 | 9.7514 | -8.3267e-16 | 1.0145 | 4.3033 | 41.9128 | 27.092 | 4.4 | -9.5 | 2.3543 | 313
| 31 March 2007 | 14.1513 | 41.9019 | 2.5347 | 29.3513 | 11.5199 | 5.8258 | 1.3252 | 3.7901 | 4.7917 | 16.9632 | 4.4093 | 1.8923 | 1.9938 | 1.5196 | 4.8615 | 13.53 | 4.2318 | 1.9208 | 2.2642 | 7.1645 | 1.8088 | 1.5637 | 0 | 5.3809 | 15.6992 | 0 | 0 | 1.8408 | 40.6025 | 26.1116 | 4.5663 | 0 | -5.7907 | 267.7259
| 31 March 2006 | 17.3947 | 35.0881 | 1.9915 | 27.1865 | 10.7806 | 3.2645 | 0.42117 | 7.2463 | 6.1037 | 11.6766 | 3.7007 | 1.9451 | 1.4675 | 2.0075 | 4.1312 | 7.0587 | 4.8947 | 1.2662 | 2.0034 | 6.7695 | 2.2294 | 5.8295 | 45.6 | 9.2172 | 8.651 | 0 | 0 | 0 | 42.3885 | 25.8639 | 4.7383 | -45.6 | -5.0463 | 250.27
Notes
| 1 | The individual activities are defined in the Electricity Distribution Price Control Review Price control cost reporting rules: Instructions and Guidance April 2008
| 2 | Pension deficit payments made by a related party and not charged in the regulatory accounts of the DNO
| 3 | Non-activity costs include Ofgem licence fee, Shetland Balancing Costs (SHEPD only), Scottish Electricity Settlements run-off (Scottish DNOs only) and proceeds of asset sales; and reconciling amounts, e.g. intra-group recharges treated as de minimis costs
| 4 | Total Annual Operating & Capital Expenditure per Regulatory Accounts has been adjusted, where appropriate, to include intangible fixed assets and customer contributions, the latter may be reported within Creditors as deferred income
| 5 | This information has not been audited.

## RRP 2.3
Regulatory Reporting Pack (RRP) |  |  | Index
2007/08
Inspections & Maintenance, Tree Cutting and Fault Costs
Memorandum Information - Scottish DNOs 132kV
|  |  | Inspections & Maintenance |  |  | Fault Costs |  | Inspections & Maintenance |  |  | Faults
|  |  |  | Cash typicals |  | Cash typicals | Atypicals
Inspection and Maintenance |  |  | Inspections | Maintenance | Total | Total | Total | Inspections | Maintenance | Total | Total
|  |  | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m
LV Services | Overhead |  | 0 | 0.36182 | 0.36182 | 0.44432 | 0
| Underground |  |  |  |  | 4.7953 | 0
LV System | Overhead Mains |  | 0.39718 | 0.11811 | 0.51529 | 1.1996 | 0.20707
| Underground Mains - Consac |  | 0.22966 | 0.11241 | 0.34208 | 0.0092384 | 0
| Underground Mains - Non Consac |  | 0 | 0 |  | 9.2963 | 0
| Switchgear (incl other plant & equipment) |  | 0 | 0 |  | 0.20111 | 0
HV | Overhead lines |  | 0.02645 | 0.32631 | 0.35276 | 1.9215 | 0.17396
| Underground Cables |  | 0 | 0.15633 | 0.15633 | 4.3444 | 0
| Switchgear, Transformers, Substation |  | 0.52096 | 3.756 | 4.2769 | 0.5505 | 0
EHV | Overhead lines |  | 0 | 0 | 0 | 0.45049 | 0
| Underground - Pressure assisted |  | 0 | 0 | 0 | 0.00012795 | 0
| Underground - Non Pressure assisted |  | 0 | 0 | 0 | 0.5069 | 0
| Switchgear, Transformers, Substation |  | 0.034253 | 0.54132 | 0.57557 | 0.00013595 | 0
132kV | Overhead lines |  | 0.1457 | 1.9379 | 2.0836 | 0.002784 | 0.0052674 | 0 | 0 | 0 | 0
| Underground - Pressure assisted |  | 0.097465 | 0.13436 | 0.23182 | 0.61959 | 0 | 0 | 0 | 0 | 0
| Underground - Non Pressure assisted |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Switchgear, Transformers, Substation |  | 0.2106 | 1.2009 | 1.4115 | 0.0015441 | 0 | 0 | 0 | 0 | 0
Submarine cables - all voltages |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non-QoS Faults | [5 empty] | 5.7302 | 0
Substation electricity |  |  |  | 0 | 0
Diesel generation costs (permanent emergency back up on islands) |  |  |  |  | 0
Third party cable damage - recoveries | [5 empty] | -2.2231
Dismantlement |  |  |  | 1.199 | 1.199
Total |  |  | 1.6623 | 9.8445 | 11.5067 | 27.8508 | 0.3863 | 0 | 0 | 0 | 0
|  |  | Fault costs allocated to Opex and Capex |  |  | Cash typicals | Atypicals
[6 empty] | £'m | £'m
|  |  | Fault opex |  |  | 7.6047 | 0.3863
|  |  | Fault capex |  |  | 20.2462 | 0
|  |  | Total Fault Costs |  |  | 27.8508 | 0.3863
|  | Tree Cutting | [5 empty] | Tree Cutting
[5 empty] | £'m |  |  |  |  | £'m
|  | LV |  |  | 2.6698 |  |  | 132kV |  | 0
|  | HV |  |  | 3.84
|  | EHV |  |  | 0.60219
|  | 132kV |  |  | 0.20886
|  | Total Tree Cutting |  |  | 7.3209

## RRP 2.4
Regulatory Reporting Pack (RRP) |  |  | Index
2007/08
NEW AND REPLACEMENT ASSETS (EXCL. FAULTS)
Load Related New Connections & Reinforcement
| Direct Costs only |  | New Connections (carried out by DNO/RP) | New Connections (carried out by Third Parties) | Customer Specific Reinforcement - Chargeable | Customer Specific Reinforcement - Non Chargeable | General Reinforcement | Fault Level Reinforcement | Non Relevant Distributed Generation | Total
|  |  | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m
| New Connections & Customer Specific Reinforcement: | [8 empty] | 0
| Connections provided at LV |  | 49.1 | 0 | 0 | 10 |  |  |  | 59.1
| Connections provided at HV |  | 24.91 | 0 | 0 | 7.25 |  |  |  | 32.16
| Connections provided at EHV |  | 0.44 | 0 | 0 | 0.2 |  |  |  | 0.64
| Connections provided at 132kV |  | 0 | 0 | 0 | 0 |  |  |  | 0
| General Reinforcement: | [8 empty] | 0
| LV System | [5 empty] | 1.3 | 0 |  | 1.3
| HV System | [5 empty] | 3.9 | 0.8 |  | 4.7
| EHV System | [5 empty] | 3.2174 | 0.82836 |  | 4.0457
| 132kV System | [5 empty] | 24.1 | 2.14 |  | 26.24
| Non Relevant Distributed Generation | [7 empty] | 0 | 0
| Total Direct Costs excluding Reallocations |  | 74.45 | 0 | 0 | 17.45 | 32.5174 | 3.7684 | 0 | 128.1857
| Direct Cost Reallocation |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| Total Costs including Reallocations |  | 74.45 | 0 | 0 | 17.45 | 32.5174 | 3.7684 | 0 | 128.1857
| Customer Contributions (-ve) |  | -81.8 | 0 | 0 |  |  |  | 0 | -81.8
| Total Costs less Capital Contributions |  | -7.35 | 0 | 0 | 17.45 | 32.5174 | 3.7684 | 0 | 46.3857
Non-load related replacement (Condition based)
Condition based
| Direct Costs only |  | Non-fault Related | Fault Related | Total
|  |  | £'m | £'m | £'m
| Metered LV Services | Overhead | 1.1213 | 0.010171 | 1.1315
|  | Underground | 3.5 | 0.1 | 3.6
| Un-metered LV Services | Overhead | 0 | 0 | 0
|  | Underground | 0 | 0 | 0
| LV System | Overhead Mains | 0.83169 | 0.007961 | 0.83965
|  | Underground Mains | 3.9067 | 0.10148 | 4.0082
|  | Switchgear (incl other plant & equipment) | 0.44802 | 0.84481 | 1.2928
| HV | Overhead lines | 2.8 | 0.1 | 2.9
|  | Underground Cables | 3.1076 | 0.020379 | 3.128
|  | Submarine | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 5.6127 | 1.0011 | 6.6138
|  | Transformers | 0.53103 | 0.70512 | 1.2362
|  | Substation | 1.9 | 0.4 | 2.3
| EHV | Overhead lines | 1.0244 | 0 | 1.0244
|  | Underground Cables | 1.9271 | 0.021755 | 1.9488
|  | Submarine | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 1.1254 | 0.1 | 1.2254
|  | Transformers | 0.2 | 0.3 | 0.5
|  | Substation | 1.0401 | 0.011384 | 1.0515
| 132kV | Overhead lines | 7.8472 | 0 | 7.8472
|  | Underground Cables | 0.038899 | 0 | 0.038899
|  | Submarine Cables | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.2 | 0 | 0.2
|  | Transformers | 0.046739 | 0 | 0.046739
|  | Substation | 0.027137 | 0.0039355 | 0.031072
| Total Non-load replacement |  | 37.236 | 3.7281 | 40.9641
| Customer Contributions (-ve) |  | 0 | 0 | 0
| Total Net Non-load replacement |  | 37.236 | 3.7281 | 40.9641
| Non-load related (other) |  | LV | HV | EHV | 132kV | Total
| Direct Costs only |  | £'m | £'m | £'m | £'m | £'m
| Quality of Service |  | 0.78155 | 7.02 | 0 | 0 | 7.8016
| Safety |  | 0.1737 | 0.35465 | 0.10272 | 0.11978 | 0.75085
| Environment |  | 0 | 0 | 0.11286 | 0 | 0.11286
| Visual Amenity |  | 0.024138 | 0.0013114 | 0 | 0 | 0.02545
| ESQCR |  | 0.11121 | 0.29513 | 0 | 0 | 0.40634
| Resilience |  | 0 | 0.018357 | 0 | 0 | 0.018357
| Operational IT & Telecoms - BT 21CN |  | 0 | 0 | 0 | 0 | 0
| Operational IT & Telecoms - other |  | 0 | 0.0098117 | 0 | 0 | 0.0098117
| Non - rechargeable diversions |  | 2.4875 | 3.2468 | 0.64504 | 1.7983 | 8.1776
| Total Non-load related (other non-fault) |  | 3.5781 | 10.9461 | 0.86062 | 1.9181 | 17.3028
| Customer Contributions (-ve) |  | 0 | 0 | 0 | 0 | 0
| Total Net Non-load related (other non-fault) |  | 3.5781 | 10.9461 | 0.86062 | 1.9181 | 17.3028
| Total Non-load related expenditure (direct costs) |  | 58.267
| Customer Contributions (-ve) |  | 0
| Total Net Non-load replacement (Direct Costs) |  | 58.267
Non-operational
| Direct Costs only |  | Total | Owned by DNO | Owned by related party
|  |  | £'m | £'m | £'m
| Vehicles |  | 0.3 | 0.3
| Plant & Machinery |  | 0
| Small Tools & Equipment |  | 1.499 | 1.499
| Office Equipment |  | 0
| Non-operational property |  | 0
| IT Non-operational Capital Expenditure |  | 0.609 | 0.609
| Telecoms Non-operational Capital Expenditures |  | 0
| Total Non-operational New Assets & Replacement |  | 2.408 | 2.408 | 0

## RRP 2.6
Regulatory Reporting Pack |  |  |  | Index
2007/08
MISCELLANEOUS
Non-activity based costs (excluded from Table 2.2)(enter as positive)
[5 empty] | £'m | £'m
Pass through Costs
|  | Transmission exit charges |  |  | 4.4
|  | Wheeled units imported |  |  | 0
|  | Network rates |  |  | 27.092
|  | Ofgem licence fee |  |  | 1.4501
|  | Shetland Balancing Costs (SHEPD only) |  |  | 0
|  | Scottish Electricity Settlements run-off (Scottish DNOs only) |  |  | 0 | 32.9421
Costs inside scope of DPCR4 allowances
|  | Guaranteed standard of performance compensation payments |  |  | 0
|  | Ex-gratia compensation payments |  |  | 0.5486
|  | Bad debt expense (net of recoveries) |  |  | 0.31404 | 0.86264
Costs outside scope of DPCR4 allowances
|  | (Profit)/loss on sale of fixed assets and scrap[(-ve)/+ve] |  |  | 0.016526
|  | Statutory Depreciation on operational assets |  |  | 39.9128
|  | Pension deficit repair payments |  |  | 9.5 | 49.4293
|  |  | Total Non-Activity Based Costs |  |  | 83.234
OTHER ITEMS adjusting RAV
Proceeds of sale of assets and scrap (not recorded on Table 2.2)
|  |  | Cash proceeds received on sale of: |  | £'m
Operational assets (-ve)
|  |  | Sales of scrap (-ve) |  | -0.34825
|  |  | Non-operational assets (-ve) |  | -0.076416
|  |  | Total |  | -0.42467
|  |  | ANALYSIS OF ASSET DISPOSALS |  | Cost | Depn. | Net Book Value | Net Sales Proceeds | (Profit) / Loss on Disposal | Asset Owner
|  |  | Asset Type |  | £m | £m | £m | £m | £m
|  |  | Network |  | 0.51625 | 0.26988 | 0.24637 |  | 0.24637
|  |  | Land and Building |  | 1.2437 | 1.0489 | 0.19483 |  | 0.19483
|  |  | Vehicles |  | 0.42554 | 0.42554 | 0 | 0.076416 | -0.076416
|  |  | Sale of various small elements of surplus Land & Buildings on sites |  |  |  | 0 | 0.34825 | -0.34825
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
|  |  | Total |  | 2.1855 | 1.7443 | 0.4412 | 0.42467 | 0.016526
[8 empty] | OK | OK
|  | Use of System Bad Debts |  |  | £m | £m
previously allowed
Costs incurred (excluding VAT)
Receipts/(recoveries)
|  |  | Total Use of System Bad Debts |  | 0
|  | Salary sacrifice schemes (including flexible benefit schemes) |  |  | Total | Direct capex | Direct opex, faults & Non-op capex | Indirect costs | All Other non-distrib'n activities
[5 empty] | £m | £m | £m | £m | £m
|  |  | Salary element sacrificed by employee(-ve) |  | 0
|  |  | Additional employer pension contributions (+ve) |  | 0
|  | Lane rentals analysis: including logged up costs (see below): |  |  | Total | Load Related New Connections & Reinforcement | Non-load non-fault new & replacement assets | Faults | Inspectns & Maint. (exc. Tree Cutting) | Tree Cutting
[5 empty] | £m | £m | £m | £m | £m | £m
|  |  | Fines and penalties |  | 0.36451 | 0.20151 | 0.054666 | 0.10834
|  |  | Road occupation costs |  | 0
|  |  | Permit scheme costs |  | 0
|  |  | Congestion charges |  | 0
|  |  | Total per Table 2.2 |  | 0.36451 | 0.20151 | 0.054666 | 0.10834 | 0 | 0
Uncertain Costs (included in table 2.2 costs)
|  | Road Occupation & Permit Scheme Costs included within Lane Rentals, previously agreed in writing with Ofgem to be treated as logged up costs: |  |  | Total | Load Related New Connections & Reinforcement | Non-load non-fault new & replacement assets | Faults | Inspectns & Maint. (exc. Tree Cutting) | Tree Cutting
[5 empty] | £m | £m | £m | £m | £m | £m
|  |  | Road occupation costs |  | 0
|  |  | Permit scheme costs |  | 0
|  |  | Congestion charges |  | 0
|  |  | Total |  | 0 | 0 | 0 | 0 | 0 | 0
|  | Costs previously agreed with Ofgem in writing for additional security |  |  | 0
Miscellaneous costs (included in table 2.2 costs)
£m
Pension administration costs (reported in HR & Non-op training)
LV Control centre costs (where it remotely controls LV network)
[5 empty] | £m | km
Expenditure replacing Pressure Assisted cables
|  | Undergrounding in National Parks / AONB - direct costs |  |  | £m | km
LV
HV
EHV/132kV
Undergrounding in National Parks / AONB - indirect costs
|  |  | Total Undergrounding in National Parks / AONB |  | 0 | 0

## RRP 5.1
Regulatory Reporting Pack (RRP) |  |  |  | Index
2007/08
Network Data
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
| QUALITY OF SERVICE |  | Historical data |  |  | For Future years
| Customer Numbers | Millions |  |  | 2580775
| Total CIs (Excluding EE) | CIs |  |  | 2119306
| Total CMLs (Excluding EE) | CMLs |  |  | 198961241
NETWORK ACTIVITY INDICATORS
CONNECTIONS
Number of new connections
| EHV (Includes 132kV) | No. Connections |  |  | 0
| HV | No. Connections |  |  | 17
| LV | No. Connections |  |  | 29758
| DG | No. Connections |  |  | 9
Total Connected Distributed Generation
| 132kV | MW |  |  | 0
| EHV | MW |  |  | 166
| HV | MW |  |  | 145
| LV | MW |  |  | 2.2
| Total |  |  |  | 313.2
DEMANDS
| System Maximum Demand | MW |  |  | 5635
| System Maximum Demand (Weather corrected) | MW |  |  | 5497
Units Distributed
| EHV (Includes 132kV) | GWh |  |  | 710
| HV | GWh |  |  | 9669
| LV | GWh |  |  | 19286
| Total |  |  |  | 29665
LOSSES
| Units of distribution losses | (GWh) |  |  | 1439
| Losses | (%) |  |  | 4.851%
SYSTEM PARAMETERS
Distribution Circuit Length - Overhead (km)
| 132kV | Circuit km |  |  | 2384
| EHV | Circuit km |  |  | 2702
| HV | Circuit km |  |  | 12593
| LV | Circuit km |  |  | 5071
| Total | Circuit km |  |  | 22750
Distribution Circuit Length - Underground (km)
| 132kV | Circuit km |  |  | 199
| EHV | Circuit km |  |  | 1721
| HV | Circuit km |  |  | 13288
| LV | Circuit km |  |  | 32990
| Total | Circuit km |  |  | 48198
Distribution Circuit Length - Total (km)
| 132kV | Circuit km |  |  | 2583
| EHV | Circuit km |  |  | 4423
| HV | Circuit km |  |  | 25881
| LV | Circuit km |  |  | 38061
| Total | Circuit km |  |  | 70948
Number of Substations and Switching Stations
| 132kV | No. Subs |  |  | 80
| EHV ground mounted | No. Subs |  |  | 340
| EHV pole mounted | No. Subs |  |  | 0
| HV ground mounted | No. Subs |  |  | 19981
| HV pole mounted | No. Subs |  |  | 22698
| Total | No. Subs |  |  | 43099