## Schedule 1 (Approved Devices)
Manufacturer | Model | Variant | Hardware version | Software/firmware version | Functions | Auxilliary supply voltage | Restrictions | Notes | Technology | Assessment type | Assessment reference | First approved issue
A-Eberle | REG DP |  |  |  | ASC |  |  | Includes voltage transducer and ASC position transducer. | Numeric | NGED | Available on request | 10 or earlier
Eaton Cooper Power Systems | CL-7 |  |  | 1.10.0 | VR |  | Only for use with Cooper Power System Voltage Regulators |  | Numeric | NGED |  | 10 or earlier
Fanox | SIA-C |  | R2.30 | 3.08/1.03 | 3OC, 3OCIT, E, EIT | Self-powered via CT inputs | Only for use on 6.6kV and 11kV network switchgear (e.g. RMUs etc.) |  | Numeric | ENA | NoC 201, issue 1 | 10 or earlier
Fundamentals | SuperTAPP SG | FP1034 – AGGG000PDS-L06-20-01A | 06 |  | TCC, TCM |  | Two-Winding Application | With 4 voltage and 3 current inputs | Numeric | NGED |  | 12
Fundamentals | SuperTAPP SG | FP1034 – AGGG00FPDS-L06-20-01A | 06 |  | TCC, TCM |  | Two-Winding Application | With 4 voltage and 10 current inputs | Numeric | NGED |  | 12
Fundamentals | SuperTAPP SG | FP1034-AGGG00DPDS-L06-20-01A | 06 |  | TCC, TCM |  | Three-Winding Application | With 8 voltage and 6 current inputs | Numeric | NGED |  | 12
GE Grid Solutions | Agile P14DB1 | P14DB11C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, NVD, TCS, BBCK, AI |  | Relay shall not be used for NVD derived from capacitive cones or bushings. |  | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Grid Solutions | Agile P14DB2 | P14DB21C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, SEF, NVD, TCS, BBCK, AI |  | Relay shall not be used for NVD derived from capacitive cones or bushings. |  | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Grid Solutions | Agile P14DL1 | P14DL11C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, 3DOCIT(LB), 3DOCIT(VC), E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, BBCK, AI |  |  | Relay includes load blinding and voltage controlled directional overcurrent features. | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Grid Solutions | Agile P14DZ2 | P14DZ21C4C0620A | A | 62 | 3OC, 3OCIT, 3DOCIT, 3DOCIT(LB), 3DOCIT(VC), E, EIT, DEIT, SEF, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, BBCK, AI |  | For use with Schneider Genie Evo switchgear only. | Relay includes load blinding and voltage controlled directional overcurrent features. | Numeric | ENA | NoC 186, issue 4 | 10 or earlier
GE Grid Solutions | Agile P14NB1 | P14NB11C4C0620A | A | 62 | 3OC, 3OCIT, EIT, TCS, BBCK, AI, SBEF |  |  |  | Numeric | ENA | NoC 185, issue 4 | 10 or earlier
GE Grid Solutions | Agile P14NB2 | P14NB21C4C0620A | A | 62 | 3OC, 3OCIT, EIT, SEF, TCS, BBCK, AI |  |  |  | Numeric | ENA | NoC 185, issue 4 | 10 or earlier
GE Grid Solutions | Agile P14NZ2 | P14NZ21C4C0620A | A | 62 | 3OC, 3OCIT, E, EIT, SEF, AR, TCS, BBCK, AI |  |  |  | Numeric | ENA | NoC 185, issue 4 | 10 or earlier
GE Grid Solutions | Agile P94VB | P94VB11A4B0620A | A | 62 | VTS, NVD, 3OV, 3UV, LFDD |  | Relay shall not be used for NVD derived from capacitive cones or bushings. |  | Numeric | ENA | NoC 187, issue 4 | 11
GE Grid Solutions | Agile P94VP | P94VP11A4B0620A | A | 62 | VTS, 3OV, 3UV, LFDD, SC |  | Relay shall not be used for NVD |  | Numeric | ENA | NoC 187, issue 4 | 11
GE Grid Solutions | Micom P142 | P142811B4S0460J | J | 46 | 3OC, 3OCIT, E, EIT, SEF, AR, AR(LLC), TCS, BBCK, AI | 110Vd.c. |  | Without interMiCOM. Relay, software and logic configuration set up specifically for NGED auto-reclose application. | Numeric | ENA | NoC 101, Issue 11 | 12
GE Grid Solutions | Micom P142 | P14281EB4S0460J | J | 46 | 3OC, 3OCIT, E, EIT, SEF, AR, AR(LLC), TCS, BBCK, AI, IT | 110Vd.c. |  | With interMiCOM. Relay, software and logic configuration set up specifically for NGED auto-reclose application. | Numeric | ENA | NoC 101, Issue 11 | 12
GE Grid Solutions | Micom P145 | P145811A4S0460J | J | 46 | 3OC, 3OCIT, 3DOCIT, DEIT, E, EIT, SEF, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, BBCK | 110Vd.c. |  |  | Numeric | ENA | NoC 101, Issue 11 | 12
GE Grid Solutions | Micom P443 | P44381xx4S0910M | M | 91 | Z, 3DOCIT, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), BBCK, TCS, VTS |  | For use on 132kV system only. | Mho & quad characteristics. | Numeric | ENA | NoC 128, Issue 8 | 12
GE Grid Solutions | Micom P445 | P445811B4S0490J | J | 49 | Z, 3DOCIT, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), BBCK, TCS, VTS |  | Only for use on 33kV and 66kV systems. | Mho Phase Characteristic and Mho/Quadrilateral E/F Characteristic. | Numeric | ENA | NoC 142, Issue 7 | 12
GE Grid Solutions | Micom P541 | P541814A4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, TCS | 110Vd.c. | For use with 850nm multi-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P541 | P541814C4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, TCS | 110Vd.c. | For use with 1300nm single-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P542 | P542814A4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, AR, TCS | 110Vd.c. | For use with 850nm multi-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P542 | P542814C4S0300J | J | 30 | CD, 3OC, 3OCIT, E, EIT, AR, TCS | 110Vd.c. | For use with 1300nm single-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P543 | P543814A4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 850nm multi-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P543 | P543814A4S0610M | M | 61 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 850nm multi-mode fibre. | Firmware version 61 does not include distance protection. | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P543 | P543814C4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 1300nm single-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P543 | P543814C4S0610M | M | 61 | CD, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), TCS, VTS | 110Vd.c. | For use with 1300nm single-mode fibre. | Firmware version 61 does not include distance protection. | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P545 | P545814A4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS | 110Vd.c. | For use with 850nm multi-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P545 | P545814C4S0570K | K | 57 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS | 110Vd.c. | For use with 1300nm single-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P546 | P546814A4S0710M | M | 71 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS |  | For use with 850nm multi-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P546 | P546814C4S0710M | M | 71 | CD, Z, 3OC, 3OCIT, 3DOCIT, E, EIT, DEIT, AR, TCS, VTS |  | For use with 1300nm single-mode fibre. |  | Numeric | ENA | NoC 116, Issue 8 | 12
GE Grid Solutions | Micom P642 | P642811D4S0060J | J | 6 | BD, REF, 3OC, 3OCIT, E, EIT, VTS, CTS |  | For use with 2 winding transformers. A suitable panel-mounted metrosil and series stabilising resistor shall be provided for each REF zone. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. |  | Numeric | ENA | NoC 153, Issue 5 | 12
GE Grid Solutions | Micom P643 | P643811A4S0060K | K | 6 | BD, REF, 3OC, 3OCIT, E, EIT, VTS, CTS |  | For use with 3 winding transformers. A suitable panel-mounted metrosil and series stabilising resistor shall be provided for each REF zone. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. |  | Numeric | ENA | NoC 153, Issue 5 | 12
GE Grid Solutions | MMLG02 |  |  |  | RTB |  |  | Intercompatible with Siemens 7XG22 (RMLG02) | N/A |  |  | 10 or earlier
GE Grid Solutions | BA300 |  |  |  | BA |  |  |  | Electronic |  |  | 10 or earlier
GE Grid Solutions | MBCI 01 (Translay 'S') |  |  |  | PW |  | For use with NGED owned pilots. Pilots shall be supervised. Isolation requirements shall be determined with reference to ACE 19. Other scheme components shall be selected in accordance with this schedule and the manufacturer's application note. | Main relay of Translay 'S' scheme. | Electronic | ENA | Approval Notice 39 | 10 or earlier
GE Grid Solutions | MCAA11 | MCAA11R1BU9032C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 3M & 1B S/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA111001 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAA11 | MCAA11R1BU9036C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 4M S/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA111001 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAA11 | MCAA11R1BU9037C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 2M & 2B S/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA111001 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAA12 | MCAA12R1BU9002C |  |  | TI | 110Vd.c. | For use with Brush Quantum and Horizon switchgear. | 1M/1B S/R & 1M/1B H/R contacts & H/R flag. Inon = 0.227A, ITEST = 0.14A Diagram 01MCAA1203 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAA12 | MCAA12R1BU9003C |  |  | TI | 110Vd.c. | For use with high burden MVAJ10x or MVAJ20x relays | 1M/1B S/R & 1M/1B H/R contacts & H/R flag. ITEST = 0.37A Diagram 01MCAA1203 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAA12 | MCAA12R1BU9004C |  |  | TI | 110Vd.c. | For use with Areva WS switchgear (Trip Coil 25VA) and Ormazabal 33kV switchgear | 2M S/R & 1M / 1B H/R contacts & H/R flag. Inon = 0.15A, ITEST = 0.0083A Diagram 01MCAA1203 Sheet 1. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAA12 | MCAA12R1BU9008C |  |  | TI | 110Vd.c. | For use with Siemens NX Plus Switchgear | 2M S/R & 1M/1B H/R contacts & H/R flag. ITEST = 0.34A | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAG14 |  |  |  | BEF |  | A suitable panel-mounted metrosil and series stabilising resistor shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | Single-pole current-calibrated high impedance relay | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MCAG34 |  |  |  | 3BBOC |  | Suitable panel-mounted metrosils and series stabilising resistors shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | Three-pole current-calibrated high impedance relay | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MFAC14 |  |  |  | REF |  | A suitable panel-mounted metrosil and shunt setting resistor shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | Single-pole voltage-calibrated high impedance relay | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MRTP 01 |  |  |  | PWS | 240Va.c. and 110Vd.c. | For use with MBCI 01 in Translay 'S' scheme. For 5kV pilot applications. | Supervision relay and send-end injection filter for Translay 'S' scheme with integrated monitoring of a.c. supply. | Electronic | ENA | Approval Notice 9 | 10 or earlier
GE Grid Solutions | MRTP 02 |  |  |  | PWS |  | For use with MBCI 01 in Translay 'S' scheme. For 5kV pilot applications. | Receive-end injection filter for Translay 'S' scheme. | Electronic | ENA | Approval Notice 9 | 10 or earlier
GE Grid Solutions | MRTP 03 |  |  |  | PWS | 240Va.c. and 110Vd.c. | For use with MBCI 01 in Translay 'S' scheme. For 15kV pilot applications. Isolation transformers shall be selected in accordance with the manufacturer's application note. | Supervision relay for Translay 'S' scheme with integrated monitoring of a.c. supply. | Electronic | ENA | Approval Notice 9 | 10 or earlier
GE Grid Solutions | MVAA11 |  |  |  | AI |  |  | All elements to have self-reset contacts and hand reset flags. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MVAA21 |  |  |  | AI |  |  | All elements to have self-reset contacts and hand reset flags. | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MVAJ051 | MVAJ051RA0201 |  |  | TS, BBCKA | 30Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ051 | MVAJ051RA0801 |  |  | TS, BBCKA | 110Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ053 | MVAJ053RA0201 |  |  | TH | 30Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ053 | MVAJ053RA0801 |  |  | TH | 110Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ055 | MVAJ055RA0201 |  |  | TH, TE | 30Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand Reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ055 | MVAJ055RA0801 |  |  | TH, TE | 110Vd.c. |  | 4 N/O & 1 N/C contact (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand Reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ101 | MVAJ101RA0202 |  |  | TS, BBCKA | 30Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ101 | MVAJ101RA0802 |  |  | TS, BBCKA | 110Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Instantaneous Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ102 | MVAJ102RA0202 |  |  | TDS | 30Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Nominal 2.5s Time Delay Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ102 | MVAJ102RA0802 |  |  | TDS | 110Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Nominal 2.5s Time Delay Self Reset Relay, Hand Reset Flag. | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ105 | MVAJ105RA0202 |  |  | TH, TE | 30Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAJ105 | MVAJ105RA0802 |  |  | TH, TE | 110Vd.c. |  | 8 N/O & 2 N/C contacts (alternative contact arrangement may be used where required). Hand / Electrical Reset Relay, Hand reset Flag | Electromechanical | ENA | NoC 43, Issue 3 | 10 or earlier
GE Grid Solutions | MVAP22 |  |  |  | VTS |  |  |  | Electromechanical |  |  | 10 or earlier
GE Grid Solutions | MVAW02 |  |  |  | SIR |  |  | Used with protection signalling schemes | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MVAX11 |  |  |  | TRS |  |  |  | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MVAX12 |  |  |  | TSS |  |  |  | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MVAX31 |  |  |  | TCS |  |  |  | Electromechanical | ENA | NoC 137, Issue 2 | 10 or earlier
GE Grid Solutions | MVTP31 |  |  |  | CTS |  |  |  | Electronic | ENA | NoC 42 | 10 or earlier
GE Grid Solutions | MVTT14 |  |  |  | TD |  |  |  | Electronic | ENA | Approval Notice 35 | 10 or earlier
GE Grid Solutions | MVUA11 |  |  |  | TD |  |  |  | Electronic |  | Approval Notice 42 | 10 or earlier
Schneider | ADVC3 |  |  |  | 3OC, 3OCIT, E, EIT, SEF, AR |  | For use with Schneider Pole Mounted Reclosers |  | Numeric | ENA | NoC 193 | 10 or earlier
Schneider | GCM05 |  |  |  | IT |  | For use with NGED owned pilots. A trip relay approved for function TS shall be installed to provide trip indication on the front of the cubicle. |  | Electronic | ENA | Approval Notice 54 | 10 or earlier
Schneider | Micom P142 | P142211B4M0468J |  | 46V | 3OC, 3OCIT, E, EIT, SEF, AR, AR(LLC), TCS, BBCK, AI | 110Vd.c. |  |  | Numeric | ENA | NoC 168, issue 3 | 10 or earlier
Schneider | VIP 400 |  |  |  | 3OC, 3OCIT, E, EIT | Self-powered via CT inputs | Only for use on Schneider Ringmaster Switchgear |  | Numeric | ENA | NoC 180, issue 1 | 10 or earlier
Siemens | 7PG1111 (AR111) | 7PG1111-1xxx0-0AC0 |  |  | AI | 30Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1111 (AR111) | 7PG1111-1xxx0-0AF0 |  |  | AI | 110Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1112 (AR121) | 7PG1112-1CC10-0AM0 |  |  | PWS | 240Va.c. |  | A.C. supply supervision for Solkor R/Rf pilot supervision scheme. Instantaneous self-reset relay, reverse-operating hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1513 (TR131) | 7PG1513-1xxx0-1AF0 |  |  | TS | 110Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-2 (TR212) | 7PG1521-2xxx0-1xC0 |  |  | TS | 30Vd.c. |  | Instantaneous self-reset relay, operating coil with economy cut-off, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-2 (TR212) | 7PG1521-2xxx0-1xF0 |  |  | TS | 110Vd.c. |  | Instantaneous self-reset relay, operating coil with economy cut-off, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-4 (TR214) | 7PG1521-4xxx0-1CC0 |  |  | TDS | 30Vd.c. |  | Nominal 2s time delay self-reset relay and hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1521-4 (TR214) | 7PG1521-4xxx0-1CF0 |  |  | TDS | 110Vd.c. |  | Nominal 2s time delay self-reset relay and hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1522 (TR221) | 7PG1522-1xxx0-1AC0 |  |  | TS | 30Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1522 (TR221) | 7PG1522-1xxx0-1AF0 |  |  | TS | 110Vd.c. |  | Instantaneous self-reset relay, hand reset flag. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1741 (XR153) | 7PG1741-1CC10-2AA0 |  |  | TSS | 30Vd.c. |  | Instantaneous self reset relay. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG1741 (XR153) | 7PG1741-1CC10-4AA0 |  |  | TSS | 110Vd.c. |  | Instantaneous self reset relay. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2111 (Solkor R/Rf) | 7PG2111-1DA30-0DB0 |  |  | PW |  | For use with NGED-owned pilots. Pilots shall be supervised. For 1A CTs. Isolation requirements shall be determined with reference to ACE 19. Other scheme components shall be selected in accordance with this schedule and the manufacturer's application note. | Main relay of Solkor Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2111 (Solkor R/Rf) | 7PG2111-1DA30-0DD0 |  |  | PW |  | For use with NGED-owned pilots. Pilots shall be supervised. For 5A CTs. Isolation requirements shall be determined with reference to ACE 19. Other scheme components shall be selected in accordance with this schedule and the manufacturer's application note. | Main relay of Solkor Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2112 (Solkor 15kV Pilot Isolation Transformer) | 7PG2112-0AA00-0AA0 |  |  | PWI |  | For 15kV pilot applications | Isolation transformer for Solkor R/Rf scheme. | N/A |  |  | 10 or earlier
Siemens | 7PG2120 (Solkor Pilot Supervision Send Unit) | 7PG2120-0AA00-1CA0 |  |  | PWS |  | For 5kV pilot applications. a.c. supply shall be supervised by 7PG2132 (B22) relay. | Supervision relay and send-end injection filter for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2120 (Solkor Pilot Supervision Send Unit) | 7PG2120-0AA00-2WA0 |  |  | PWS |  | For 15kV pilot applications. a.c. supply shall be supervised by 7PG2132 (B22) relay. | Supervision relay and send-end injection filter for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2132 (B22) | 7PG2132-1CC40-1AC0 |  |  | PWS | 240Va.c. |  | A.C. supply supervision for Solkor R/Rf pilot supervision scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2144 (B75/B74) | 7PG2144-1CC40-1CB0 |  |  | PWS | 30Vd.c. | For 5kV pilot applications. | Combined pilot supervision receive unit and repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2144 (B75/B74) | 7PG2144-1CC40-1CE0 |  |  | PWS | 110Vd.c. | For 5kV pilot applications. | Combined pilot supervision receive unit and repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2154 (B75) | 7PG2154-1BA10-2WA0 |  |  | PWS |  | For 15kV pilot applications. | Pilot supervision receive unit for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2164 (B74) | 7PG2164-1CC40-2AB0 |  |  | PWS | 30Vd.c. | For 15kV pilot applications. | Receive-end pilot supervision repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2164 (B74) | 7PG2164-1CC40-2AE0 |  |  | PWS | 110Vd.c. | For 15kV pilot applications. | Receive-end pilot supervision repeat relay for Solkor R/Rf scheme. | Electromechanical |  |  | 10 or earlier
Siemens | 7PG2311 (5B3) | 7PG2311-1DA30-1BA0 |  |  | REF, BEF |  | A suitable panel-mounted shunt setting resistor shall be provided. The necessary rating and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. | An external metrosil is not required with this relay, which has a built-in non-linear resistor. | Electromechanical |  |  | 10 or earlier
Siemens | 7SA522 (Siprotec) | 7SA5221-5ABxx-0xN4-LOH | /GG | 4.74 | Z, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), NVD, BBCK, TCS |  | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Relay shall not be used for NVD derived from capacitive cones or bushings. | The relay has 8 binary inputs and 16 binary outputs. | Numeric | ENA | NoC 58 | 10 or earlier
Siemens | 7SA522 (Siprotec) | 7SA5221-5DBxx-0xN4-LOH | /GG | 4.74 | Z, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), NVD, BBCK, TCS |  | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Relay shall not be used for NVD derived from capacitive cones or bushings. | The relay has 24 binary inputs and 32 binary outputs | Numeric | ENA | NoC 58 | 10 or earlier
Siemens | 7SD522 (Siprotec) | 7SD5221-5DBxx-xxxx-xxx |  | 4.73 | CD, Z, 3OCIT, EIT, DEIT, AR, AR(SC), AR(LLC), AR(DBLLC), BBCK, TCS |  | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. |  | Numeric | ENA | NoC 102 | 10 or earlier
Siemens | 7SR1101-1 (Argus C) | 7SR1101-1MA12-1CA0 | /FF | 2436H80003R4k-3d | E, EIT, SBEF | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element relay without SEF | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1101-1 (Argus C) | 7SR1101-1NA12-1CA0 | /FF | 2436H80003R4k-3d | E, EIT, SBEF | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element relay without SEF | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1101-3 (Argus C) | 7SR1101-3MA12-1CA0 | /FF | 2436H80003R4k-3d | SEF | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element SEF relay. | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1101-3 (Argus C) | 7SR1101-3NA12-1CA0 | /FF | 2436H80003R4k-3d | SEF | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | Single element SEF relay. | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-1 (Argus C) | 7SR1103-1MA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, E, EIT, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay without SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-1 (Argus C) | 7SR1103-1NA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, E, EIT, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay without SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-3 (Argus C) | 7SR1103-3MA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, SEF, E, EIT, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay with SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1103-3 (Argus C) | 7SR1103-3NA12-2CA0 | /FF | 2436H80003R4k-3d | 3OC, 3HOC, 3OCIT, SEF, E, EIT, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay with SEF, without A/R | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1204-2 (Argus C) | 7SR1204-2MA12-1CA0 | /FF | 2436H80004R4k-3d | DEIT, NVD, 3OV | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | Single element directional earth fault / NVD relay. Relay may be used in conjunction with a conventional VT or with appropriate capacitor bushings to provide NVD protection. Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1204-2 (Argus C) | 7SR1204-2NA12-1CA0 | /FF | 2436H80004R4k-3d | DEIT, NVD, 3OV | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | Single element directional earth fault / NVD relay. Relay may be used in conjunction with a conventional VT or with appropriate capacitor bushings to provide NVD protection. Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1206-2 (Argus C) | 7SR1206-2M12-2CA0 | /FF | 2436H80004R4k-3d | 3DOCIT, DEIT, NVD, 3OV, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | 4 element directional relay without SEF, without A/R Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1206-2 (Argus C) | 7SR1206-2NA12-2CA0 | /FF | 2436H80004R4k-3d | 3DOCIT, DEIT, NVD, 3OV, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted | 4 element directional relay without SEF, without A/R Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 156 | 10 or earlier
Siemens | 7SR1587 (Argus) | 7SR1587-5HA12-1CA0 | /CC | 2436H80011 R4e-2a | 3UV, 3OV, NVD, LFDD |  | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. Where NVD is derived from capacitive cones or bushings, a Siemens 7XG21 (Capacitor Cone Adaptor Unit) shall be fitted. | Voltage & Frequency Protection Relay Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 196 | 10 or earlier
Siemens | 7SR2103-1 (Argus M) | 7SR2103-1MA12-0DA0 | /DD | 2435H85008 R8e-8a | 3OC, 3HOC, 3OCIT, E, EIT, SBEF, SEF, AR, BBCK, TCS | 30Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay including SEF and A/R Refer to Siemens 7XG21 below for additional information | Numeric | ENA | NoC 151 | 10 or earlier
Siemens | 7SR2103-1 (Argus M) | 7SR2103-1NA12-0DA0 | /DD | 2435H85008 R8e-8a | 3OC, 3HOC, 3OCIT, E, EIT, SBEF, SEF, AR, BBCK, TCS | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element relay including SEF and A/R | Numeric | ENA | NoC 151 | 10 or earlier
Siemens | 7SR2203-2 (Argus M) | 7SR2203-2NA12-0DA0 | /DD | 2435H85009 R8e-8a | 3OC, 3OCIT, 3DOCIT, 3DOCIT(LB), 3DOCIT(VC), E, EIT, DEIT, AR, TCS, BBCK, AI | 110Vd.c. | Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | 4 element directional relay including load-blinding and voltage-controlled directional overcurrent features. | Numeric | ENA | NoC 151 | 10 or earlier
Siemens | 7SR23 (DAD) | 7SR2302-1NA12-0CA0 | /CC | 2435H85014 R8e-1c | 3BBOC | 110Vd.c. | Suitable panel-mounted metrosils and series stabilising resistors shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | The relay has 9 binary inputs, 8 binary outputs, and 8 LEDs. | Numeric | ENA | NoC 184 | 10 or earlier
Siemens | 7SR23 (DAD) | 7SR2303-1NA12-0CA0 | /CC | 2435H85014 R8e-1c | 3BBOC | 110Vd.c. | Suitable panel-mounted metrosils and stabilising resistors shall be provided. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. | The relay has 19 binary inputs, 16 binary outputs, and 16 LEDs. | Numeric | ENA | NoC 184 | 10 or earlier
Siemens | 7SR242 (Duobias) | 7SR2423-2NA12-0BA0 | /DD | 2662H85001 RB8b-7c | BD, REF |  | For use with 2 winding transformers. A suitable panel-mounted metrosil and series stabilising resistor shall be provided for each REF zone. The necessary ratings and parameters are scheme-dependent, so shall be specified by the engineer designing the scheme. Where relay inputs are used for tripping or closing functions resistors shall be provided and installed to ensure compliance with the high burden requirements defined in ENA TS 48-4. |  | Numeric | ENA | NoC 150 | 10 or earlier
Siemens | 7XG22 (RMLG02) |  |  |  | RTB |  |  | Intercompatible with GE Grid Solutions MMLG02 | N/A |  |  | 10 or earlier
Siemens | 7XG21 Capacitor Cone Adaptor Units | 7XG2100-1AA00-0AA0 |  |  | NVD |  | Siemens 7XG21 Capacitor Cone Adaptor Units are now obsolete and no longer available to purchase from Siemens. NGED have secured a number of Capacitor Cone Adaptor Units that are located at central stores in Huthwaite - Item Number 63562 | Units to be free-issued to sub-suppliers on request.

## Schedule 2 (Function Key)
Function Code | Description | Notes
3BBOC | 3 phase busbar overcurrent | High impedance
3DOCIT | 3 phase directional IDMT overcurrent
3DOCIT(LB) | 3 phase directional IDMT overcurrent with load blinding
3DOCIT(VC) | 3 phase voltage controlled directional IDMT overcurrent
3HOC | 3 phase high set overcurrent
3OC | 3 phase instantaneous or definite time overcurrent
3OCIT | 3 phase IDMT overcurrent
3OV | 3 phase over voltage
3UV | 3 phase under voltage
AI | Alarm indication relay | Used for buchholz alarm, winding temperature alarm, SF6 pressure low alarm etc.
AR | Auto-reclose
AR(DBLLC) | Auto-reclose with dead bus, live line check
AR(LLC) | Auto-reclose with live line check
AR(SC) | Auto-reclose with synchronising check
ASC | ASC control relay
BA | Battery Alarm
BBCK | Busbar protection check relay
BBCKA | Busbar protection check auxiliary relay
BD | Biased differential
BEF | Balanced Earth Fault | High impedance
CD | Current Differential | Feeder differential protection using Category 1 communications links
CTS | CT supervision
DEIT | Directional IDMT earth fault
E | Instantaneous or definite time earth fault
EIT | IDMT earth fault
IT | Intertrip send/receive system
LFDD | Low frequency demand disconnection. | In addition to WPD requirements, ENA Technical Specifications and British Standards, LFDD relays must comply with CC.A.5 of the Grid Code.
NVD | Neutral voltage displacement
PW | Pilot wire protection | Feeder differential protection using WPD-owned pilot cables
PWI | Pilot wire isolation
PWS | Pilot wire supervision
REF | Restricted Earth Fault | High impedance
RTB | Relay test block
S | Signalling relay (for distance protection schemes)
SBEF | Standby earth fault
SC | Synchronising check
SEF | Sensitive earth fault
SIR | Signalling scheme interposing relay
TCC | Tap Change Control
TCM | Tap Change Monitor
TCS | Trip circuit supervision
TD | Time delay relay
TDS | Trip relay with time-delayed self-reset contacts, hand reset flag
TE | Trip relay with electrically reset contacts, hand reset flag
TH | Trip relay with hand reset contacts and flag
TI | Trip indication relay | Used in series with trip coil or trip relay coil, e.g. buchholz trip, winding temperature trip etc.
TRS | Trip relay supervision
TS | Trip relay with instantaneous self-reset contacts, hand reset flag
TSS | Trip Supply Supervision
VR | Voltage regulation relay
VTS | VT supervision
Z | Distance protection