## Metadata
Data Dictionary
Column Heading | Description
Associated GSP Group | Name of the upstream Grid Supply Point (GSP) group which supplies the substation. Note that multiple GSPs can run in parallel so are therefore reported as groups.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) or Best View scenario the headroom figures refer to
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below)
2022 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the fiscal year
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2040
2045
2050

## Demand Headroom
Associated GSP Group | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.3275 | 6.7765 | 5.5087 | 4.5891 | 3.7269 | 3.0114 | 2.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.3275 | 6.6207 | 5.1496 | 4.0902 | 2.9991 | 2.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.3275 | 6.824 | 5.8971 | 5.0675 | 4.3721 | 3.7219 | 3.0747 | 2.377 | 1.6613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.3275 | 6.482 | 5.013 | 3.6952 | 2.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.3275 | 6.727 | 5.4182 | 4.4567 | 3.6031 | 2.9526 | 2.2435 | 1.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.0531 | 6.9662 | 6.7974 | 6.6536 | 6.466 | 6.2259 | 4.5733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.0531 | 6.9018 | 6.6947 | 6.483 | 6.0648 | 5.6478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.0531 | 7.0728 | 7.0912 | 7.0303 | 6.9375 | 6.8328 | 6.716 | 6.575 | 3.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.0531 | 6.7999 | 6.5719 | 6.1792 | 5.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.0531 | 7.0704 | 7.077 | 6.9921 | 6.9421 | 6.8638 | 6.7555 | 2.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.9793 | 4.9205 | 4.7516 | 4.6033 | 4.254 | 3.8199 | 3.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.9793 | 4.6778 | 4.1967 | 3.8841 | 3.3393 | 2.7717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.9793 | 4.9743 | 4.9464 | 4.9403 | 4.7372 | 4.5498 | 4.339 | 4.0079 | 3.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.9793 | 4.557 | 4.1295 | 3.5928 | 3.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.9793 | 4.8577 | 4.6826 | 4.5093 | 4.2164 | 3.8889 | 3.1001 | 2.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.9394 | 19.8903 | 19.8456 | 19.8078 | 19.7642 | 19.6995 | 19.6189 | 19.5844 | 19.5311 | 19.4768 | 19.441 | 19.4249 | 19.4044 | 19.3878 | 19.2465 | 19.26 | 19.3635
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.9394 | 19.8722 | 19.794 | 19.7199 | 19.627 | 19.5228 | 19.3909 | 19.298 | 19.2222 | 19.1282 | 19.0681 | 19.0168 | 18.9562 | 18.9034 | 18.5855 | 18.4924 | 18.5824
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.9394 | 19.9004 | 19.8758 | 19.8458 | 19.8189 | 19.773 | 19.7261 | 19.7029 | 19.6915 | 19.6794 | 19.6686 | 19.6458 | 19.6293 | 19.6127 | 19.3669 | 19.1342 | 19.0216
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.9394 | 19.8508 | 19.7673 | 19.6674 | 19.5628 | 19.4273 | 19.2937 | 19.2015 | 19.1453 | 19.0842 | 19.0359 | 19.0045 | 18.9754 | 18.967 | 18.7698 | 18.785 | 18.8925
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.9394 | 19.8814 | 19.809 | 19.7462 | 19.6789 | 19.6212 | 19.559 | 19.5273 | 19.505 | 19.4741 | 19.4266 | 19.3897 | 19.3584 | 19.3362 | 19.0477 | 19.0592 | 19.1944
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 4.9328 | 4.9276 | 4.8515 | 4.8894 | 4.7796 | 4.6224 | 4.0826 | 3.6412 | 3.133 | 2.218 | 1.8229 | 1.6688 | 1.1441 | 0.71868 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.9328 | 4.8111 | 4.6307 | 4.5409 | 4.1536 | 3.772 | 2.9949 | 2.2997 | 1.5286 | 0.14113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.9328 | 4.9818 | 5.0184 | 5.0745 | 5.0063 | 4.9481 | 4.8838 | 4.8097 | 4.7292 | 4.5493 | 4.3765 | 3.8528 | 3.3229 | 2.8231 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.9328 | 4.615 | 4.322 | 4.002 | 3.6815 | 2.6542 | 1.9185 | 1.1415 | 0.36698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.9328 | 4.9766 | 5.0043 | 5.0338 | 5.0381 | 4.9951 | 4.928 | 4.8356 | 4.3961 | 3.5546 | 3.0041 | 2.4689 | 2.0184 | 1.7391 | 0 | 0 | 0
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Best View | Headroom (MW) | 17.0018 | 17.05 | 17.0701 | 17.1073 | 17.1122 | 17.0936 | 17.0373 | 16.9997 | 16.9366 | 16.8543 | 16.8118 | 16.8039 | 16.7796 | 16.7546 | 16.3349 | 16.1059 | 16.0091
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 17.0018 | 17.024 | 17.0266 | 17.0375 | 16.997 | 16.94 | 16.8391 | 16.7438 | 16.6489 | 16.4941 | 16.3855 | 16.2811 | 16.157 | 16.0371 | 14.8634 | 11.74 | 11.332
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 17.0018 | 17.0539 | 17.0893 | 17.1273 | 17.1339 | 17.1481 | 17.1301 | 17.1165 | 17.1062 | 17.0957 | 17.0661 | 17.0218 | 16.9834 | 16.9515 | 16.4141 | 15.7949 | 15.0287
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 17.0018 | 16.9769 | 16.9564 | 16.9217 | 16.8819 | 16.8314 | 16.7417 | 16.6223 | 16.5276 | 16.3921 | 16.2635 | 16.1455 | 16.0614 | 15.9903 | 15.3321 | 14.0839 | 13.4884
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 17.0018 | 17.0598 | 17.0993 | 17.1258 | 17.1483 | 17.1628 | 17.1529 | 17.1441 | 17.1251 | 17.079 | 17.0222 | 16.9539 | 16.8919 | 16.8492 | 16.1382 | 15.9187 | 15.8203
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 74.2086 | 74.5086 | 70.7491 | 72.2716 | 65.8238 | 58.8637 | 24.7167 | 11.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 74.2086 | 70.9028 | 63.2757 | 59.4453 | 42.8622 | 28.0058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 74.2086 | 76.8489 | 78.2776 | 81.0894 | 78.4818 | 76.797 | 60.7069 | 57.1355 | 52.682 | 44.9234 | 37.5067 | 25.5861 | 14.1121 | 0.21142 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 74.2086 | 64.7974 | 53.6982 | 41.8939 | 26.8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 74.2086 | 76.3083 | 76.1842 | 76.6302 | 73.7298 | 71.8553 | 51.2894 | 47.0556 | 34.1892 | 12.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 56.9708 | 52.4839 | 32.3507 | 16.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 56.9708 | 47.832 | 23.1619 | 1.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 56.9708 | 57.8508 | 51.3211 | 40.7064 | 21.5493 | 7.2129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 56.9708 | 40.8948 | 15.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 56.9708 | 57.0941 | 46.7274 | 32.3212 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 61.0454 | 56.2377 | 34.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 61.0454 | 51.2531 | 24.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 61.0454 | 61.9884 | 54.9917 | 39.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 61.0454 | 43.8197 | 16.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 61.0454 | 61.1776 | 50.0694 | 16.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 14.9749 | 14.8403 | 14.4716 | 14.1386 | 13.7369 | 13.3036 | 12.8091 | 12.3982 | 11.9167 | 11.6464 | 11.6188 | 11.8799 | 12.2027 | 12.5706 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 14.9749 | 14.7018 | 14.1525 | 13.6439 | 12.8524 | 12.1011 | 11.2324 | 10.5154 | 9.5345 | 8.591 | 4.7178 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 14.9749 | 14.9138 | 14.736 | 14.5364 | 14.2513 | 14.0004 | 13.7977 | 13.5165 | 13.1988 | 12.8151 | 12.4623 | 12.0737 | 11.7293 | 11.4412 | 4.5783 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 14.9749 | 14.5333 | 13.9207 | 13.113 | 12.3183 | 11.5043 | 10.7602 | 9.9005 | 8.9357 | 8.3417 | 2.4006 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 14.9749 | 14.8834 | 14.6943 | 14.3634 | 14.0469 | 13.7556 | 13.4987 | 13.0873 | 12.5769 | 12.217 | 11.8619 | 11.554 | 11.3913 | 11.4719 | 0 | 0 | 0
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 12.774 | 12.8661 | 12.8136 | 12.881 | 12.9286 | 12.9244 | 12.8926 | 12.8749 | 12.7566 | 12.6862 | 12.6461 | 12.6415 | 12.5976 | 12.5872 | 12.4777 | 12.7265 | 13.2046
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 12.774 | 12.8512 | 12.7889 | 12.8166 | 12.8384 | 12.8197 | 12.7489 | 12.6963 | 12.5671 | 12.4319 | 12.3672 | 12.3318 | 12.2465 | 12.1974 | 11.8714 | 11.9432 | 12.3123
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 12.774 | 12.8798 | 12.8821 | 12.9506 | 13.0246 | 13.0759 | 13.1147 | 13.1601 | 13.1653 | 13.184 | 13.2014 | 13.1959 | 13.1901 | 13.1905 | 12.9527 | 12.7464 | 12.7969
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 12.774 | 12.8321 | 12.7638 | 12.7675 | 12.8092 | 12.8085 | 12.7393 | 12.6785 | 12.5654 | 12.4607 | 12.3951 | 12.3298 | 12.2969 | 12.2622 | 12.1158 | 12.3738 | 12.8202
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 12.774 | 12.8892 | 12.8619 | 12.9153 | 13.0014 | 13.0462 | 13.0736 | 13.0982 | 13.0713 | 13.0511 | 13.0281 | 12.9967 | 12.961 | 12.9376 | 12.5987 | 12.8011 | 13.2077
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.606 | 14.4535 | 13.9518 | 13.8329 | 13.5914 | 13.3325 | 12.9957 | 12.7208 | 12.512 | 12.2892 | 12.2616 | 12.402 | 12.5321 | 12.7178 | 11.1303 | 2.522 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.606 | 14.4063 | 13.872 | 13.7023 | 13.2822 | 12.86 | 12.3491 | 11.8663 | 11.4367 | 10.9114 | 10.5867 | 7.7902 | 4.3174 | 1.5639 | 0 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.606 | 14.5574 | 14.3159 | 14.2452 | 14.096 | 13.9337 | 13.7629 | 13.5427 | 13.3631 | 13.0973 | 12.8539 | 12.5943 | 12.3526 | 12.159 | 9.9544 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.606 | 14.3273 | 13.8093 | 13.4838 | 13.0858 | 12.6366 | 12.1728 | 11.6142 | 11.202 | 10.825 | 8.3356 | 5.1926 | 3.3312 | 2.0295 | 0 | 0 | 0
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.606 | 14.5371 | 14.1805 | 14.1093 | 13.9749 | 13.8315 | 13.6481 | 13.3694 | 13.1844 | 12.9614 | 12.7745 | 12.5855 | 12.4777 | 12.4993 | 6.4342 | 0.12439 | 0
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 15.7655 | 15.809 | 15.8479 | 15.8923 | 15.9192 | 15.9037 | 15.8946 | 15.8881 | 15.8745 | 15.8508 | 15.8421 | 15.8534 | 15.8619 | 15.8691 | 15.7249 | 15.6885 | 15.7583
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 15.7655 | 15.794 | 15.8192 | 15.8515 | 15.8397 | 15.7928 | 15.723 | 15.6888 | 15.6433 | 15.5634 | 15.5024 | 15.4496 | 15.3896 | 15.3336 | 14.8567 | 14.7146 | 14.8324
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 15.7655 | 15.8161 | 15.8775 | 15.9404 | 15.9956 | 16.0154 | 16.0394 | 16.0661 | 16.0922 | 16.103 | 16.1143 | 16.1174 | 16.132 | 16.1194 | 15.5248 | 14.5231 | 13.9629
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 15.7655 | 15.7703 | 15.789 | 15.7883 | 15.7726 | 15.7144 | 15.6422 | 15.5991 | 15.5604 | 15.4992 | 15.4491 | 15.4004 | 15.3721 | 15.3532 | 15.0717 | 15.084 | 15.2123
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 15.7655 | 15.8132 | 15.8703 | 15.9383 | 15.9993 | 16.013 | 16.0252 | 16.0502 | 16.0638 | 16.0618 | 16.0556 | 16.0568 | 16.0602 | 16.0608 | 15.0547 | 14.6743 | 14.7055
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.2226 | 9.3982 | 9.5575 | 9.6951 | 9.6851 | 9.6415 | 8.8768 | 8.1047 | 7.3219 | 5.9361 | 5.2666 | 4.638 | 3.3202 | 2.024 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.2226 | 9.2005 | 9.1405 | 9.1257 | 9.0403 | 8.9929 | 8.192 | 7.4236 | 6.5761 | 5.0863 | 4.3324 | 3.632 | 2.1897 | 0.78347 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.2226 | 9.3528 | 9.4977 | 9.6254 | 9.5815 | 9.5842 | 9.5663 | 9.5666 | 9.5346 | 9.5041 | 9.4795 | 9.4112 | 9.3452 | 9.3002 | 6.1315 | 3.2343 | 1.98
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.2226 | 9.1244 | 9.0429 | 8.945 | 8.9369 | 7.5017 | 6.7546 | 5.9289 | 5.0439 | 3.6181 | 2.8989 | 1.514 | 0.13513 | 0 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.2226 | 9.3219 | 9.401 | 9.5169 | 9.5114 | 9.549 | 9.5556 | 9.5426 | 9.4913 | 9.4261 | 8.6335 | 7.8349 | 7.0849 | 6.3729 | 3.0831 | 2.6092 | 2.9321
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.4808 | 15.4999 | 15.1318 | 14.9062 | 14.6232 | 14.3706 | 14.069 | 13.7757 | 13.4683 | 13.2253 | 13.162 | 13.1502 | 13.1939 | 13.2754 | 12.7276 | 12.4684 | 12.2692
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.4808 | 15.4025 | 14.8919 | 14.5815 | 14.2252 | 13.9088 | 13.5274 | 13.2032 | 12.7886 | 12.3785 | 12.1886 | 12.0543 | 11.9315 | 11.8582 | 10.6054 | 10.0046 | 9.8835
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.4808 | 15.6892 | 15.3952 | 15.1867 | 14.9578 | 14.7376 | 14.5048 | 14.2842 | 14.0693 | 13.7994 | 13.6014 | 13.366 | 13.1728 | 13.0186 | 11.5815 | 10.3298 | 9.4836
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.4808 | 15.2917 | 14.7575 | 14.3416 | 14.0029 | 13.6325 | 13.2831 | 12.92 | 12.5471 | 12.2789 | 12.1515 | 12.0855 | 12.0715 | 12.0838 | 11.1898 | 10.7708 | 10.6148
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.4808 | 15.459 | 15.0355 | 14.7544 | 14.4934 | 14.2774 | 14.0496 | 13.8247 | 13.5369 | 13.2825 | 13.1397 | 13.0111 | 12.9181 | 12.8913 | 11.2951 | 10.7513 | 10.5839
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 84.8766 | 76.1317 | 72.5797 | 70.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 84.8766 | 72.1779 | 63.711 | 58.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 84.8766 | 77.6202 | 75.1308 | 73.5408 | 68.5799 | 64.7065 | 60.4208 | 56.3077 | 52.2255 | 47.301 | 10.1982 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 84.8766 | 69.475 | 60.5262 | 52.4207 | 44.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 84.8766 | 74.9728 | 70.2552 | 67.3882 | 62.3574 | 58.7794 | 54.6306 | 50.1948 | 35.8225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 12.5635 | 12.5674 | 12.4973 | 12.4219 | 12.3339 | 12.2184 | 11.4858 | 11.3018 | 11.0798 | 10.8392 | 10.7482 | 10.7015 | 10.6719 | 10.6495 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 12.5635 | 12.5591 | 12.4826 | 12.3643 | 12.1836 | 11.9971 | 11.1675 | 10.8393 | 10.4664 | 10.0409 | 4.7357 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 12.5635 | 12.583 | 12.5448 | 12.4811 | 12.3972 | 12.3057 | 11.7409 | 11.5519 | 11.3544 | 11.1378 | 10.9916 | 10.8576 | 10.7432 | 10.6313 | 4.5956 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 12.5635 | 12.5443 | 12.4457 | 12.2659 | 12.0648 | 11.8433 | 10.9045 | 10.5077 | 10.0708 | 9.6369 | 2.4097 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 12.5635 | 12.5788 | 12.5332 | 12.4213 | 12.3106 | 12.1988 | 11.4673 | 11.2495 | 11.0289 | 10.7844 | 10.6329 | 10.5391 | 10.4545 | 10.418 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 5.798 | 5.764 | 5.5932 | 5.5638 | 5.0335 | 4.7576 | 2.1063 | 1.5197 | 0.83669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 5.798 | 5.6749 | 5.4167 | 5.2292 | 4.3597 | 3.8165 | 0.86722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 5.798 | 5.8462 | 5.8629 | 5.8958 | 5.5692 | 5.4581 | 3.8135 | 3.5918 | 3.3788 | 3.0129 | 2.6315 | 2.2317 | 1.8458 | 1.1526 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 5.798 | 5.4976 | 5.1328 | 4.6901 | 3.8297 | 2.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 5.798 | 5.8185 | 5.7998 | 5.721 | 5.2568 | 5.1075 | 3.0316 | 2.8318 | 2.2396 | 1.2199 | 0.52444 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.9179 | 12.8935 | 12.742 | 12.7051 | 12.5482 | 12.3258 | 12.0117 | 11.8802 | 11.6723 | 11.4842 | 11.5313 | 11.8295 | 12.1121 | 12.4897 | 11.1856 | 2.5345 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.9179 | 12.8458 | 12.6607 | 12.565 | 12.1629 | 11.7232 | 11.1756 | 10.7626 | 10.2561 | 9.6355 | 9.2573 | 7.8289 | 4.3388 | 1.5717 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.9179 | 12.9962 | 13.0722 | 13.1234 | 13.0681 | 12.9961 | 12.8983 | 12.7816 | 12.6319 | 12.3863 | 12.1412 | 11.8692 | 11.6217 | 11.4325 | 8.4034 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.9179 | 12.7383 | 12.5599 | 12.2712 | 11.8948 | 11.4368 | 10.9451 | 10.4283 | 9.9431 | 9.4859 | 8.377 | 5.2184 | 3.3478 | 2.0396 | 0 | 0 | 0
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.9179 | 13.0025 | 13.059 | 13.0803 | 13.0637 | 12.9828 | 12.8646 | 12.7062 | 12.5205 | 12.3144 | 12.0993 | 11.9118 | 11.8602 | 12.001 | 6.4661 | 0.12501 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.9077 | 16.9387 | 16.9473 | 16.9602 | 16.9461 | 16.9041 | 16.7505 | 16.6923 | 16.6286 | 16.6137 | 16.5985 | 16.6345 | 16.6756 | 16.7335 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.9077 | 16.8954 | 16.8585 | 16.8625 | 16.7847 | 16.7173 | 16.5215 | 16.4221 | 16.2993 | 16.2368 | 4.6583 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.9077 | 16.9478 | 16.9863 | 17.0205 | 17.0231 | 17.0255 | 17.036 | 17.0342 | 17.0247 | 17.0009 | 16.9436 | 16.8987 | 16.8577 | 16.8085 | 4.5205 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.9077 | 16.8643 | 16.8393 | 16.7811 | 16.7276 | 16.6516 | 16.5447 | 16.3924 | 16.213 | 12.2168 | 2.3703 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.9077 | 16.939 | 16.9739 | 17.0101 | 17.017 | 17.0282 | 17.0318 | 17.0295 | 16.9904 | 16.9674 | 16.8312 | 16.7217 | 16.6457 | 16.5553 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.0157 | 4.7218 | 3.5011 | 2.3756 | 0.48295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.0157 | 4.6021 | 3.287 | 1.9841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.0157 | 4.8769 | 4.2236 | 3.2604 | 1.8563 | 0.69897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.0157 | 4.4642 | 3.191 | 1.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.0157 | 4.8243 | 3.8836 | 2.768 | 0.9487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.7688 | 15.2833 | 14.8048 | 14.7844 | 14.7374 | 14.6762 | 4.6338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.7688 | 15.2721 | 14.7664 | 14.7109 | 14.566 | 8.0092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.7688 | 15.4108 | 15.1121 | 15.1025 | 15.0632 | 15.0122 | 14.8348 | 13.0641 | 3.5109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.7688 | 15.1994 | 14.6972 | 14.5566 | 14.3965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.7688 | 15.3032 | 14.8494 | 14.8004 | 14.755 | 14.7114 | 12.9334 | 2.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.6645 | 7.6632 | 7.63 | 7.6155 | 7.5603 | 7.5028 | 7.0671 | 6.6711 | 6.249 | 5.476 | 5.0961 | 4.7518 | 4.0481 | 3.3639 | 0.022799 | 0 | 0
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.6645 | 7.64 | 7.5878 | 7.5444 | 7.4655 | 7.3774 | 6.9127 | 6.4788 | 6.0153 | 5.192 | 4.7686 | 4.3757 | 3.6226 | 2.8922 | 0 | 0 | 0
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.6645 | 7.6809 | 7.6953 | 7.7125 | 7.6875 | 7.6711 | 7.6457 | 7.6214 | 7.5833 | 7.509 | 7.4313 | 7.3513 | 7.2799 | 7.2204 | 5.354 | 3.566 | 2.5857
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.6645 | 7.6266 | 7.586 | 7.5185 | 7.4397 | 6.6386 | 6.176 | 5.7106 | 5.2438 | 4.4548 | 4.0469 | 3.3125 | 2.6109 | 1.9109 | 0 | 0 | 0
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.6645 | 7.6681 | 7.6706 | 7.666 | 7.6353 | 7.6092 | 7.5663 | 7.5064 | 7.4347 | 7.3666 | 6.9476 | 6.53 | 6.1296 | 5.7725 | 3.7987 | 3.26 | 3.2171
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 8.8616 | 8.7919 | 8.6552 | 8.6988 | 8.5979 | 8.3966 | 8.1132 | 7.9218 | 7.5653 | 7.2176 | 7.1339 | 7.3045 | 7.4581 | 7.6725 | 6.3832 | 5.3158 | 4.2543
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 8.8616 | 8.6757 | 8.3931 | 8.264 | 7.8795 | 7.4781 | 6.9322 | 6.4771 | 5.8061 | 4.9246 | 4.3617 | 4.0655 | 3.7623 | 3.5563 | 0.11259 | 0 | 0
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 8.8616 | 8.8811 | 8.9026 | 8.9783 | 8.9683 | 8.9154 | 8.8554 | 8.7516 | 8.5831 | 8.328 | 8.1391 | 7.9279 | 7.7346 | 7.5664 | 4.8395 | 2.0181 | 0
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 8.8616 | 8.4959 | 8.113 | 7.7595 | 7.4682 | 7.0733 | 6.6324 | 6.101 | 5.4563 | 4.7317 | 4.2374 | 3.9512 | 3.8361 | 3.8475 | 2.0007 | 1.8721 | 1.5367
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 8.8616 | 8.8592 | 8.8276 | 8.8328 | 8.8572 | 8.8325 | 8.7558 | 8.6107 | 8.3737 | 8.0751 | 7.8126 | 7.5948 | 7.4659 | 7.5051 | 4.4759 | 3.7025 | 2.9875
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.9475 | 15.8569 | 15.7078 | 15.5834 | 15.2783 | 15.0079 | 14.3651 | 13.6942 | 13.061 | 12.1754 | 11.711 | 11.3326 | 10.696 | 10.0959 | 6.2001 | 4.4607 | 3.7779
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.9475 | 15.7407 | 15.4393 | 15.2349 | 14.7798 | 14.391 | 13.5884 | 12.8218 | 12.0184 | 10.8559 | 10.1756 | 9.598 | 8.6639 | 7.809 | 2.8593 | 0.48514 | 0
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.9475 | 15.8707 | 15.7759 | 15.708 | 15.4798 | 15.3095 | 15.1282 | 14.9332 | 14.7684 | 14.5658 | 14.3668 | 14.1498 | 13.9372 | 13.7547 | 10.8739 | 8.2725 | 6.3882
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.9475 | 15.6441 | 15.3367 | 15.0138 | 14.5746 | 13.4506 | 12.6673 | 11.8437 | 11.0759 | 10.0732 | 9.4839 | 8.6256 | 7.8439 | 7.1121 | 2.8865 | 1.0309 | 0.54097
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.9475 | 15.8547 | 15.7209 | 15.601 | 15.356 | 15.1751 | 14.9767 | 14.7641 | 14.5435 | 14.36 | 13.8049 | 13.2693 | 12.7611 | 12.3677 | 9.3047 | 8.3321 | 7.6864
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 13.8715 | 13.9542 | 14.0418 | 14.0891 | 14.0316 | 13.9363 | 13.4807 | 13.0324 | 12.5201 | 11.6261 | 11.1815 | 10.8394 | 10.117 | 9.3969 | 6.2268 | 2.5361 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 13.8715 | 13.8825 | 13.9004 | 13.8842 | 13.6753 | 13.4811 | 12.9106 | 12.4002 | 11.8016 | 10.7946 | 10.2237 | 7.8337 | 4.3415 | 1.5726 | 0 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 13.8715 | 13.9798 | 14.1321 | 14.196 | 14.1989 | 14.2187 | 14.2656 | 14.277 | 14.2856 | 14.273 | 14.2572 | 14.2305 | 14.1882 | 14.1453 | 11.7325 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 13.8715 | 13.8011 | 13.7948 | 13.6544 | 13.4461 | 12.5308 | 12.0311 | 11.5019 | 10.9635 | 10.0429 | 8.3821 | 5.2216 | 3.3498 | 2.0409 | 0 | 0 | 0
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 13.8715 | 13.9854 | 14.1384 | 14.2136 | 14.204 | 14.1817 | 14.2051 | 14.2089 | 14.2013 | 14.1091 | 13.6646 | 13.196 | 12.7459 | 12.3426 | 6.4701 | 0.12508 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.8117 | 10.8016 | 10.6924 | 10.6873 | 10.5721 | 10.3961 | 9.8167 | 9.3418 | 8.8064 | 7.8711 | 7.4757 | 7.298 | 6.7569 | 6.2746 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.8117 | 10.7617 | 10.617 | 10.5371 | 10.1604 | 9.7508 | 8.9254 | 8.1898 | 7.3839 | 6.0592 | 4.7037 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.8117 | 10.8921 | 10.941 | 10.9892 | 10.9608 | 10.929 | 10.8751 | 10.7959 | 10.7017 | 10.5038 | 10.2905 | 10.0596 | 9.8519 | 9.6816 | 4.5646 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.8117 | 10.6311 | 10.4282 | 10.1559 | 9.8054 | 8.6937 | 7.9142 | 7.0843 | 6.2854 | 5.1141 | 2.3934 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.8117 | 10.8995 | 10.9291 | 10.9378 | 10.9318 | 10.8767 | 10.7937 | 10.6765 | 10.5315 | 10.3464 | 9.7788 | 9.2269 | 8.7745 | 8.4642 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 21.2659 | 21.0455 | 20.9836 | 20.9453 | 20.8827 | 17.9178 | 4.6647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.2659 | 21.0395 | 20.974 | 20.9225 | 19.2608 | 8.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.2659 | 21.102 | 21.0887 | 21.0765 | 21.0476 | 21.0237 | 20.9876 | 13.1512 | 3.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.2659 | 21.0018 | 20.9424 | 20.8557 | 14.7307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.2659 | 21.0711 | 21.0698 | 21.0568 | 21.0432 | 21.0104 | 13.0196 | 2.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.3578 | 18.2626 | 17.8316 | 17.2488 | 16.2166 | 15.7165 | 15.0468 | 14.6545 | 14.1424 | 13.6604 | 13.4429 | 13.5291 | 13.6289 | 13.7689 | 11.1799 | 2.5332 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.3578 | 18.2085 | 17.7261 | 17.0286 | 15.7293 | 14.981 | 13.979 | 13.1796 | 12.2243 | 11.1945 | 10.5267 | 7.8249 | 4.3366 | 1.5709 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.3578 | 18.3513 | 18.1575 | 17.6684 | 16.9244 | 16.568 | 16.1236 | 15.7423 | 15.3339 | 14.8638 | 14.457 | 14.0835 | 13.7501 | 13.4729 | 10.9168 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.3578 | 18.1266 | 17.6339 | 16.6825 | 15.3268 | 14.4684 | 13.4645 | 12.5761 | 11.6871 | 10.9208 | 8.3728 | 5.2157 | 3.3461 | 2.0386 | 0 | 0 | 0
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.3578 | 18.3399 | 18.0502 | 17.4544 | 16.4521 | 16.0193 | 15.4499 | 14.9845 | 14.4652 | 13.9201 | 13.4722 | 13.1578 | 12.9718 | 12.9379 | 6.4629 | 0.12494 | 0
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 26.7576 | 26.508 | 24.1146 | 21.8325 | 18.8808 | 18.3332 | 17.8226 | 17.4396 | 16.4317 | 15.5205 | 14.6574 | 14.2951 | 13.7548 | 13.2884 | 10.3726 | 8.9826 | 8.6144
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 26.7576 | 26.4024 | 23.9089 | 21.4965 | 18.3474 | 17.6655 | 17.0084 | 16.4468 | 15.257 | 14.0725 | 12.9518 | 12.3217 | 11.5102 | 10.7975 | 6.5601 | 4.6343 | 4.3254
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 26.7576 | 26.6005 | 26.3791 | 26.2872 | 26.0706 | 25.8737 | 25.6834 | 25.4673 | 25.0839 | 24.641 | 24.0972 | 23.6192 | 23.1499 | 22.7363 | 19.6181 | 17.4771 | 15.6543
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 26.7576 | 26.2733 | 25.6686 | 25.2325 | 24.7665 | 24.0468 | 23.3851 | 22.754 | 21.9099 | 21.0596 | 20.4811 | 20.0889 | 19.6217 | 19.3831 | 16.7092 | 15.9359 | 15.7882
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 26.7576 | 26.5738 | 26.2279 | 26.1033 | 25.9195 | 25.7835 | 25.6275 | 25.2059 | 24.5426 | 23.7924 | 23.1652 | 22.8603 | 22.6029 | 22.3624 | 19.6021 | 19.1046 | 18.581
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 36.5085 | 28.9596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 36.5085 | 17.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 36.5085 | 32.5321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 36.5085 | 5.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 36.5085 | 31.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.2663 | 5.259 | 5.1314 | 5.1568 | 4.9992 | 4.7806 | 4.4474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.2663 | 5.1506 | 4.9378 | 4.8557 | 4.441 | 4.0388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.2663 | 5.3587 | 5.4894 | 5.5963 | 5.55 | 5.505 | 5.4328 | 5.3218 | 3.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.2663 | 4.9938 | 4.7741 | 4.4882 | 4.1477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.2663 | 5.3763 | 5.4883 | 5.5891 | 5.6297 | 5.6459 | 5.5992 | 2.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.98848 | 1.2009 | 0.91796 | 0.40302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.98848 | 0.8592 | 0.24916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.98848 | 1.3547 | 1.526 | 1.2449 | 0.79842 | 0.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.98848 | 0.45318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.98848 | 1.2714 | 0.95627 | 0.44533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.0549 | 2.9146 | 2.7969 | 2.7373 | 2.5974 | 2.4734 | 2.3268 | 2.1972 | 1.8702 | 1.7102 | 1.5967 | 1.5397 | 1.4814 | 0.88287 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.0549 | 2.8361 | 2.6123 | 2.452 | 2.2536 | 2.1071 | 1.9207 | 1.7515 | 1.4072 | 1.1992 | 1.0531 | 0.95599 | 0.87955 | 0.25984 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.0549 | 2.9658 | 2.9063 | 2.8687 | 2.721 | 2.6107 | 2.5196 | 2.4142 | 2.3066 | 2.1185 | 1.9474 | 1.764 | 1.5831 | 1.4059 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.0549 | 2.7671 | 2.5269 | 2.2972 | 2.1288 | 1.9741 | 1.8352 | 1.6039 | 1.1451 | 1.0266 | 0.92127 | 0.842 | 0.79261 | 0.76118 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.0549 | 2.891 | 2.751 | 2.6403 | 2.4565 | 2.1184 | 1.8028 | 1.3777 | 1.0838 | 0.32382 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.54401 | 0.66094 | 0.5052 | 0.5369 | 0.30866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.54401 | 0.47286 | 0.13713 | 0.022799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.54401 | 0.74553 | 0.83984 | 1.022 | 0.9339 | 0.89457 | 0.80353 | 0.72121 | 0.5951 | 0.26667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.54401 | 0.24941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.54401 | 0.69974 | 0.72195 | 0.82747 | 0.80563 | 0.74497 | 0.35813 | 0.16413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.324 | 8.3599 | 8.3556 | 8.386 | 8.3667 | 8.3428 | 8.2962 | 8.2521 | 8.0912 | 8.0557 | 8.0692 | 8.1394 | 8.2144 | 8.3124 | 7.8677 | 6.8776 | 6.3101
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.324 | 8.3043 | 8.2518 | 8.2136 | 8.1273 | 8.0605 | 7.9746 | 7.8818 | 7.7256 | 7.6114 | 7.5553 | 7.5534 | 7.5688 | 7.6058 | 6.5661 | 2.2652 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.324 | 8.3789 | 8.4294 | 8.4744 | 8.4476 | 8.4488 | 8.4427 | 8.4228 | 8.3924 | 8.3267 | 8.2612 | 8.1924 | 8.1277 | 8.0783 | 6.8096 | 5.7772 | 4.5529
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.324 | 8.2682 | 8.2113 | 8.1214 | 8.0494 | 7.9853 | 7.9092 | 7.7734 | 7.5407 | 7.4803 | 7.4551 | 7.4706 | 7.5238 | 7.6098 | 7.158 | 6.0749 | 2.3807
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.324 | 8.353 | 8.3733 | 8.3804 | 8.3567 | 8.3356 | 8.1883 | 8.1502 | 8.071 | 7.9999 | 7.5909 | 7.5324 | 7.4927 | 7.5031 | 5.8822 | 5.0366 | 4.2385
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.9111 | 2.7774 | 2.6652 | 2.6084 | 2.4752 | 2.357 | 2.2172 | 2.0938 | 1.7822 | 1.6297 | 1.5215 | 1.4673 | 1.4116 | 0.84131 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.9111 | 2.7026 | 2.4893 | 2.3366 | 2.1476 | 2.0079 | 1.8303 | 1.6691 | 1.3409 | 1.1427 | 1.0035 | 0.91099 | 0.83815 | 0.24761 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.9111 | 2.8262 | 2.7695 | 2.7337 | 2.5929 | 2.4878 | 2.401 | 2.3006 | 2.198 | 2.0188 | 1.8557 | 1.681 | 1.5086 | 1.3397 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.9111 | 2.6368 | 2.408 | 2.1891 | 2.0285 | 1.8812 | 1.7488 | 1.5284 | 1.0912 | 0.9783 | 0.8779 | 0.80236 | 0.7553 | 0.72535 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.9111 | 2.7549 | 2.6215 | 2.516 | 2.3409 | 2.0187 | 1.718 | 1.3128 | 1.0328 | 0.30858 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 89.8504 | 89.3383 | 88.3779 | 87.4416 | 86.0175 | 84.4436 | 82.5168 | 80.9389 | 78.6708 | 76.7025 | 75.1415 | 74.1543 | 72.0452 | 70.924 | 58.4709 | 47.3257 | 36.8412
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 89.8504 | 88.9767 | 87.6218 | 86.2122 | 83.854 | 81.5345 | 78.6753 | 75.8522 | 72.2723 | 68.3176 | 64.8452 | 61.8233 | 57.7914 | 54.8642 | 26.1669 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 89.8504 | 89.6605 | 89.3504 | 88.7443 | 87.558 | 86.4768 | 85.3101 | 84.0025 | 82.6533 | 80.7157 | 78.7737 | 76.7399 | 74.7563 | 72.8532 | 57.8574 | 40.5181 | 6.781
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 89.8504 | 88.5184 | 87.0342 | 84.8392 | 82.4383 | 79.8556 | 77.0336 | 73.7134 | 69.83 | 66.7295 | 63.7791 | 61.7127 | 60.6289 | 59.878 | 48.8334 | 15.3984 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 89.8504 | 89.4282 | 88.7994 | 87.7576 | 86.3081 | 84.0968 | 82.1692 | 79.8391 | 76.459 | 73.6169 | 70.0355 | 66.455 | 64.1977 | 61.7847 | 42.44 | 19.2723 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.8749 | 5.7722 | 5.6483 | 5.6121 | 5.4555 | 5.2933 | 5.0645 | 4.8976 | 4.4775 | 4.2173 | 4.0607 | 4.0281 | 3.9704 | 3.4017 | 0.97582 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.8749 | 5.6705 | 5.431 | 5.2645 | 4.9851 | 4.751 | 4.4189 | 4.1331 | 3.6574 | 3.244 | 2.9458 | 2.7631 | 2.577 | 1.8883 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.8749 | 5.828 | 5.8051 | 5.7916 | 5.6314 | 5.5043 | 5.381 | 5.2361 | 5.0718 | 4.7788 | 4.5095 | 4.222 | 3.935 | 3.6663 | 0.20294 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.8749 | 5.5913 | 5.3558 | 5.0837 | 4.844 | 4.5804 | 4.2909 | 3.9104 | 3.3045 | 3.0166 | 2.7637 | 2.5954 | 2.5059 | 2.4487 | 0.4195 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.8749 | 5.747 | 5.6582 | 5.5605 | 5.3824 | 5.0186 | 4.649 | 4.4214 | 4.063 | 3.2213 | 2.3614 | 2.0256 | 1.7422 | 1.5936 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.69848 | 0.84861 | 0.64865 | 0.68935 | 0.3963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.69848 | 0.60713 | 0.17606 | 0.029272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.69848 | 0.95723 | 1.0783 | 1.3121 | 1.1991 | 1.1486 | 1.0317 | 0.926 | 0.76408 | 0.34239 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.69848 | 0.32022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.69848 | 0.89843 | 0.92694 | 1.0624 | 1.0344 | 0.9565 | 0.45982 | 0.21073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.9078 | 7.8984 | 7.8589 | 7.8426 | 7.7773 | 7.7162 | 7.6394 | 7.5652 | 7.4325 | 7.3611 | 7.3221 | 7.3234 | 7.3316 | 7.3605 | 6.8198 | 5.7224 | 5.0334
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.9078 | 7.8448 | 7.7566 | 7.6775 | 7.5721 | 7.4904 | 7.3896 | 7.2843 | 7.1259 | 7.0129 | 6.9434 | 6.9125 | 6.897 | 6.8997 | 5.9991 | 2.2432 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.9078 | 7.9086 | 7.9088 | 7.905 | 7.8311 | 7.7851 | 7.7395 | 7.682 | 7.614 | 7.5235 | 7.4332 | 7.3419 | 7.2512 | 7.1708 | 5.8763 | 4.7426 | 3.7416
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.9078 | 7.8159 | 7.7226 | 7.605 | 7.5184 | 7.437 | 7.3508 | 7.2199 | 7.0454 | 6.9715 | 6.9197 | 6.8963 | 6.9036 | 6.9404 | 6.4572 | 5.2812 | 2.3576
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.9078 | 7.8827 | 7.8527 | 7.8152 | 7.7401 | 7.6781 | 7.4916 | 7.4208 | 7.3099 | 7.201 | 6.7519 | 6.6503 | 6.5579 | 6.5121 | 4.8428 | 3.8901 | 3.0409
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.5216 | 6.4905 | 6.4404 | 6.412 | 6.3265 | 6.2128 | 6.0774 | 5.9881 | 5.8759 | 5.7121 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.5216 | 6.4802 | 6.396 | 6.339 | 6.2096 | 6.0462 | 5.85 | 5.6648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.5216 | 6.5366 | 6.5459 | 6.5474 | 6.4835 | 6.4213 | 6.3646 | 6.2982 | 6.2392 | 6.1147 | 5.9807 | 5.8598 | 5.7115 | 5.581 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.5216 | 6.4419 | 6.3601 | 6.245 | 6.1069 | 5.9345 | 5.7286 | 5.5102 | 5.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.5216 | 6.5152 | 6.4963 | 6.4789 | 6.4014 | 6.3162 | 6.2293 | 6.1334 | 6.0048 | 5.8729 | 5.7291 | 5.5949 | 5.4829 | 5.4228 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.5087 | 8.3672 | 8.0158 | 7.6173 | 7.0592 | 6.4067 | 5.6037 | 4.9512 | 4.1282 | 3.3067 | 2.6342 | 2.1766 | 1.1641 | 0.90263 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.5087 | 8.2765 | 7.8285 | 7.305 | 6.3597 | 5.3799 | 4.1665 | 2.9607 | 1.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.5087 | 8.4852 | 8.3838 | 8.1223 | 7.6886 | 7.258 | 6.7719 | 6.2336 | 5.6829 | 4.9128 | 4.1292 | 3.3085 | 2.5117 | 1.7408 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.5087 | 8.1178 | 7.6226 | 6.7876 | 5.7931 | 4.6888 | 3.4516 | 2.057 | 0.56046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.5087 | 8.4378 | 8.2529 | 7.8499 | 7.3128 | 6.4589 | 5.8016 | 5.0539 | 3.6544 | 2.7443 | 1.6791 | 0.68749 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.383 | 12.3746 | 12.2934 | 12.2702 | 12.2082 | 12.1393 | 12.07 | 12.0459 | 11.913 | 11.8154 | 11.8088 | 11.9 | 11.9901 | 12.1115 | 10.9811 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.383 | 12.3454 | 12.2423 | 12.1569 | 11.9568 | 11.7645 | 11.5473 | 11.3758 | 11.1244 | 10.7897 | 10.5709 | 10.4465 | 10.3289 | 10.2661 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.383 | 12.4225 | 12.4354 | 12.4423 | 12.4045 | 12.3819 | 12.3689 | 12.3404 | 12.3054 | 12.1804 | 12.0697 | 11.9441 | 11.8223 | 11.7191 | 10.2721 | 8.832 | 4.5669
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.383 | 12.2954 | 12.1755 | 12.0022 | 11.7895 | 11.5689 | 11.3658 | 11.1269 | 10.8261 | 10.6011 | 10.4447 | 10.3655 | 10.3643 | 10.3949 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.383 | 12.3978 | 12.3809 | 12.3442 | 12.2838 | 12.2262 | 12.1702 | 12.1003 | 11.977 | 11.8601 | 11.7271 | 11.6226 | 11.5661 | 11.5962 | 9.8162 | 9.0287 | 6.9998
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 50.7797 | 50.4642 | 49.4043 | 49.2066 | 47.6366 | 39.5809 | 33.7647 | 28.3323 | 21.1055 | 11.1227 | 5.5662 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 50.7797 | 49.411 | 36.3824 | 22.6994 | 3.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 50.7797 | 50.9986 | 51.2226 | 51.711 | 50.8306 | 50.254 | 49.4039 | 48.5871 | 47.2867 | 43.8641 | 40.6778 | 36.6398 | 32.5429 | 28.4991 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 50.7797 | 48.2601 | 45.9322 | 43.3806 | 40.5959 | 31.1898 | 24.3016 | 16.4859 | 7.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 50.7797 | 50.6041 | 50.3343 | 50.3812 | 49.6724 | 48.4451 | 46.7616 | 44.43 | 41.1497 | 35.9825 | 28.5471 | 21.8948 | 16.2603 | 11.0866 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.2229 | 8.0862 | 7.7466 | 7.3614 | 6.8221 | 6.1915 | 5.4155 | 4.7849 | 3.9895 | 3.1956 | 2.5457 | 2.1035 | 1.125 | 0.87232 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.2229 | 7.9986 | 7.5656 | 7.0597 | 6.1461 | 5.1992 | 4.0266 | 2.8613 | 1.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.2229 | 8.2002 | 8.1022 | 7.8495 | 7.4304 | 7.0143 | 6.5445 | 6.0242 | 5.492 | 4.7478 | 3.9905 | 3.1974 | 2.4274 | 1.6823 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.2229 | 7.8452 | 7.3666 | 6.5596 | 5.5985 | 4.5313 | 3.3357 | 1.988 | 0.54164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.2229 | 8.1544 | 7.9758 | 7.5863 | 7.0672 | 6.242 | 5.6068 | 4.8842 | 3.5317 | 2.6521 | 1.6227 | 0.6644 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.5322 | 12.2326 | 11.8902 | 11.6674 | 11.323 | 10.0819 | 9.3239 | 8.6904 | 7.917 | 6.746 | 6.1999 | 5.523 | 4.8195 | 4.1636 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.5322 | 12.1835 | 11.7746 | 11.4172 | 10.7599 | 9.9938 | 8.8527 | 7.8867 | 6.792 | 5.0362 | 3.9798 | 3.1406 | 1.913 | 0.78933 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.5322 | 12.3916 | 12.2914 | 12.1394 | 11.8782 | 11.52 | 11.2735 | 11.0118 | 10.7712 | 10.3206 | 9.8925 | 9.1133 | 8.3461 | 7.605 | 2.6132 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.5322 | 12.0446 | 11.6156 | 11.0361 | 10.357 | 8.7648 | 7.6886 | 6.5956 | 5.4573 | 4.0021 | 3.099 | 1.9479 | 0.95217 | 0.0075221 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.5322 | 12.3417 | 12.1947 | 11.9628 | 11.664 | 11.2313 | 10.9047 | 10.551 | 9.7988 | 8.5963 | 7.8129 | 7.0742 | 6.4075 | 5.9146 | 0.46967 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 57.0843 | 56.1158 | 54.5715 | 53.8324 | 52.0553 | 47.5316 | 44.2966 | 41.6252 | 37.0142 | 32.3601 | 30.2072 | 28.4535 | 26.6062 | 24.9253 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 57.0843 | 55.3454 | 53.0794 | 51.2188 | 47.756 | 44.0668 | 38.9168 | 34.4726 | 28.3643 | 20.5252 | 15.4606 | 11.9266 | 6.746 | 2.272 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 57.0843 | 56.8036 | 56.5877 | 56.2875 | 54.906 | 53.4756 | 52.3275 | 51.0757 | 49.5163 | 46.9024 | 44.453 | 41.2101 | 38.0198 | 35.0425 | 1.7914 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 57.0843 | 54.4957 | 52.0918 | 48.9505 | 45.5715 | 39.2916 | 34.4804 | 29.1517 | 22.4155 | 16.2766 | 12.1886 | 8.0186 | 5.0173 | 2.6143 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 57.0843 | 56.2814 | 55.5266 | 54.51 | 52.912 | 50.5603 | 48.5046 | 46.6078 | 42.9038 | 37.9178 | 32.6129 | 28.8315 | 25.6743 | 23.8554 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.5783 | 8.3726 | 8.0532 | 7.8994 | 7.4839 | 6.6115 | 5.9731 | 5.4201 | 4.3999 | 3.53 | 2.5369 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.5783 | 8.1567 | 7.65 | 7.245 | 6.5576 | 5.825 | 4.8543 | 4.0138 | 2.7313 | 1.3377 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.5783 | 8.4771 | 8.3977 | 8.3362 | 8.0098 | 7.692 | 7.4178 | 7.1474 | 6.7423 | 6.1896 | 5.6789 | 5.1422 | 4.618 | 4.1329 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.5783 | 7.9813 | 7.4448 | 6.8044 | 6.1694 | 5.0316 | 4.1369 | 3.1457 | 1.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.5783 | 8.3425 | 8.1181 | 7.8884 | 7.5178 | 6.9549 | 6.5738 | 6.1697 | 5.4212 | 4.5975 | 3.8342 | 3.1294 | 2.5497 | 2.2186 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.54439 | 0.66139 | 0.50555 | 0.53727 | 0.30887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.54439 | 0.47319 | 0.13722 | 0.022815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.54439 | 0.74605 | 0.84042 | 1.0227 | 0.93454 | 0.89519 | 0.80408 | 0.72171 | 0.59551 | 0.26686 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.54439 | 0.24958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.54439 | 0.70022 | 0.72245 | 0.82804 | 0.80619 | 0.74549 | 0.35838 | 0.16424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.472 | 22.5622 | 22.5699 | 22.6595 | 22.5093 | 21.6598 | 21.0438 | 20.4956 | 19.7564 | 18.6491 | 18.0439 | 17.3239 | 16.5038 | 15.6997 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.472 | 22.411 | 16.8224 | 10.4978 | 2.3097 | 1.1875 | 0.25536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.472 | 22.5853 | 22.7527 | 22.9087 | 22.8521 | 22.8383 | 22.7953 | 22.7438 | 22.6534 | 21.8395 | 21.1361 | 20.0608 | 18.9746 | 17.8787 | 13.5661 | 4.7035 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.472 | 22.2195 | 22.0218 | 21.7651 | 21.4309 | 20.3853 | 19.6068 | 18.7097 | 17.7059 | 16.3634 | 15.4122 | 14.2398 | 11.0719 | 7.1596 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.472 | 22.6115 | 22.7803 | 22.9176 | 22.9185 | 22.9151 | 22.8726 | 22.4385 | 21.9106 | 20.9302 | 20.2259 | 19.5228 | 18.871 | 18.0279 | 10.141 | 1.1201 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.4767 | 8.4843 | 8.4728 | 8.4632 | 8.3497 | 8.2585 | 8.159 | 8.051 | 7.8955 | 7.7677 | 7.651 | 5.2496 | 2.2135 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.4767 | 8.4366 | 8.3865 | 8.3341 | 8.1914 | 8.0854 | 7.961 | 7.8444 | 7.7071 | 5.082 | 0.32685 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.4767 | 8.4837 | 8.4888 | 8.4866 | 8.3894 | 8.3081 | 8.2314 | 8.1658 | 8.0874 | 7.9714 | 7.8507 | 7.7244 | 7.6187 | 7.5103 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.4767 | 8.4178 | 8.3676 | 8.2904 | 8.1603 | 8.0262 | 7.9013 | 7.7622 | 6.9348 | 1.7201 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.4767 | 8.4548 | 8.434 | 8.4056 | 8.2766 | 8.1677 | 8.0684 | 7.8191 | 7.7022 | 7.5539 | 7.3919 | 6.9176 | 6.8337 | 5.9753 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.865 | 16.5021 | 16.1658 | 16.0602 | 15.8966 | 15.5176 | 13.332 | 10.4848 | 6.2344 | 1.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.865 | 16.4462 | 16.072 | 15.9168 | 15.5663 | 12.8855 | 8.8585 | 4.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.865 | 16.6094 | 16.4288 | 16.3612 | 16.2396 | 15.9141 | 15.5886 | 15.2989 | 14.9735 | 14.5076 | 14.0155 | 13.4787 | 12.8831 | 12.422 | 0.80349 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.865 | 16.3263 | 15.9266 | 15.6257 | 15.2917 | 14.6395 | 13.9928 | 13.3319 | 12.6443 | 11.7019 | 7.7071 | 4.214 | 1.5669 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.865 | 16.513 | 16.2469 | 16.1479 | 16.0216 | 15.6815 | 15.2562 | 14.819 | 14.2899 | 13.7262 | 13.0611 | 12.4294 | 11.9785 | 11.8106 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 23.2457 | 13.9741 | 11.9157 | 10.5023 | 9.2902 | 8.6544 | 7.4258 | 6.8295 | 6.0198 | 3.9942 | 3.2725 | 3.2483 | 2.8886 | 2.735 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 23.2457 | 14.2563 | 12.0908 | 10.5398 | 8.4316 | 7.0316 | 4.9213 | 3.4563 | 1.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 23.2457 | 16.6303 | 15.4089 | 14.231 | 13.1234 | 12.525 | 11.8487 | 11.2803 | 10.6827 | 9.337 | 8.1521 | 6.9688 | 6.076 | 5.4015 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 23.2457 | 13.3995 | 11.1401 | 8.8248 | 6.8386 | 4.697 | 2.8126 | 1.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 23.2457 | 14.5924 | 12.9253 | 11.6294 | 10.4107 | 9.8639 | 9.1882 | 8.5387 | 7.9055 | 6.6901 | 5.1472 | 3.9502 | 2.4096 | 2.0063 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.9736 | 0.11137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.9736 | 1.7353 | 1.5639 | 1.394 | 1.1242 | 0.88368 | 0.6493 | 0.41862 | 0.16475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.9736 | 0.19221 | 0.069388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.9505 | 11.7368 | 11.5381 | 11.48 | 11.285 | 11.008 | 10.2388 | 9.6874 | 8.3923 | 2.5598 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.9505 | 11.6696 | 11.4323 | 11.2755 | 10.7327 | 10.163 | 9.0884 | 5.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.9505 | 11.8878 | 11.9318 | 11.9692 | 11.8881 | 11.8185 | 11.7103 | 11.5872 | 11.4253 | 11.0625 | 10.6989 | 10.3131 | 9.927 | 9.5819 | 4.9595 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.9505 | 11.5333 | 11.2321 | 10.8431 | 10.3163 | 9.0476 | 8.0377 | 7.0302 | 5.9784 | 4.4883 | 2.5608 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.9505 | 11.8434 | 11.8759 | 11.8417 | 11.7586 | 11.6266 | 11.4233 | 11.225 | 10.9555 | 10.5866 | 9.8474 | 9.1158 | 8.4764 | 8.0532 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 34.5096 | 33.0897 | 27.7296 | 22.3438 | 15.3879 | 13.3728 | 10.763 | 8.6332 | 5.7276 | 1.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 34.5096 | 32.9096 | 27.4303 | 21.7113 | 13.6986 | 10.7632 | 7.108 | 3.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 34.5096 | 33.7916 | 33.3432 | 32.7196 | 31.7594 | 30.9107 | 30.2263 | 29.3703 | 28.5081 | 27.0283 | 25.5839 | 23.823 | 22.1217 | 20.644 | 4.1364 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 34.5096 | 32.3973 | 30.6717 | 28.4394 | 25.7793 | 21.0053 | 17.5743 | 13.5925 | 9.4061 | 4.7808 | 1.7477 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 34.5096 | 33.4665 | 32.7308 | 31.8234 | 30.6156 | 29.4314 | 28.5054 | 27.0653 | 25.5165 | 23.538 | 21.0989 | 18.7743 | 16.45 | 14.9158 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.3021 | 9.0467 | 8.1979 | 7.4035 | 6.391 | 5.2355 | 4.6697 | 4.166 | 3.6375 | 2.6311 | 2.0478 | 1.3352 | 0.63035 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.3021 | 9.0503 | 8.1793 | 7.4417 | 6.3889 | 5.8415 | 5.1767 | 4.5542 | 3.7932 | 2.603 | 1.8552 | 1.2445 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.3021 | 9.1882 | 8.6755 | 8.1032 | 7.4593 | 7.1242 | 6.9751 | 6.8099 | 6.6384 | 6.3364 | 6.0472 | 5.7349 | 5.445 | 5.2183 | 2.6511 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.3021 | 8.9504 | 8.0799 | 7.1055 | 6.0094 | 4.5973 | 3.9762 | 3.0882 | 1.7875 | 0.81784 | 0.19513 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.3021 | 9.12 | 8.3585 | 7.6812 | 6.6403 | 6.2851 | 5.9518 | 5.7589 | 4.9403 | 4.6632 | 4.0809 | 3.5197 | 3.028 | 2.6315 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.6422 | 9.3722 | 8.7755 | 8.4286 | 7.5836 | 6.6766 | 5.0823 | 2.9978 | 1.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.6422 | 9.2694 | 8.574 | 8.0361 | 6.5611 | 5.1389 | 2.9477 | 0.19116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.6422 | 9.5948 | 9.4098 | 9.2383 | 8.6621 | 8.0831 | 7.3923 | 6.2872 | 5.2268 | 3.7249 | 2.3885 | 0.67873 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.6422 | 8.949 | 8.1365 | 7.1096 | 5.5798 | 3.2176 | 1.0209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.6422 | 9.5132 | 9.2073 | 8.864 | 8.1176 | 7.4031 | 6.4617 | 4.6854 | 2.7755 | 0.3439 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.5732 | 11.765 | 10.774 | 10.092 | 9.1572 | 8.5395 | 7.3272 | 6.7388 | 5.9399 | 3.9412 | 3.229 | 3.2051 | 2.8502 | 2.6987 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.5732 | 11.7277 | 10.719 | 9.9849 | 8.3196 | 6.9382 | 4.8559 | 3.4104 | 1.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.5732 | 12.0117 | 11.3947 | 10.7908 | 10.094 | 9.8409 | 9.6544 | 9.4537 | 9.2322 | 8.8919 | 8.0438 | 6.8763 | 5.9953 | 5.3298 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.5732 | 11.5869 | 10.5659 | 8.7076 | 6.7477 | 4.6346 | 2.7752 | 0.98877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.5732 | 11.8299 | 10.9609 | 10.3044 | 9.4373 | 9.2237 | 9.0467 | 8.4253 | 7.8005 | 6.6013 | 5.0788 | 3.8978 | 2.3776 | 1.9796 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.45463 | 0.35096 | 0.13534 | 0.029477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.45463 | 0.33339 | 0.10956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.45463 | 0.46159 | 0.45523 | 0.42196 | 0.32199 | 0.23208 | 0.11073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.45463 | 0.27228 | 0.07078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.45463 | 0.43732 | 0.39571 | 0.32488 | 0.19007 | 0.04921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 13.6046 | 12.8794 | 11.603 | 10.8237 | 10.6054 | 10.4101 | 10.1452 | 9.9576 | 9.6832 | 9.3284 | 9.1096 | 9.0657 | 9.0376 | 9.0755 | 7.6574 | 6.698 | 4.7851
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.6046 | 12.856 | 11.569 | 10.7291 | 10.2996 | 9.9219 | 9.4683 | 9.0704 | 8.5398 | 7.8004 | 7.2363 | 6.8252 | 6.4444 | 6.1546 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.6046 | 13.0819 | 12.256 | 11.553 | 11.3521 | 11.1993 | 11.05 | 10.8696 | 10.6803 | 10.3613 | 10.0535 | 9.7361 | 9.4414 | 9.219 | 6.0352 | 1.7704 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.6046 | 12.6895 | 11.3892 | 10.2681 | 9.7922 | 9.3662 | 8.925 | 8.4328 | 7.9038 | 7.3997 | 6.9747 | 6.6878 | 6.4992 | 6.3491 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.6046 | 12.9368 | 11.783 | 11.0117 | 10.8346 | 10.6866 | 10.5456 | 10.3772 | 10.0977 | 9.8188 | 9.5429 | 9.2909 | 9.108 | 9.0261 | 4.4384 | 2.283 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.2812 | 4.2863 | 4.2843 | 4.2828 | 4.2868 | 4.2695 | 4.2551 | 4.2466 | 4.2301 | 4.1938 | 3.3757 | 2.201 | 1.0391 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.2812 | 4.2843 | 4.2815 | 4.2722 | 4.2668 | 4.2474 | 4.2223 | 4.1982 | 4.1397 | 4.0833 | 3.0582 | 2.0515 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.2812 | 4.2913 | 4.2973 | 4.3056 | 4.3062 | 4.3081 | 4.3124 | 4.3073 | 4.2997 | 4.2807 | 4.2613 | 4.2267 | 4.1967 | 4.1654 | 3.9435 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.2812 | 4.279 | 4.2748 | 4.2627 | 4.2495 | 4.231 | 4.2091 | 4.1871 | 2.9465 | 1.3482 | 0.32166 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.2812 | 4.2871 | 4.2857 | 4.2875 | 4.2864 | 4.2806 | 4.2783 | 4.2674 | 4.2294 | 4.1995 | 4.1607 | 4.1339 | 4.1019 | 4.0834 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.0858 | 3.911 | 3.6155 | 3.4061 | 3.1201 | 2.8252 | 2.1311 | 1.5564 | 0.95981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.0858 | 3.8937 | 3.5815 | 3.2997 | 2.8189 | 2.3358 | 1.4381 | 0.58798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.0858 | 4.0158 | 3.9258 | 3.7882 | 3.6181 | 3.4791 | 3.3066 | 3.1358 | 2.9454 | 2.6546 | 2.3703 | 2.0536 | 1.767 | 1.5318 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.0858 | 3.8172 | 3.4973 | 3.0623 | 2.5558 | 1.2229 | 0.3298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.0858 | 3.9885 | 3.8394 | 3.6445 | 3.4259 | 3.1213 | 2.8921 | 2.6292 | 2.324 | 2.0569 | 1.4195 | 0.83615 | 0.10719 | 0 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 56.828 | 55.6803 | 53.5397 | 52.3809 | 51.155 | 49.8405 | 47.2668 | 44.321 | 41.3116 | 37.1801 | 34.711 | 33.2716 | 31.3349 | 29.6993 | 16.1035 | 9.3308 | 4.907
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 56.828 | 55.577 | 53.3484 | 51.8631 | 49.6021 | 47.4337 | 43.8794 | 39.876 | 35.6619 | 29.4263 | 25.1452 | 21.8842 | 18.189 | 14.9256 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 56.828 | 56.2116 | 55.1335 | 54.2893 | 53.4868 | 52.6929 | 51.7749 | 50.3782 | 48.9989 | 46.9072 | 44.9986 | 42.2881 | 39.7395 | 37.3396 | 19.7673 | 1.8155 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 56.828 | 54.9699 | 52.5332 | 50.1285 | 47.7568 | 43.8182 | 40.3387 | 35.8633 | 31.592 | 26.4529 | 22.9327 | 19.4659 | 16.907 | 14.6193 | 0 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 56.828 | 56.0196 | 54.5378 | 53.3877 | 52.4047 | 51.477 | 50.2854 | 48.1485 | 45.328 | 41.5273 | 38.6908 | 36.0743 | 34.1174 | 32.7511 | 11.6819 | 2.819 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.7158 | 17.433 | 16.1009 | 14.9709 | 13.6689 | 12.3811 | 12.1942 | 12.021 | 11.8915 | 11.6939 | 11.5686 | 11.5864 | 11.6111 | 11.6797 | 11.1305 | 6.0241 | 5.5777
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.7158 | 17.4889 | 16.0854 | 15.0997 | 13.7685 | 12.811 | 12.5239 | 12.2508 | 11.9439 | 11.5519 | 11.2382 | 11.0216 | 10.8603 | 10.7472 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.7158 | 17.7913 | 16.8343 | 15.9193 | 14.9393 | 13.9851 | 13.7158 | 13.4484 | 13.1771 | 12.8744 | 12.5717 | 12.2994 | 12.0759 | 11.9435 | 11.4017 | 11.0772 | 7.341
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.7158 | 17.3853 | 16.0242 | 14.8165 | 13.4513 | 12.1034 | 11.8434 | 11.5574 | 11.2756 | 11.0302 | 10.8379 | 10.7825 | 10.8151 | 10.8874 | 0.22769 | 0 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.7158 | 17.5264 | 16.1768 | 15.2199 | 13.9749 | 13.1032 | 12.9133 | 12.7291 | 12.5391 | 12.3243 | 12.1215 | 11.971 | 11.8784 | 11.8398 | 11.3281 | 11.2449 | 8.0806
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 57.8375 | 54.4385 | 48.3416 | 44.0868 | 40.841 | 37.3053 | 34.9789 | 33.1513 | 31.3039 | 28.1508 | 26.2908 | 24.965 | 23.4077 | 22.1148 | 11.1603 | 6.0402 | 5.5926
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 57.8375 | 54.4955 | 48.166 | 44.2017 | 40.4972 | 37.8073 | 34.8818 | 32.3793 | 29.4822 | 25.1237 | 22.1383 | 19.9235 | 16.5931 | 14.1891 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 57.8375 | 55.5602 | 51.5091 | 48.1609 | 45.8867 | 43.9965 | 42.8822 | 41.8554 | 40.8125 | 39.2729 | 37.7584 | 36.2708 | 34.9771 | 34.1194 | 24.0214 | 14.0993 | 7.3607
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 57.8375 | 53.9282 | 47.6884 | 42.5335 | 38.6508 | 33.5408 | 30.6958 | 27.5808 | 24.07 | 20.6298 | 18.2432 | 15.8457 | 14.1465 | 12.5731 | 0.2283 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 57.8375 | 54.8118 | 48.9591 | 45.2998 | 42.2708 | 40.4767 | 39.1719 | 38.1614 | 36.263 | 35.0024 | 32.921 | 31.1032 | 29.6343 | 28.6277 | 16.8609 | 11.7741 | 8.1022
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.1402 | 4.0976 | 3.9863 | 3.9278 | 3.8194 | 3.6777 | 2.7829 | 1.9583 | 0.96654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.1402 | 4.0699 | 3.9463 | 3.8556 | 3.5809 | 3.3044 | 2.2456 | 1.2284 | 0.02433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.1402 | 4.1536 | 4.1591 | 4.1583 | 4.1079 | 4.0561 | 3.4431 | 2.9264 | 2.3095 | 1.5045 | 0.61793 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.1402 | 3.9915 | 3.858 | 3.652 | 3.3709 | 3.055 | 1.9128 | 0.7975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.1402 | 4.1325 | 4.1327 | 4.1074 | 4.053 | 3.9665 | 3.1769 | 2.3449 | 1.3558 | 0.32338 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.2347 | 17.117 | 17.0379 | 16.9497 | 16.8205 | 16.2051 | 15.7413 | 15.3634 | 15.2258 | 15.0479 | 14.3516 | 14.3617 | 14.3711 | 13.9078 | 6.5248 | 1.6477 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.2347 | 17.0814 | 16.9862 | 16.8699 | 16.5885 | 15.8774 | 15.2277 | 14.5589 | 14.2764 | 13.3076 | 12.997 | 12.1156 | 11.8955 | 8.5334 | 0 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.2347 | 17.1674 | 17.1748 | 17.1358 | 17.0429 | 16.4727 | 16.0871 | 15.732 | 15.6457 | 15.4778 | 14.7009 | 14.5379 | 14.3734 | 13.6975 | 8.0558 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.2347 | 17.0091 | 16.8796 | 16.6687 | 16.3776 | 16.0452 | 15.6928 | 15.3649 | 15.0582 | 14.7737 | 14.5445 | 14.3985 | 14.3523 | 12.0978 | 0 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.2347 | 17.1171 | 17.0898 | 17.0084 | 15.2558 | 14.0267 | 13.1841 | 11.9854 | 11.1589 | 11.0067 | 9.9707 | 9.8206 | 8.9122 | 8.8945 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.7763 | 9.7018 | 9.5304 | 9.1875 | 9.004 | 8.7697 | 8.0146 | 7.4933 | 6.8914 | 5.8862 | 5.3811 | 5.1164 | 4.5025 | 3.9574 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.7763 | 9.642 | 9.4284 | 9.0093 | 8.5926 | 8.1696 | 7.2013 | 6.432 | 5.5855 | 4.1696 | 3.2691 | 2.6058 | 1.6119 | 0.71847 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.7763 | 9.7758 | 9.758 | 9.5069 | 9.3965 | 9.2793 | 9.0571 | 8.9175 | 8.7572 | 8.4497 | 8.1534 | 7.8588 | 7.5867 | 7.3698 | 3.9662 | 0.91924 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.7763 | 9.5446 | 9.3053 | 8.6902 | 8.2592 | 7.0697 | 6.0833 | 5.2217 | 4.4035 | 3.1802 | 2.4259 | 1.5208 | 0.78215 | 0.12141 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.7763 | 9.7284 | 9.6423 | 9.3 | 9.1402 | 8.965 | 8.6541 | 8.4275 | 8.1845 | 7.9005 | 7.2358 | 6.6472 | 6.1567 | 5.8063 | 2.2283 | 0.92073 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.7158 | 9.4438 | 8.8425 | 8.493 | 7.6415 | 6.7276 | 5.1211 | 3.0207 | 1.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.7158 | 9.3402 | 8.6395 | 8.0974 | 6.6112 | 5.1781 | 2.9702 | 0.19262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.7158 | 9.6681 | 9.4817 | 9.3089 | 8.7282 | 8.1449 | 7.4487 | 6.3352 | 5.2667 | 3.7533 | 2.4067 | 0.68391 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.7158 | 9.0173 | 8.1986 | 7.1638 | 5.6224 | 3.2422 | 1.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.7158 | 9.5859 | 9.2776 | 8.9317 | 8.1796 | 7.4596 | 6.511 | 4.7212 | 2.7967 | 0.34653 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.9425 | 4.7998 | 4.6879 | 4.5985 | 4.4258 | 4.2044 | 3.5709 | 2.8528 | 2.2103 | 1.1458 | 0.50568 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.9425 | 4.7568 | 4.5864 | 4.4761 | 4.1069 | 3.7425 | 2.9248 | 2.0489 | 1.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.9425 | 4.8991 | 4.9145 | 4.9298 | 4.8756 | 4.8222 | 4.7424 | 4.5576 | 4.418 | 4.1179 | 3.8501 | 3.5676 | 3.2856 | 3.0164 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.9425 | 4.6528 | 4.4698 | 4.2259 | 3.8635 | 2.7678 | 1.9883 | 1.0321 | 0.073745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.9425 | 4.8699 | 4.8596 | 4.8457 | 4.8047 | 4.7213 | 4.602 | 4.2861 | 4.0522 | 3.7993 | 3.1771 | 2.5846 | 2.0693 | 1.6636 | 0 | 0 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Best View | Headroom (MW) | 18.7442 | 18.3341 | 17.7404 | 17.1715 | 16.3173 | 13.8505 | 11.8521 | 9.6038 | 7.6651 | 4.6074 | 2.1701 | 0.54092 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.7442 | 18.2824 | 17.5968 | 16.9993 | 15.4506 | 13.63 | 10.899 | 7.9386 | 5.1332 | 0.68628 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.7442 | 18.6492 | 18.5233 | 18.3663 | 17.9549 | 17.307 | 16.8666 | 16.0758 | 15.4792 | 14.3836 | 12.879 | 11.6684 | 10.5064 | 9.3946 | 0 | 0 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.7442 | 17.9067 | 17.092 | 15.9315 | 14.3091 | 10.4319 | 7.7897 | 4.5897 | 1.8488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Erin Road | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.7442 | 18.6041 | 18.4141 | 18.0506 | 17.5378 | 16.6896 | 16.0092 | 14.7423 | 13.7968 | 12.7442 | 9.6325 | 7.7295 | 6.0577 | 4.8784 | 0 | 0 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.2351 | 6.2147 | 6.1251 | 6.0906 | 5.9646 | 5.8113 | 5.3862 | 5.0038 | 4.5711 | 3.8338 | 3.423 | 3.0864 | 2.4803 | 1.8957 | 0 | 0 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.2351 | 6.2104 | 6.1226 | 6.0746 | 5.9252 | 5.7586 | 5.3101 | 4.8992 | 4.4371 | 3.6636 | 3.2222 | 2.8468 | 2.1965 | 1.5787 | 0 | 0 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.2351 | 6.268 | 6.2839 | 6.2899 | 6.2674 | 6.234 | 6.1903 | 6.129 | 6.0654 | 5.938 | 5.8193 | 5.6805 | 5.5458 | 5.4196 | 3.4266 | 1.568 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.2351 | 6.1719 | 6.1093 | 5.9957 | 5.8458 | 5.176 | 4.7464 | 4.2925 | 3.8504 | 3.1541 | 2.7407 | 2.1127 | 1.5359 | 0.9836 | 0 | 0 | 0
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.2351 | 6.2613 | 6.2703 | 6.2662 | 6.235 | 6.1901 | 6.1401 | 6.0711 | 5.9797 | 5.8861 | 5.5253 | 5.1637 | 4.8212 | 4.5355 | 2.4065 | 1.6151 | 1.2174
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.43634 | 0.33684 | 0.1299 | 0.028291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.43634 | 0.31997 | 0.10515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.43634 | 0.44301 | 0.43691 | 0.40498 | 0.30903 | 0.22274 | 0.10627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.43634 | 0.26132 | 0.067932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.43634 | 0.41972 | 0.37979 | 0.31181 | 0.18242 | 0.04723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 61.1376 | 60.6071 | 59.6206 | 58.7505 | 57.3232 | 49.1599 | 45.0291 | 41.5176 | 37.8006 | 32.5717 | 24.3338 | 21.6631 | 18.7148 | 16.1376 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 61.1376 | 60.3941 | 59.32 | 58.2632 | 55.605 | 49.9429 | 44.5779 | 39.5407 | 34.1765 | 26.5497 | 13.9506 | 10.3207 | 5.3175 | 0.93851 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 61.1376 | 61.1739 | 61.2467 | 60.9506 | 60.3274 | 56.6958 | 55.3014 | 53.7723 | 52.2991 | 50.1956 | 45.167 | 41.6265 | 38.1465 | 34.9152 | 10.4557 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 61.1376 | 59.7587 | 58.4696 | 56.3492 | 53.6816 | 43.6748 | 38.4975 | 32.9739 | 27.9319 | 21.6904 | 12.263 | 7.6378 | 3.9627 | 0.97149 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 61.1376 | 61.0892 | 61.0966 | 60.5724 | 59.7764 | 56.0235 | 54.2855 | 52.2045 | 49.5102 | 46.0589 | 35.0836 | 31.9704 | 29.3252 | 27.5296 | 2.4662 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 8.8301 | 8.6877 | 8.4296 | 8.2258 | 7.8923 | 7.4521 | 6.9061 | 6.5661 | 6.1401 | 5.733 | 3.7635 | 3.9278 | 4.1092 | 4.4122 | 1.8383 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 8.8301 | 8.6553 | 8.3776 | 8.1748 | 7.4574 | 6.7011 | 5.8181 | 5.0807 | 4.2093 | 3.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 8.8301 | 8.8577 | 8.8733 | 8.8475 | 8.7099 | 8.5496 | 8.3579 | 8.1303 | 7.8763 | 7.432 | 5.9376 | 5.2399 | 4.5857 | 3.9895 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 8.8301 | 8.4857 | 8.1748 | 7.6764 | 6.9468 | 6.1347 | 5.2786 | 4.3644 | 3.5111 | 2.7829 | 0.46665 | 0.20008 | 0.17016 | 0.34123 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 8.8301 | 8.8356 | 8.8397 | 8.7581 | 8.6119 | 8.3942 | 8.1248 | 7.7958 | 7.4002 | 7.0419 | 4.0627 | 3.8164 | 3.7379 | 3.9179 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.7025 | 9.4309 | 8.8304 | 8.4814 | 7.631 | 6.7184 | 5.1141 | 3.0165 | 1.0907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.7025 | 9.3274 | 8.6277 | 8.0864 | 6.6021 | 5.1711 | 2.9661 | 0.19236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.7025 | 9.6549 | 9.4687 | 9.2961 | 8.7163 | 8.1337 | 7.4385 | 6.3265 | 5.2595 | 3.7482 | 2.4034 | 0.68298 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.7025 | 9.005 | 8.1874 | 7.154 | 5.6147 | 3.2377 | 1.0273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.7025 | 9.5728 | 9.2649 | 8.9194 | 8.1684 | 7.4494 | 6.5021 | 4.7147 | 2.7928 | 0.34606 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.9761 | 7.9905 | 7.9694 | 7.8389 | 7.6775 | 6.8222 | 6.3115 | 5.769 | 5.229 | 3.3931 | 1.3488 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.9761 | 7.9609 | 7.8651 | 7.7557 | 7.4691 | 7.2036 | 6.5639 | 5.9696 | 4.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.9761 | 8.0203 | 8.0344 | 7.9986 | 7.9283 | 7.8767 | 7.8212 | 7.7501 | 7.6808 | 7.5477 | 7.4105 | 7.267 | 7.1192 | 6.9714 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.9761 | 7.9195 | 7.832 | 7.6325 | 7.3478 | 6.3662 | 5.753 | 3.4982 | 0.19669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.9761 | 8.0144 | 8.0222 | 7.9519 | 7.8512 | 7.7702 | 7.6788 | 7.5808 | 7.4679 | 7.3444 | 6.8319 | 6.3299 | 5.8456 | 5.4238 | 0 | 0 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.0876 | 8.9543 | 8.8047 | 7.8692 | 6.6114 | 5.6809 | 4.5424 | 3.4177 | 2.0933 | 0.66297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.0876 | 8.9519 | 8.7997 | 7.8493 | 6.5545 | 5.6032 | 4.4269 | 3.2588 | 1.8948 | 0.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.0876 | 9.0137 | 8.9415 | 8.1191 | 7.2565 | 6.4138 | 5.5566 | 4.823 | 3.9838 | 2.9985 | 1.8892 | 0.68997 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.0876 | 8.9061 | 8.7351 | 7.5835 | 6.2576 | 4.9195 | 3.6694 | 2.4613 | 1.3002 | 0.11192 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.0876 | 8.9991 | 8.8981 | 7.9588 | 6.7828 | 5.9479 | 4.9354 | 3.884 | 2.6664 | 1.4206 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.3517 | 19.6748 | 18.4821 | 17.3614 | 16.2622 | 15.3739 | 13.9306 | 12.5686 | 8.3385 | 2.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.3517 | 19.5656 | 18.2918 | 16.9981 | 15.3407 | 13.9634 | 10.3481 | 5.3797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.3517 | 20.2012 | 19.5734 | 18.6796 | 17.8756 | 17.2914 | 16.6407 | 15.9348 | 15.2405 | 14.359 | 13.4763 | 12.5472 | 11.6645 | 10.939 | 3.2483 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.3517 | 19.2579 | 17.8989 | 16.0649 | 14.3798 | 12.0722 | 10.1239 | 7.9109 | 5.6074 | 3.5527 | 2.1236 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.3517 | 19.8475 | 18.9963 | 17.9113 | 16.9556 | 16.1645 | 15.3927 | 14.5314 | 13.5979 | 12.8073 | 11.5651 | 10.4155 | 9.1626 | 8.5352 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.9009 | 10.8443 | 4.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.9009 | 10.8056 | 4.8717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.9009 | 10.9497 | 10.8355 | 10.8256 | 10.5164 | 10.1386 | 10.002 | 9.7305 | 9.5153 | 9.1502 | 8.7678 | 8.0305 | 7.2912 | 6.5864 | 1.8166 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.9009 | 10.6815 | 10.2585 | 9.9216 | 9.1828 | 7.6199 | 6.7721 | 5.6752 | 4.7139 | 3.2977 | 2.3324 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.9009 | 10.9361 | 10.7462 | 10.6946 | 10.2969 | 9.8939 | 9.7243 | 8.9983 | 8.3922 | 7.3349 | 6.6039 | 5.8806 | 5.2225 | 4.3515 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.7284 | 19.1751 | 18.4169 | 17.9303 | 17.1916 | 16.0782 | 13.248 | 10.4188 | 6.1951 | 1.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.7284 | 19.0914 | 18.2612 | 17.6516 | 16.0447 | 12.8043 | 8.8027 | 4.6194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.7284 | 19.3802 | 19.0233 | 18.6334 | 18.1209 | 17.9151 | 17.3631 | 16.7778 | 16.1807 | 15.3768 | 14.5364 | 13.6559 | 12.7698 | 11.8945 | 0.79843 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.7284 | 18.8994 | 18.0544 | 17.1336 | 16.0735 | 15.4358 | 14.2679 | 12.9507 | 11.7727 | 10.5487 | 7.6586 | 4.1874 | 1.557 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.7284 | 19.2594 | 18.7113 | 18.2454 | 17.6012 | 17.3905 | 16.7148 | 15.8821 | 15.0565 | 14.1559 | 13.0845 | 12.1472 | 11.5372 | 11.1346 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.8449 | 14.6795 | 8.7567 | 2.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.8449 | 14.5896 | 8.6052 | 1.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.8449 | 14.843 | 14.8463 | 14.7029 | 14.4153 | 14.1844 | 13.8696 | 13.2536 | 12.5813 | 11.7931 | 11.0516 | 9.9593 | 8.879 | 7.8443 | 0.80092 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.8449 | 14.3674 | 13.8948 | 13.1261 | 12.1403 | 10.5089 | 9.1065 | 7.1215 | 5.2499 | 3.2628 | 1.9346 | 0.55628 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.8449 | 14.789 | 14.7203 | 14.4569 | 14.0648 | 13.7627 | 13.3422 | 12.0001 | 10.6332 | 9.1925 | 8.1641 | 7.2324 | 6.429 | 5.5827 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 43.1065 | 42.011 | 35.0338 | 27.9177 | 18.6485 | 16.4072 | 13.5191 | 10.632 | 6.3219 | 1.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 43.1065 | 41.7135 | 34.4981 | 26.9657 | 16.373 | 13.0663 | 8.9828 | 4.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 43.1065 | 42.5974 | 42.1124 | 41.5288 | 40.5038 | 39.6676 | 38.3683 | 36.7437 | 34.8561 | 32.2901 | 29.661 | 26.5788 | 23.4309 | 20.4727 | 0.81477 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 43.1065 | 41.0439 | 39.0785 | 36.6744 | 33.7569 | 30.2374 | 26.3691 | 21.6564 | 16.9049 | 11.8662 | 7.8153 | 4.2731 | 1.5888 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 43.1065 | 42.2955 | 41.4179 | 40.5231 | 39.2402 | 38.24 | 36.5429 | 33.6831 | 30.3773 | 26.7927 | 23.2291 | 20.022 | 17.7115 | 16.0595 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.3096 | 8.7831 | 8.1078 | 7.5856 | 7.4113 | 7.2303 | 7.017 | 6.717 | 5.9206 | 3.9284 | 3.2186 | 3.1947 | 2.841 | 2.69 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.3096 | 8.7754 | 8.0452 | 7.557 | 7.263 | 6.9157 | 4.8402 | 3.3993 | 1.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.3096 | 8.9711 | 8.542 | 8.1501 | 8.0347 | 7.9258 | 7.7919 | 7.6978 | 7.617 | 7.4004 | 7.1829 | 6.854 | 5.9759 | 5.3125 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.3096 | 8.6738 | 7.9514 | 7.279 | 6.7259 | 4.6196 | 2.7663 | 0.98557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.3096 | 8.8377 | 8.2064 | 7.7607 | 7.6473 | 7.5435 | 7.4086 | 7.3483 | 7.2472 | 6.5799 | 5.0624 | 3.8852 | 2.3699 | 1.9732 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.6593 | 11.3393 | 10.2754 | 9.2796 | 8.0106 | 6.5623 | 5.853 | 5.2218 | 4.5593 | 3.2978 | 2.5668 | 1.6735 | 0.79009 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.6593 | 11.3437 | 10.2521 | 9.3275 | 8.0079 | 7.3218 | 6.4886 | 5.7083 | 4.7544 | 3.2627 | 2.3253 | 1.5598 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.6593 | 11.5166 | 10.874 | 10.1566 | 9.3496 | 8.9296 | 8.7427 | 8.5357 | 8.3207 | 7.9421 | 7.5797 | 7.1882 | 6.8249 | 6.5407 | 3.3229 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.6593 | 11.2185 | 10.1274 | 8.9062 | 7.5322 | 5.7623 | 4.9839 | 3.8708 | 2.2404 | 1.0251 | 0.24458 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.6593 | 11.4312 | 10.4767 | 9.6277 | 8.323 | 7.8778 | 7.4601 | 7.2183 | 6.1922 | 5.8449 | 5.1151 | 4.4116 | 3.7954 | 3.2984 | 0 | 0 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.4281 | 13.415 | 13.5381 | 13.6186 | 13.7405 | 13.8411 | 13.9013 | 14.0095 | 14.0811 | 14.1313 | 14.2432 | 14.428 | 14.5985 | 14.7898 | 14.9474 | 15.2812 | 15.477
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.4281 | 13.4013 | 13.5087 | 13.5608 | 13.5752 | 13.5834 | 13.5378 | 13.5417 | 13.5071 | 13.3716 | 13.3106 | 13.3079 | 13.2969 | 13.3201 | 12.5375 | 12.5834 | 13.0898
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.4281 | 13.4858 | 13.6787 | 13.7966 | 13.9464 | 14.1002 | 14.2566 | 14.4071 | 14.5427 | 14.6137 | 14.6832 | 14.7365 | 14.8027 | 14.8861 | 14.3523 | 13.5711 | 13.18
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.4281 | 13.3381 | 13.434 | 13.4054 | 13.4086 | 13.393 | 13.3765 | 13.3418 | 13.3189 | 13.2803 | 13.2797 | 13.3437 | 13.4533 | 13.5198 | 13.4982 | 13.8531 | 13.9401
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.4281 | 13.4355 | 13.609 | 13.7092 | 13.8534 | 13.9928 | 14.1286 | 14.2411 | 14.3308 | 14.3995 | 14.4586 | 14.5176 | 14.623 | 14.785 | 13.7219 | 13.6031 | 13.7083
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.3382 | 20.4561 | 20.4936 | 20.526 | 20.489 | 20.4302 | 20.3179 | 20.272 | 20.1398 | 19.9959 | 19.9195 | 19.9326 | 19.9283 | 19.9445 | 11.9123 | 2.7495 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.3382 | 20.4262 | 20.4541 | 20.474 | 20.3278 | 20.192 | 19.9866 | 19.8605 | 19.6397 | 19.3371 | 19.1084 | 19.0147 | 18.8376 | 15.983 | 0 | 0 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.3382 | 20.5018 | 20.6464 | 20.7447 | 20.8014 | 20.8651 | 20.9027 | 20.9337 | 20.9471 | 20.935 | 20.9045 | 20.8436 | 20.7806 | 20.7173 | 19.7105 | 6.1098 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.3382 | 20.3599 | 20.3742 | 20.2816 | 20.1405 | 19.9969 | 19.8296 | 19.6445 | 19.4614 | 19.2717 | 19.0985 | 18.9377 | 18.1814 | 16.1447 | 0 | 0 | 0
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.3382 | 20.5095 | 20.6491 | 20.7213 | 20.7585 | 20.803 | 20.8332 | 20.8484 | 20.845 | 20.8182 | 20.7609 | 20.6848 | 20.6175 | 20.6046 | 17.5265 | 9.7251 | 4.5356
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.7521 | 0.1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.7521 | 1.6839 | 1.5176 | 1.3528 | 1.0907 | 0.85713 | 0.62983 | 0.4062 | 0.15998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.7521 | 0.18914 | 0.068281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.2093 | 9.289 | 9.3667 | 9.4447 | 9.5221 | 9.5972 | 9.6704 | 9.7444 | 9.8174 | 9.8904 | 9.9645 | 10.0405 | 10.1158 | 10.1912 | 10.5334 | 9.2116 | 4.8443
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.2093 | 9.2891 | 9.3669 | 9.4458 | 9.5232 | 9.5989 | 9.6726 | 9.7455 | 9.8171 | 9.889 | 9.9618 | 10.0368 | 10.1113 | 10.1862 | 0 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.2093 | 9.2889 | 9.3683 | 9.4469 | 9.5247 | 9.6017 | 9.6769 | 9.7513 | 9.8261 | 9.8998 | 9.9721 | 10.0433 | 10.1136 | 10.1842 | 10.5188 | 1.7923 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.2093 | 9.289 | 9.3676 | 9.4447 | 9.5213 | 9.5956 | 9.669 | 9.7417 | 9.8144 | 9.888 | 9.9622 | 10.0372 | 10.1136 | 10.1899 | 0 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.2093 | 9.2901 | 9.3694 | 9.4481 | 9.526 | 9.6022 | 9.6778 | 9.7518 | 9.8253 | 9.8979 | 9.9698 | 10.0421 | 10.1139 | 10.1872 | 10.5252 | 2.783 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.8383 | 4.8426 | 4.8329 | 4.8381 | 4.8053 | 4.7607 | 4.7155 | 4.6855 | 4.6379 | 4.5678 | 4.5276 | 4.514 | 4.524 | 4.5416 | 0 | 0 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.8383 | 4.8385 | 4.8241 | 4.8258 | 4.776 | 4.7248 | 4.6616 | 4.6112 | 4.5422 | 4.4508 | 4.393 | 4.3603 | 4.3495 | 4.2188 | 0 | 0 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.8383 | 4.8605 | 4.8824 | 4.8951 | 4.8973 | 4.8945 | 4.8974 | 4.8912 | 4.8763 | 4.8483 | 4.8207 | 4.7822 | 4.7422 | 4.712 | 3.9271 | 2.3335 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.8383 | 4.826 | 4.8077 | 4.7705 | 4.7275 | 4.6736 | 4.6083 | 4.541 | 4.4788 | 4.4198 | 4.3798 | 4.3696 | 3.9654 | 2.7587 | 0 | 0 | 0
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.8383 | 4.8583 | 4.8717 | 4.888 | 4.8808 | 4.8843 | 4.8764 | 4.8624 | 4.843 | 4.8214 | 4.7924 | 4.7746 | 4.7666 | 4.778 | 3.7003 | 2.5344 | 1.3001
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.0011 | 9.5021 | 9.1639 | 8.7407 | 8.391 | 8.0881 | 7.7596 | 7.5521 | 7.3823 | 7.1025 | 6.8869 | 6.7717 | 6.6786 | 6.6058 | 5.7395 | 5.4616 | 5.4061
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.0011 | 9.5039 | 9.142 | 8.7188 | 8.3088 | 8.0334 | 7.6694 | 7.4089 | 7.1407 | 6.7679 | 6.473 | 6.2522 | 6.048 | 5.881 | 0 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.0011 | 9.6566 | 9.4494 | 9.099 | 8.8769 | 8.696 | 8.4999 | 8.3667 | 8.2403 | 8.0693 | 7.8974 | 7.7288 | 7.5857 | 7.4803 | 6.162 | 4.5725 | 3.5942
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.0011 | 9.4208 | 9.0471 | 8.495 | 8.1042 | 7.7421 | 7.3787 | 7.0578 | 6.7823 | 6.5081 | 6.2538 | 6.0749 | 5.9872 | 5.9092 | 0.22068 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.0011 | 9.5532 | 9.264 | 8.8846 | 8.6097 | 8.4469 | 8.2418 | 8.0841 | 7.9299 | 7.7861 | 7.6327 | 7.5031 | 7.3923 | 7.3356 | 5.529 | 4.7491 | 4.397
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 13.3428 | 13.1465 | 12.863 | 12.7836 | 12.5851 | 12.3433 | 11.6457 | 11.0024 | 10.214 | 8.986 | 8.1895 | 7.6243 | 6.6225 | 5.641 | 0.7635 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 13.3428 | 13.1722 | 12.9125 | 12.7682 | 12.4095 | 12.0386 | 11.1785 | 10.397 | 9.4771 | 7.9792 | 6.9428 | 6.0769 | 4.7859 | 3.539 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 13.3428 | 13.2364 | 13.1205 | 13.0939 | 13.0172 | 12.9052 | 12.7838 | 12.6463 | 12.4895 | 12.2166 | 11.9458 | 11.287 | 10.6369 | 9.9704 | 5.5749 | 0.88734 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 13.3428 | 13.0713 | 12.7403 | 12.4767 | 12.1128 | 11.0258 | 10.2314 | 9.383 | 8.4526 | 7.1128 | 6.131 | 4.8729 | 3.7327 | 2.6593 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 13.3428 | 13.2747 | 13.2126 | 13.1295 | 13.0251 | 12.9158 | 12.7724 | 12.5807 | 11.9756 | 10.9485 | 10.2142 | 9.4723 | 8.7727 | 8.1289 | 2.9692 | 0.93512 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 20.9497 | 20.8117 | 20.6486 | 20.5535 | 20.3862 | 17.306 | 16.2992 | 15.4032 | 14.6152 | 13.4138 | 11.008 | 10.1402 | 9.2575 | 8.4422 | 3.4948 | 1.0173 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 20.9497 | 20.7793 | 20.6123 | 20.4754 | 20.083 | 18.1814 | 16.9425 | 15.7776 | 14.7005 | 13.0534 | 9.519 | 8.5865 | 7.2639 | 6.0492 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 20.9497 | 20.8705 | 20.8172 | 20.7671 | 20.6679 | 19.3068 | 18.8694 | 18.4457 | 18.0947 | 17.6296 | 16.2128 | 15.1464 | 14.0893 | 13.0859 | 8.1252 | 3.8935 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 20.9497 | 20.7048 | 20.4807 | 20.2177 | 19.7412 | 16.421 | 15.2703 | 14.1063 | 13.1274 | 11.7439 | 9.0978 | 7.8988 | 6.8419 | 5.9173 | 0 | 0 | 0
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 20.9497 | 20.851 | 20.8012 | 20.7244 | 20.6069 | 19.2124 | 18.7194 | 18.162 | 17.4083 | 16.2293 | 12.9656 | 12.1465 | 11.3841 | 10.7723 | 6.0115 | 4.3079 | 3.2839
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.6 | 15.6772 | 15.7423 | 15.8091 | 15.8735 | 15.9378 | 15.5427 | 12.4671 | 8.2711 | 2.5228 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.6 | 15.6772 | 15.7429 | 15.8081 | 15.8687 | 15.543 | 10.2646 | 5.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.6 | 15.6772 | 15.754 | 15.8301 | 15.9054 | 15.9771 | 16.0488 | 16.1212 | 16.1929 | 16.2535 | 16.3093 | 16.3692 | 16.4259 | 16.4823 | 5.9734 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.6 | 15.6772 | 15.7526 | 15.8183 | 15.8817 | 15.9455 | 16.0071 | 16.0585 | 13.5833 | 6.9039 | 2.5239 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.6 | 15.6772 | 15.754 | 15.8301 | 15.903 | 15.9755 | 16.0447 | 16.1081 | 16.1699 | 16.2214 | 16.2737 | 16.3155 | 16.3595 | 16.4036 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.9374 | 10.9104 | 10.8331 | 10.7512 | 10.6547 | 10.5611 | 10.4277 | 10.344 | 10.2121 | 10.0358 | 9.9281 | 9.9072 | 9.8817 | 9.8715 | 6.4512 | 1.6291 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.9374 | 10.8981 | 10.808 | 10.6971 | 10.4859 | 10.3081 | 10.0761 | 9.8872 | 9.6332 | 9.2728 | 8.9866 | 8.7824 | 8.5723 | 8.3982 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.9374 | 10.9369 | 10.925 | 10.8854 | 10.8227 | 10.7678 | 10.7122 | 10.6525 | 10.5845 | 10.4568 | 10.3321 | 10.1943 | 10.0676 | 9.9434 | 7.9649 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.9374 | 10.8556 | 10.7516 | 10.5586 | 10.3256 | 10.106 | 9.8798 | 9.6354 | 9.3618 | 9.1108 | 8.8821 | 8.7188 | 8.6273 | 8.5606 | 0 | 0 | 0
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.9374 | 10.9283 | 10.8865 | 10.8106 | 10.7162 | 10.6284 | 10.5421 | 10.4417 | 10.3148 | 10.1857 | 10.0379 | 9.8992 | 9.8049 | 9.7408 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.3779 | 4.3105 | 4.0919 | 3.9731 | 3.7162 | 3.3809 | 2.9531 | 2.6714 | 2 | 1.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.3779 | 4.2332 | 3.947 | 3.7179 | 3.1127 | 2.4742 | 1.6902 | 1.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.3779 | 4.4378 | 4.455 | 4.4427 | 4.2982 | 4.1713 | 4.012 | 3.8218 | 3.4705 | 2.898 | 2.2863 | 1.6567 | 1.021 | 0.39769 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.3779 | 4.0775 | 3.7621 | 3.2804 | 2.673 | 1.9788 | 1.2567 | 0.44113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.3779 | 4.3972 | 4.3613 | 4.2571 | 4.0932 | 3.8903 | 3.6547 | 3.3266 | 2.6637 | 1.9152 | 1.0652 | 0.3189 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.7667 | 8.7781 | 8.7556 | 8.7787 | 8.7817 | 8.4202 | 7.2248 | 6.6447 | 5.8569 | 3.8861 | 3.1839 | 3.1603 | 2.8104 | 2.661 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.7667 | 8.7569 | 8.7259 | 8.7053 | 8.2034 | 6.8413 | 4.7881 | 3.3627 | 1.5209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.7667 | 8.8389 | 8.904 | 8.9545 | 8.9885 | 9.0368 | 8.9664 | 8.9682 | 8.9745 | 8.7149 | 7.9314 | 6.7802 | 5.9115 | 5.2553 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.7667 | 8.6926 | 8.6264 | 8.5043 | 6.6535 | 4.5699 | 2.7365 | 0.97495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.7667 | 8.8244 | 8.8673 | 8.889 | 8.9156 | 8.9431 | 8.8238 | 8.3076 | 7.6915 | 6.5091 | 5.0078 | 3.8433 | 2.3444 | 1.9519 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.7217 | 14.5138 | 14.1906 | 13.9436 | 13.6329 | 12.5802 | 11.8187 | 9.6027 | 7.6642 | 4.6069 | 2.1698 | 0.54085 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.7217 | 14.5214 | 14.2065 | 13.9374 | 13.3439 | 12.7416 | 10.8978 | 7.9377 | 5.1326 | 0.6862 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.7217 | 14.6425 | 14.5212 | 14.4293 | 14.2663 | 14.1261 | 13.9699 | 13.7989 | 13.6248 | 13.2749 | 12.4457 | 11.6671 | 10.5052 | 9.3935 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.7217 | 14.356 | 13.9579 | 13.4581 | 12.8312 | 10.4306 | 7.7887 | 4.5892 | 1.8486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.7217 | 14.6426 | 14.5042 | 14.3094 | 14.1111 | 13.9046 | 13.676 | 13.4038 | 13.0868 | 12.7427 | 9.6314 | 7.7286 | 6.057 | 4.8778 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 18.7596 | 18.3492 | 17.755 | 17.1856 | 16.3307 | 13.8619 | 11.8618 | 9.6117 | 7.6714 | 4.6112 | 2.1719 | 0.54136 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 18.7596 | 18.2974 | 17.6113 | 17.0133 | 15.4633 | 13.6413 | 10.908 | 7.9451 | 5.1374 | 0.68684 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 18.7596 | 18.6645 | 18.5386 | 18.3814 | 17.9696 | 17.3212 | 16.8804 | 16.0891 | 15.4919 | 14.3954 | 12.8896 | 11.678 | 10.5151 | 9.4024 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 18.7596 | 17.9214 | 17.106 | 15.9445 | 14.3209 | 10.4404 | 7.7961 | 4.5935 | 1.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 18.7596 | 18.6194 | 18.4292 | 18.0654 | 17.5523 | 16.7033 | 16.0223 | 14.7544 | 13.8082 | 12.7547 | 9.6404 | 7.7358 | 6.0627 | 4.8824 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.3668 | 4.2996 | 4.0815 | 3.9631 | 3.7068 | 3.3724 | 2.9457 | 2.6647 | 1.9949 | 1.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.3668 | 4.2225 | 3.9371 | 3.7086 | 3.1048 | 2.468 | 1.686 | 0.99825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.3668 | 4.4267 | 4.4438 | 4.4315 | 4.2873 | 4.1608 | 4.0019 | 3.8122 | 3.4618 | 2.8907 | 2.2805 | 1.6525 | 1.0184 | 0.39669 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.3668 | 4.0672 | 3.7526 | 3.2722 | 2.6662 | 1.9738 | 1.2536 | 0.44002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.3668 | 4.3861 | 4.3503 | 4.2464 | 4.0829 | 3.8805 | 3.6455 | 3.3182 | 2.657 | 1.9103 | 1.0625 | 0.3181 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.4391 | 4.3708 | 4.1491 | 4.0287 | 3.7682 | 3.4282 | 2.9944 | 2.7088 | 2.0279 | 1.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.4391 | 4.2924 | 4.0023 | 3.77 | 3.1562 | 2.5088 | 1.7139 | 1.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.4391 | 4.4999 | 4.5173 | 4.5048 | 4.3583 | 4.2297 | 4.0681 | 3.8753 | 3.5191 | 2.9386 | 2.3183 | 1.6798 | 1.0353 | 0.40326 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.4391 | 4.1345 | 3.8147 | 3.3263 | 2.7104 | 2.0065 | 1.2743 | 0.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.4391 | 4.4587 | 4.4224 | 4.3167 | 4.1504 | 3.9447 | 3.7058 | 3.3731 | 2.7009 | 1.942 | 1.0801 | 0.32336 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.6614 | 15.4668 | 13.5877 | 12.1678 | 11.9851 | 11.7649 | 11.5185 | 11.2908 | 11.0933 | 10.7965 | 10.5582 | 10.4751 | 10.1352 | 9.3926 | 4.3776 | 2.0392 | 2.725
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.6614 | 15.542 | 13.6023 | 12.3663 | 12.188 | 11.949 | 11.6356 | 11.3462 | 10.9492 | 10.5063 | 10.1332 | 9.8889 | 8.2786 | 7.1414 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.6614 | 15.8196 | 14.4811 | 13.3435 | 13.1887 | 13.0133 | 12.8351 | 12.6242 | 12.4118 | 12.1367 | 11.8577 | 11.5935 | 11.3929 | 11.3209 | 10.4485 | 8.0879 | 5.3295
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.6614 | 15.4154 | 13.5123 | 12.0046 | 11.7612 | 11.4891 | 11.187 | 10.8232 | 10.4262 | 9.8644 | 8.7976 | 7.6421 | 6.7933 | 5.9251 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.6614 | 15.5773 | 13.6776 | 12.4917 | 12.4025 | 12.2809 | 12.1463 | 11.9878 | 11.7555 | 11.5325 | 11.2712 | 11.0949 | 10.9757 | 10.9232 | 7.9306 | 5.3542 | 3.4396
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.502 | 13.8126 | 11.2223 | 10.2868 | 9.7294 | 9.0517 | 8.619 | 8.2474 | 7.8617 | 7.2129 | 6.8282 | 6.5012 | 6.2122 | 5.9834 | 3.7634 | 2.5741 | 2.3891
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.502 | 13.8272 | 11.1944 | 10.3348 | 9.6769 | 9.2057 | 8.6438 | 8.1346 | 7.5259 | 6.614 | 5.9907 | 5.536 | 4.7727 | 4.2971 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.502 | 14.041 | 12.2756 | 11.5216 | 11.1088 | 10.8101 | 10.6 | 10.3587 | 10.127 | 9.7657 | 9.4133 | 9.0634 | 8.7556 | 8.5735 | 6.4169 | 4.3048 | 2.8199
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.502 | 13.6927 | 11.13 | 9.9742 | 9.2422 | 8.3409 | 7.8131 | 7.1241 | 6.2973 | 5.5974 | 5.1041 | 4.615 | 4.2855 | 3.9735 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.502 | 13.8953 | 11.3728 | 10.5886 | 10.0609 | 9.8092 | 9.5589 | 9.3617 | 8.8451 | 8.5791 | 8.1576 | 7.7785 | 7.4819 | 7.2806 | 4.7592 | 3.4648 | 2.3926
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.2536 | 0.1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.2536 | 1.809 | 1.6303 | 1.4533 | 1.1717 | 0.92078 | 0.6766 | 0.43637 | 0.17186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.2536 | 0.2007 | 0.072455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.655 | 10.6621 | 10.5949 | 10.4605 | 10.1524 | 9.176 | 8.4735 | 7.3982 | 6.6007 | 3.3973 | 1.3504 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.655 | 10.6164 | 10.4639 | 10.3303 | 9.7674 | 9.2563 | 8.2708 | 7.018 | 4.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.655 | 10.7568 | 10.8127 | 10.8169 | 10.6843 | 10.5969 | 10.5209 | 10.1621 | 9.9484 | 9.5604 | 9.1775 | 8.7834 | 8.4197 | 8.0635 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.655 | 10.5116 | 10.3511 | 10.0232 | 9.4476 | 8.1009 | 7.1598 | 3.5025 | 0.19694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.655 | 10.7396 | 10.7831 | 10.7279 | 10.5292 | 10.377 | 10.2103 | 9.6374 | 9.3206 | 8.9706 | 8.1843 | 7.4139 | 6.739 | 5.579 | 0 | 0 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 47.3078 | 46.9904 | 46.537 | 45.3141 | 43.5751 | 41.2888 | 38.2708 | 35.259 | 32.2252 | 28.6836 | 24.7499 | 21.8909 | 19.8347 | 17.4435 | 6.5521 | 1.6546 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 47.3078 | 46.8862 | 46.3394 | 45.012 | 42.6556 | 40.2784 | 36.6108 | 32.8634 | 29.1362 | 23.9499 | 19.5725 | 15.1973 | 12.0552 | 8.569 | 0 | 0 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 47.3078 | 47.2382 | 47.2018 | 46.3196 | 45.1986 | 43.668 | 41.7431 | 39.8979 | 38.1847 | 35.8937 | 32.8089 | 30.1138 | 27.284 | 23.8508 | 8.0894 | 0 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 47.3078 | 46.5867 | 45.9592 | 44.0306 | 41.5989 | 38.6249 | 35.1236 | 31.4461 | 27.9454 | 24.2198 | 20.9441 | 17.738 | 14.9666 | 12.1484 | 0 | 0 | 0
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 47.3078 | 47.1344 | 46.9924 | 45.8595 | 42.7555 | 40.4838 | 37.6935 | 34.2209 | 30.9066 | 28.1583 | 23.7582 | 20.4372 | 17.3448 | 15.4712 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.651 | 6.5977 | 6.4781 | 6.1302 | 5.8222 | 5.3104 | 4.816 | 4.3402 | 3.7546 | 3.2042 | 2.7076 | 2.6498 | 2.0043 | 1.3645 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.651 | 6.5706 | 6.4255 | 6.062 | 5.6302 | 4.9995 | 4.3009 | 3.4795 | 2.5364 | 1.5856 | 0.77368 | 0.38571 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.651 | 6.6483 | 6.6484 | 6.3903 | 6.1819 | 5.7744 | 5.4503 | 5.0546 | 4.6389 | 4.1883 | 3.7319 | 3.3539 | 2.9877 | 2.6664 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.651 | 6.5087 | 6.3644 | 5.8432 | 5.3649 | 4.544 | 3.7963 | 2.8671 | 1.964 | 1.2 | 0.3301 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.651 | 6.6431 | 6.6198 | 6.3075 | 6.0332 | 5.5903 | 5.1637 | 4.6313 | 4.0051 | 3.4435 | 2.8192 | 2.5158 | 2.3083 | 2.1984 | 0 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.4717 | 8.4343 | 8.375 | 8.3427 | 8.2684 | 8.188 | 8.086 | 8.0202 | 7.9218 | 7.8085 | 7.7419 | 7.7259 | 7.6979 | 7.7014 | 7.1589 | 6.5836 | 5.1359
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.4717 | 8.4262 | 8.3607 | 8.3144 | 8.2202 | 8.1302 | 8.0126 | 7.9196 | 7.7925 | 7.6526 | 7.5618 | 7.5228 | 7.4774 | 7.4673 | 6.8115 | 5.2518 | 3.6295
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.4717 | 8.4806 | 8.49 | 8.4913 | 8.4502 | 8.4186 | 8.3826 | 8.3351 | 8.2789 | 8.1993 | 8.1217 | 8.0409 | 7.9616 | 7.891 | 6.9405 | 6.26 | 4.705
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.4717 | 8.4053 | 8.343 | 8.2573 | 8.1758 | 8.0751 | 7.9693 | 7.8502 | 7.7158 | 7.6258 | 7.5589 | 7.5201 | 7.5241 | 7.5573 | 7.1226 | 6.4842 | 3.7556
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.4717 | 8.4699 | 8.464 | 8.4546 | 8.42 | 8.3773 | 8.3266 | 8.2644 | 8.1882 | 8.1211 | 8.0471 | 7.9769 | 7.9295 | 7.9212 | 7.0387 | 4.3087 | 2.2424
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.4923 | 11.3026 | 10.8523 | 7.8326 | 5.9003 | 5.1991 | 4.3637 | 3.7382 | 2.2566 | 1.6762 | 1.3722 | 1.484 | 1.6027 | 1.9425 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.4923 | 11.1769 | 10.6234 | 7.7917 | 5.5533 | 4.6371 | 3.4291 | 2.3334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.4923 | 11.467 | 11.3381 | 9.0143 | 7.6448 | 7.1915 | 6.7152 | 6.1826 | 5.0934 | 4.214 | 3.3522 | 2.4432 | 1.564 | 0.9346 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.4923 | 10.9406 | 10.2977 | 6.784 | 4.4979 | 3.0827 | 1.8894 | 0.12101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.4923 | 11.4171 | 11.1848 | 8.5464 | 6.7701 | 5.9672 | 5.4031 | 4.5591 | 2.8164 | 2.0246 | 1.2013 | 0.44874 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.2475 | 14.9323 | 14.9098 | 14.9285 | 14.9122 | 14.8943 | 14.8402 | 14.8461 | 14.8284 | 14.8203 | 14.877 | 14.9994 | 15.1105 | 15.2442 | 15.1444 | 15.1243 | 15.1501
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.2475 | 14.9085 | 14.8655 | 14.845 | 14.7638 | 14.6871 | 14.5662 | 14.4885 | 14.3534 | 14.2125 | 14.1407 | 14.1276 | 14.1142 | 14.1276 | 13.2883 | 12.9481 | 12.9274
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.2475 | 15.0336 | 15.0713 | 15.1007 | 15.0936 | 15.0936 | 15.0854 | 15.0806 | 15.045 | 14.9869 | 14.9295 | 14.87 | 14.8294 | 14.7967 | 14.1107 | 13.7619 | 13.4061
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.2475 | 14.867 | 14.8294 | 14.7569 | 14.686 | 14.5996 | 14.5144 | 14.3792 | 14.2191 | 14.1454 | 14.1014 | 14.0906 | 14.142 | 14.1611 | 13.6773 | 13.4469 | 13.3746
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.2475 | 14.9526 | 14.9876 | 15.0088 | 15.0075 | 15.0019 | 14.982 | 14.9429 | 14.8836 | 14.8417 | 14.7843 | 14.7381 | 14.7264 | 14.7772 | 14.1529 | 14.0824 | 14.0022
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.7558 | 1.5767 | 1.2514 | 1.0711 | 0.80837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.7558 | 1.5163 | 1.1025 | 0.77796 | 0.011566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.7558 | 1.7682 | 1.7642 | 1.7165 | 1.5407 | 1.3891 | 1.1871 | 0.97434 | 0.73457 | 0.26557 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.7558 | 1.3014 | 0.82949 | 0.17019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.7558 | 1.7344 | 1.6472 | 1.5174 | 1.3315 | 1.1371 | 0.85913 | 0.50065 | 0.079211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Best View | Headroom (MW) | 82.1829 | 82.1098 | 81.3402 | 81.299 | 79.3454 | 77.8723 | 74.2279 | 71.6595 | 68.4587 | 63.8984 | 62.4255 | 62.5108 | 61.8812 | 61.889 | 45.1047 | 36.7055 | 33.0233
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 82.1829 | 81.7077 | 80.4554 | 79.7781 | 75.2722 | 71.6859 | 65.738 | 60.1664 | 53.5078 | 44.1172 | 37.8175 | 34.1121 | 29.4031 | 25.5102 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Falling Short | Headroom (MW) | 82.1829 | 82.4061 | 82.4892 | 82.5532 | 81.0615 | 80.5005 | 79.731 | 78.7893 | 77.6339 | 75.0641 | 72.7659 | 70.4646 | 68.3288 | 65.8322 | 40.4881 | 18.593 | 0
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Leading the Way | Headroom (MW) | 82.1829 | 81.0435 | 76.9063 | 67.6835 | 62.8961 | 56.582 | 50.8731 | 44.1715 | 37.5137 | 29.8017 | 24.7876 | 20.5018 | 17.6458 | 15.4998 | 0 | 0 | 0
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | System Transformation | Headroom (MW) | 82.1829 | 82.5307 | 81.9951 | 75.5727 | 73.3318 | 72.1436 | 70.4209 | 67.9567 | 64.5556 | 60.2424 | 56.3281 | 53.1716 | 50.8839 | 49.8795 | 20.9942 | 10.9759 | 2.2792
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Best View | Headroom (MW) | 62.795 | 61.8795 | 60.4125 | 59.5987 | 55.6763 | 52.3583 | 48.851 | 46.2226 | 43.1103 | 39.0601 | 37.4015 | 36.7319 | 36.1928 | 36.2773 | 2.6613 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 62.795 | 59.5593 | 57.6904 | 54.4183 | 50.5884 | 46.922 | 41.112 | 34.9148 | 20.784 | 0.87454 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 62.795 | 62.7669 | 62.79 | 62.4717 | 59.1095 | 57.8795 | 56.4551 | 54.9084 | 53.176 | 50.5977 | 48.1406 | 45.5811 | 43.2875 | 41.3067 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 62.795 | 54.2184 | 48.0926 | 31.5186 | 27.7046 | 21.5166 | 15.2708 | 1.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 62.795 | 56.5379 | 53.2207 | 39.3222 | 37.8718 | 36.4115 | 34.4928 | 31.5942 | 28.6961 | 25.8976 | 22.0674 | 18.845 | 15.0973 | 12.9374 | 0 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 79.4448 | 77.6683 | 76.5599 | 75.0164 | 71.0567 | 66.7453 | 60.1552 | 53.7476 | 47.1612 | 39.0211 | 33.2291 | 29.4488 | 26.6325 | 24.1841 | 12.3112 | 10.5299 | 13.8054
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 79.4448 | 77.3685 | 75.8855 | 73.6425 | 68.5337 | 63.1634 | 55.305 | 46.3163 | 36.5494 | 24.8521 | 15.6654 | 10.0072 | 5.3198 | 1.0942 | 0 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 79.4448 | 78.3289 | 77.9791 | 76.6522 | 73.6972 | 69.5944 | 65.4629 | 61.3692 | 57.0281 | 52.1418 | 47.8205 | 43.7996 | 40.6919 | 37.7159 | 22.8802 | 14.1846 | 9.0412
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 79.4448 | 76.7561 | 75.1358 | 71.9074 | 66.7395 | 57.0043 | 48.8272 | 39.3024 | 29.8038 | 19.4725 | 12.3786 | 6.851 | 3.9131 | 1.3332 | 0 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 79.4448 | 77.9151 | 77.3139 | 75.5174 | 71.4828 | 67.1947 | 62.0818 | 55.9886 | 49.7511 | 43.2826 | 35.8267 | 30.4289 | 27.5277 | 25.4014 | 12.8639 | 12.803 | 14.0622
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.5601 | 9.3753 | 9.1339 | 8.496 | 8.3406 | 8.1572 | 7.9091 | 7.7164 | 7.4714 | 7.1706 | 7.0487 | 7.1775 | 7.3119 | 7.5163 | 5.9573 | 4.9214 | 4.148
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.5601 | 9.3324 | 9.0557 | 8.3825 | 7.9622 | 7.561 | 7.0346 | 6.4925 | 5.7431 | 4.7951 | 4.0151 | 3.4466 | 2.8958 | 2.4736 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.5601 | 9.4904 | 9.4436 | 8.9626 | 8.8328 | 8.7263 | 8.5884 | 8.3919 | 8.1618 | 7.8137 | 7.462 | 7.0987 | 6.7422 | 6.4499 | 3.1807 | 0.42257 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.5601 | 9.1816 | 8.8323 | 7.8921 | 7.4874 | 7.0539 | 6.5604 | 5.9023 | 5.1601 | 4.4226 | 3.7856 | 3.3395 | 3.1182 | 2.9321 | 0.076162 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.5601 | 9.463 | 9.3617 | 8.7845 | 8.6545 | 8.5402 | 8.3748 | 8.1025 | 7.7276 | 7.3398 | 6.911 | 6.5329 | 6.2235 | 6.0813 | 2.3486 | 0.86379 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 71.2054 | 70.3842 | 68.8864 | 61.0754 | 56.6393 | 54.7251 | 52.3768 | 50.5977 | 46.8898 | 44.9542 | 44.0154 | 44.5334 | 45.0791 | 46.2534 | 37.6718 | 32.2933 | 26.72
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 71.2054 | 70.0239 | 68.2279 | 60.728 | 55.0336 | 52.1626 | 48.3853 | 44.8084 | 38.1317 | 32.7035 | 28.3559 | 25.0896 | 21.9376 | 19.9027 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 71.2054 | 70.9904 | 70.611 | 64.6338 | 61.4483 | 60.2376 | 58.904 | 57.315 | 54.4726 | 51.7979 | 49.1511 | 46.3775 | 43.6825 | 41.6635 | 22.7108 | 8.9032 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 71.2054 | 69.185 | 67.0336 | 57.4769 | 51.7125 | 47.7129 | 44.0417 | 38.7771 | 32.3801 | 28.4988 | 25.251 | 21.9049 | 20.9565 | 20.4307 | 4.7573 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 71.2054 | 70.8237 | 70.1031 | 63.2409 | 59.1962 | 57.2298 | 55.6458 | 53.2225 | 48.6642 | 46.0808 | 43.3364 | 40.8594 | 38.826 | 38.1527 | 17.9876 | 10.8814 | 5.8677
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.8033 | 13.6425 | 13.41 | 13.3718 | 13.2613 | 13.1471 | 12.957 | 12.9429 | 12.8505 | 12.8205 | 12.9914 | 13.3982 | 13.798 | 14.2868 | 13.6021 | 13.1198 | 12.7788
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.8033 | 13.5961 | 13.3204 | 13.1554 | 12.7125 | 12.3458 | 11.8466 | 11.4295 | 10.8582 | 10.2282 | 9.8464 | 9.6728 | 9.515 | 9.4747 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.8033 | 13.7988 | 13.817 | 13.8295 | 13.7559 | 13.7348 | 13.6829 | 13.6011 | 13.4895 | 13.2783 | 13.0576 | 12.8252 | 12.6111 | 12.4693 | 9.2202 | 6.4074 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.8033 | 13.4499 | 13.1454 | 12.7633 | 12.3547 | 11.9442 | 11.5069 | 10.7505 | 10.1811 | 9.8163 | 9.5724 | 9.4822 | 9.5525 | 9.7157 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.8033 | 13.7486 | 13.7151 | 13.6605 | 13.5731 | 13.5235 | 13.432 | 13.0636 | 12.8243 | 12.6757 | 12.4897 | 12.345 | 12.3079 | 12.4533 | 8.8555 | 7.5263 | 2.337
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.4636 | 4.4438 | 4.3819 | 4.3427 | 4.2311 | 4.0998 | 3.9261 | 3.7677 | 2.2744 | 1.6894 | 1.383 | 1.4957 | 1.6154 | 1.9578 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.4636 | 4.3738 | 4.2505 | 4.1487 | 3.9451 | 3.7526 | 3.4561 | 2.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.4636 | 4.4684 | 4.4838 | 4.4678 | 4.3778 | 4.2813 | 4.187 | 4.0671 | 3.9334 | 3.7477 | 3.3786 | 2.4625 | 1.5763 | 0.94196 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.4636 | 4.3193 | 4.2036 | 4.015 | 3.8294 | 3.107 | 1.9043 | 0.12196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.4636 | 4.4215 | 4.3958 | 4.3442 | 4.2239 | 4.0913 | 3.9436 | 3.7781 | 2.8386 | 2.0406 | 1.2108 | 0.45228 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.0886 | 16.1222 | 16.0768 | 16.0606 | 15.948 | 15.8314 | 15.6353 | 15.4253 | 15.1256 | 14.8021 | 14.5997 | 14.4659 | 14.2914 | 14.1456 | 13.4644 | 13.517 | 14.0709
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.0886 | 16.0903 | 16.0275 | 15.9577 | 15.7692 | 15.5946 | 15.3267 | 15.0191 | 14.5977 | 14.0954 | 13.7384 | 13.5184 | 13.2312 | 12.977 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.0886 | 16.1578 | 16.2197 | 16.2341 | 16.1932 | 16.1571 | 16.0827 | 15.9744 | 15.8296 | 15.6853 | 15.5666 | 15.4549 | 15.3379 | 15.1937 | 13.7265 | 12.0475 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.0886 | 16.0565 | 16.0195 | 15.8991 | 15.7335 | 15.5487 | 15.2972 | 14.934 | 14.4937 | 14.0331 | 13.6814 | 13.4267 | 13.2197 | 13.0747 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.0886 | 16.1688 | 16.2203 | 16.2121 | 16.1535 | 16.1073 | 16.0128 | 15.8562 | 15.6641 | 15.4297 | 15.2578 | 15.071 | 14.8724 | 14.71 | 12.8398 | 12.3782 | 4.2902
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.1514 | 11.1382 | 11.1082 | 11.0909 | 9.963 | 9.8994 | 9.8289 | 9.8097 | 9.7778 | 9.7432 | 9.7518 | 9.807 | 9.8671 | 9.9546 | 9.6699 | 9.4246 | 9.2491
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.1514 | 10.1478 | 10.0936 | 9.2177 | 9.1111 | 8.9863 | 8.8379 | 8.724 | 8.5661 | 8.4012 | 8.2772 | 8.2078 | 8.1473 | 8.1134 | 0 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.1514 | 11.1635 | 11.1767 | 11.1825 | 10.0807 | 10.0489 | 10.0228 | 9.9898 | 9.9564 | 9.8891 | 9.8126 | 9.728 | 9.655 | 9.5913 | 8.5715 | 7.4318 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.1514 | 7.9264 | 5.8345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.1514 | 8.1815 | 6.6905 | 0.089225 | 0.062838 | 0.018053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.1508 | 10.6205 | 10.1588 | 9.4304 | 7.6199 | 5.6287 | 2.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.1508 | 10.5181 | 9.9068 | 8.9089 | 6.6441 | 4.2224 | 0.66477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.1508 | 10.816 | 10.6005 | 9.9508 | 8.5808 | 6.6357 | 4.6928 | 2.7739 | 0.77831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.1508 | 10.2855 | 9.5887 | 8.1936 | 5.8719 | 1.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.1508 | 10.6934 | 10.366 | 9.5108 | 7.6208 | 5.5907 | 3.1869 | 0.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.2995 | 11.282 | 10.8337 | 7.8191 | 5.8902 | 5.1902 | 4.3562 | 3.7318 | 2.2527 | 1.6733 | 1.3698 | 1.4815 | 1.6 | 1.9391 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.2995 | 11.1578 | 10.6052 | 7.7784 | 5.5438 | 4.6292 | 3.4232 | 2.3294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.2995 | 11.3675 | 11.3187 | 8.9989 | 7.6317 | 7.1792 | 6.7037 | 6.172 | 5.0846 | 4.2068 | 3.3465 | 2.439 | 1.5613 | 0.93299 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.2995 | 10.9219 | 10.2801 | 6.7724 | 4.4902 | 3.0775 | 1.8862 | 0.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.2995 | 11.3553 | 11.1656 | 8.5318 | 6.7585 | 5.9569 | 5.3938 | 4.5513 | 2.8116 | 2.0212 | 1.1992 | 0.44797 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Best View | Headroom (MW) | 1.7548 | 1.5758 | 1.2507 | 1.0705 | 0.8079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.7548 | 1.5154 | 1.1018 | 0.7775 | 0.011559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.7548 | 1.7672 | 1.7632 | 1.7155 | 1.5398 | 1.3883 | 1.1864 | 0.97377 | 0.73414 | 0.26542 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.7548 | 1.3006 | 0.82901 | 0.17009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.7548 | 1.7334 | 1.6463 | 1.5165 | 1.3307 | 1.1364 | 0.85862 | 0.50035 | 0.079165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.0121 | 20.0193 | 19.9083 | 19.909 | 19.764 | 19.5565 | 19.2791 | 19.1362 | 18.9018 | 18.622 | 18.5176 | 18.6336 | 18.7134 | 18.8828 | 17.078 | 15.3876 | 13.2488
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.0121 | 19.9905 | 19.8643 | 19.7945 | 19.3661 | 18.9449 | 18.4256 | 18.0196 | 17.5332 | 16.8074 | 16.2917 | 14.9257 | 8.0471 | 2.1089 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.0121 | 20.0518 | 20.1024 | 20.1834 | 20.1197 | 20.0682 | 20.0168 | 19.9333 | 19.8308 | 19.6318 | 19.4331 | 19.1929 | 18.9781 | 18.7857 | 16.0179 | 13.2954 | 8.8862
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.0121 | 19.755 | 19.4972 | 19.1972 | 18.7765 | 18.3232 | 17.831 | 17.3143 | 16.8333 | 10.7488 | 5.2123 | 2.9709 | 2.8473 | 3.6576 | 0 | 0 | 6.1789
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.0121 | 20.1588 | 20.2817 | 20.3457 | 20.3464 | 20.3116 | 20.2509 | 20.1429 | 20.0125 | 19.8328 | 19.6324 | 19.45 | 19.3606 | 19.4279 | 16.084 | 14.6256 | 13.1069
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 65.6502 | 29.3701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 65.6502 | 58.8607 | 45.4911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 65.6502 | 63.6694 | 59.7106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 65.6502 | 1.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 65.6502 | 52.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Best View | Headroom (MW) | 18.8938 | 18.4188 | 18.1291 | 17.9352 | 17.6443 | 17.3924 | 17.103 | 16.8756 | 16.5976 | 16.372 | 16.2399 | 16.2017 | 16.1659 | 16.1695 | 14.8205 | 14.156 | 13.9269
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.8938 | 18.3895 | 18.0948 | 17.8825 | 17.5576 | 17.2877 | 16.9729 | 16.6945 | 16.3573 | 16.0682 | 15.8826 | 15.7896 | 15.7155 | 15.6945 | 14.1311 | 13.3578 | 13.0877
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.8938 | 18.543 | 18.4003 | 18.2671 | 18.0891 | 17.9233 | 17.7479 | 17.5787 | 17.4079 | 17.2378 | 17.0641 | 16.8914 | 16.7349 | 16.6121 | 15.118 | 13.7319 | 12.5997
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.8938 | 18.3388 | 18.0652 | 17.7947 | 17.5063 | 17.2084 | 16.9067 | 16.5745 | 16.2372 | 16.0423 | 15.9201 | 15.8773 | 15.8953 | 15.8683 | 14.7377 | 14.268 | 13.8798
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.8938 | 18.4279 | 18.2435 | 18.0879 | 17.8892 | 17.7448 | 17.5839 | 17.3927 | 17.157 | 17.036 | 16.9112 | 16.8177 | 16.7641 | 16.7959 | 14.9483 | 14.1868 | 13.7019
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 89.1281 | 6.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 89.1281 | 8.7287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 89.1281 | 32.1543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 89.1281 | 4.6139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 89.1281 | 15.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.9251 | 10.2751 | 9.8704 | 9.7513 | 9.5834 | 9.3866 | 9.1292 | 8.9354 | 8.6649 | 8.4387 | 8.2753 | 8.1798 | 8.0499 | 7.9407 | 6.7274 | 6.1101 | 6.2363
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.9251 | 10.3305 | 9.9557 | 9.8225 | 9.593 | 9.3643 | 9.0614 | 8.8165 | 8.5082 | 8.1983 | 7.9897 | 7.8433 | 7.6637 | 7.5275 | 6.062 | 5.2362 | 5.1022
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.9251 | 10.5364 | 10.381 | 10.3652 | 10.2807 | 10.1944 | 10.108 | 10.0055 | 9.9315 | 9.8091 | 9.7019 | 9.5689 | 9.4491 | 9.34 | 7.8465 | 6.428 | 5.5663
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.9251 | 10.2116 | 9.8285 | 9.5905 | 9.3877 | 9.1816 | 8.938 | 8.6662 | 8.3705 | 8.1883 | 8.03 | 7.9108 | 7.8456 | 7.8191 | 6.7772 | 6.354 | 6.0556
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.9251 | 10.4271 | 10.2048 | 10.1527 | 10.0747 | 10.0038 | 9.9211 | 9.8277 | 9.7155 | 9.5995 | 9.4563 | 9.3197 | 9.2218 | 9.1844 | 7.3677 | 6.8482 | 6.6712
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 54.0928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 54.0928 | 36.0473 | 11.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 54.0928 | 45.2038 | 34.6628 | 13.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 54.0928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 54.0928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.3022 | 9.8195 | 9.3625 | 8.9526 | 8.6226 | 7.6045 | 6.8923 | 6.1122 | 5.2231 | 3.123 | 0.48655 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.3022 | 9.9074 | 9.49 | 9.2093 | 8.8377 | 8.5101 | 7.7286 | 7.0385 | 5.7049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.3022 | 10.1264 | 9.9717 | 9.8731 | 9.7198 | 9.5868 | 9.4448 | 9.2658 | 9.0869 | 8.8709 | 8.6649 | 8.4241 | 8.1862 | 7.9941 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.3022 | 9.812 | 9.3514 | 8.9157 | 8.5882 | 7.5646 | 6.8468 | 5.4049 | 0.050073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.3022 | 10.0647 | 9.8644 | 9.7001 | 9.5416 | 9.4337 | 9.0611 | 8.8654 | 8.583 | 8.3796 | 7.3061 | 6.3433 | 5.6552 | 4.3171 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.3285 | 19.138 | 18.8985 | 18.6351 | 18.3073 | 17.9455 | 17.5481 | 17.2257 | 16.8875 | 16.6539 | 16.6207 | 16.6826 | 16.7775 | 16.8931 | 10.417 | 5.2365 | 0.19131
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.3285 | 19.1234 | 18.858 | 18.5628 | 18.1264 | 17.6558 | 17.0838 | 16.4985 | 15.8889 | 15.2901 | 14.9066 | 14.7196 | 14.57 | 14.4595 | 5.4952 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.3285 | 19.1901 | 19.032 | 18.8375 | 18.5737 | 18.3021 | 18.0173 | 17.737 | 17.4573 | 17.2066 | 17.0446 | 16.9 | 16.7699 | 16.651 | 15.7907 | 15.5094 | 9.1819
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.3285 | 19.0464 | 18.7258 | 18.3147 | 17.8373 | 17.2975 | 16.7122 | 16.1062 | 14.216 | 11.2524 | 9.2723 | 7.9125 | 7.2626 | 6.978 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.3285 | 19.1749 | 18.9723 | 18.7132 | 18.3984 | 18.0679 | 17.71 | 17.3405 | 16.9784 | 16.6657 | 16.4423 | 16.3066 | 16.2185 | 16.2009 | 11.4995 | 8.7358 | 6.1193
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 28.8259 | 28.684 | 28.4802 | 28.3914 | 28.2071 | 27.9722 | 27.759 | 27.6551 | 27.488 | 27.4293 | 27.4624 | 27.6211 | 27.7631 | 27.9076 | 27.2436 | 26.7462 | 26.1683
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 28.8259 | 28.5788 | 28.3311 | 28.1425 | 27.8063 | 27.4597 | 27.0732 | 26.8199 | 26.484 | 26.1826 | 26.0131 | 25.9497 | 25.8962 | 25.8831 | 24.5315 | 19.126 | 20.1107
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 28.8259 | 28.7282 | 28.6638 | 28.6109 | 28.4941 | 28.3748 | 28.2875 | 28.182 | 28.0834 | 27.9985 | 27.9223 | 27.8276 | 27.7286 | 27.6706 | 26.0733 | 24.833 | 23.6
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 28.8259 | 28.4946 | 28.2165 | 27.8969 | 27.5842 | 27.202 | 26.8672 | 26.5832 | 26.3235 | 26.1995 | 26.1219 | 26.1294 | 26.196 | 26.3151 | 25.6895 | 25.6165 | 24.834
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 28.8259 | 28.6826 | 28.6007 | 28.4962 | 28.3726 | 28.2386 | 28.1508 | 28.0661 | 27.9507 | 27.9166 | 27.8462 | 27.7987 | 27.7903 | 27.8848 | 26.2164 | 25.889 | 25.7226
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.1674 | 6.5863 | 6.4586 | 6.4369 | 6.3048 | 6.1203 | 5.8702 | 5.6488 | 5.45 | 3.2017 | 0.4988 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.1674 | 6.5517 | 6.3001 | 6.2073 | 5.8556 | 5.5314 | 5.0779 | 4.6382 | 4.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.1674 | 6.8031 | 6.7837 | 6.8262 | 6.7719 | 6.7238 | 6.6611 | 6.4829 | 6.3485 | 6.1975 | 6.0672 | 5.9254 | 5.7817 | 5.6672 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.1674 | 6.3567 | 6.0631 | 5.7708 | 5.4632 | 5.1019 | 4.7377 | 4.2198 | 0.051333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.1674 | 6.7251 | 6.6762 | 6.7014 | 6.6676 | 6.6342 | 6.5609 | 6.342 | 6.1887 | 6.137 | 6.0698 | 6.0145 | 5.7975 | 4.4258 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.5637 | 14.7075 | 14.8506 | 14.9922 | 15.1325 | 6.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.5637 | 14.7075 | 14.8506 | 14.9922 | 15.1325 | 15.2715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.5637 | 14.7075 | 14.8506 | 14.9922 | 15.1325 | 15.2715 | 12.8184 | 0.13416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.5637 | 14.7075 | 14.8506 | 14.9922 | 15.1325 | 1.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.5637 | 14.7075 | 14.8506 | 14.9922 | 15.1325 | 15.2715 | 0.80977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.524 | 6.2493 | 5.8647 | 5.7015 | 5.1247 | 4.5882 | 3.9304 | 3.4076 | 2.7705 | 2.2596 | 1.8921 | 1.748 | 1.5859 | 1.3637 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.524 | 6.468 | 6.4169 | 6.4044 | 6.214 | 6.0288 | 5.8353 | 5.6231 | 5.3808 | 5.1407 | 4.9269 | 4.7097 | 4.5013 | 4.343 | 1.7271 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.524 | 0.27529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.5686 | 5.3776 | 5.1445 | 5.0419 | 4.517 | 3.9935 | 3.3993 | 2.9395 | 2.3137 | 1.4382 | 0.85085 | 0.54391 | 0.2618 | 0.082095 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.5686 | 5.5856 | 5.6351 | 5.7059 | 5.5765 | 5.4485 | 5.321 | 5.1613 | 4.9528 | 4.6974 | 4.4828 | 4.2297 | 3.9854 | 3.7698 | 0.97574 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.2344 | 7.8676 | 7.3046 | 6.7218 | 6.1352 | 4.9274 | 4.0196 | 3.2937 | 2.4818 | 1.3147 | 0.48897 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.2344 | 7.8566 | 7.2813 | 6.6323 | 5.7334 | 4.9353 | 3.7084 | 2.5269 | 1.2625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.2344 | 7.9568 | 7.6268 | 7.204 | 6.762 | 6.4121 | 6.0589 | 5.7099 | 5.3502 | 4.9091 | 4.4725 | 4.1164 | 3.8191 | 3.5465 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.2344 | 7.7021 | 6.9922 | 6.0738 | 5.0912 | 3.5169 | 2.2899 | 1.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.2344 | 7.964 | 7.5391 | 6.9545 | 6.3848 | 5.9322 | 5.4699 | 4.9921 | 4.4957 | 3.97 | 2.9944 | 2.2523 | 1.692 | 1.2813 | 0 | 0 | 0
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.4619 | 10.5356 | 10.5806 | 10.6281 | 10.6684 | 10.681 | 10.6745 | 10.714 | 10.7141 | 10.7634 | 10.8503 | 10.9849 | 11.1179 | 11.2756 | 10.8022 | 10.8617 | 10.7304
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.4619 | 10.5099 | 10.5332 | 10.5619 | 10.5456 | 10.5209 | 10.4755 | 10.452 | 10.3949 | 10.3522 | 10.3512 | 10.3959 | 6.2417 | 1.6357 | 0 | 0 | 0
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.4619 | 10.5535 | 10.6395 | 10.7062 | 10.7575 | 10.8072 | 10.8499 | 10.8896 | 10.9193 | 10.9508 | 10.9927 | 11.0192 | 11.049 | 11.092 | 10.8734 | 10.9403 | 6.8925
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.4619 | 10.477 | 10.4944 | 10.4692 | 10.4528 | 10.4231 | 10.3865 | 10.345 | 10.2949 | 8.3324 | 4.0429 | 2.3043 | 2.2085 | 2.837 | 0 | 0 | 4.7926
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.4619 | 10.5536 | 10.6455 | 10.7185 | 10.7735 | 10.8255 | 10.8785 | 10.9114 | 10.9402 | 10.9964 | 11.0402 | 11.0942 | 11.171 | 11.2841 | 11.1809 | 11.4134 | 11.2424
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.5126 | 7.2802 | 7.1731 | 7.0936 | 6.9259 | 6.0415 | 5.4314 | 4.9472 | 4.3664 | 3.4503 | 3.0469 | 2.4953 | 1.9395 | 1.4395 | 0 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.5126 | 7.2407 | 7.0967 | 6.9913 | 6.5801 | 6.1893 | 5.3824 | 4.6791 | 3.8693 | 2.5541 | 1.782 | 1.2108 | 0.29624 | 0 | 0 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.5126 | 7.4165 | 7.4576 | 7.4743 | 7.4051 | 7.3571 | 7.2935 | 7.2084 | 7.1071 | 6.9127 | 6.7073 | 6.5 | 6.2889 | 6.1335 | 2.8446 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.5126 | 7.0875 | 6.8847 | 6.5635 | 6.158 | 5.0452 | 4.2768 | 3.4495 | 2.6593 | 1.551 | 0.90907 | 0.064516 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.5126 | 7.389 | 7.4411 | 7.4305 | 7.375 | 7.3203 | 7.2431 | 7.1276 | 6.972 | 6.8264 | 6.3039 | 5.8236 | 5.4215 | 5.1832 | 1.5323 | 0.32883 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.7749 | 5.5768 | 5.3351 | 5.2287 | 4.6843 | 4.1415 | 3.5253 | 3.0484 | 2.3937 | 1.4879 | 0.88025 | 0.56271 | 0.27085 | 0.084932 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.7749 | 5.7925 | 5.8438 | 5.9172 | 5.7831 | 5.6504 | 5.5181 | 5.3525 | 5.1362 | 4.8714 | 4.6489 | 4.3864 | 4.1331 | 3.9001 | 1.0095 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.7749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.9288 | 15.7183 | 15.3901 | 15.0145 | 14.5612 | 14.0967 | 13.6539 | 13.3093 | 12.8647 | 12.511 | 12.3156 | 12.3375 | 12.4114 | 12.56 | 10.7416 | 9.3498 | 7.9023
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.9288 | 15.7072 | 15.3753 | 15.0237 | 14.3471 | 13.7166 | 13.0481 | 12.5472 | 11.9229 | 11.1439 | 10.5867 | 10.2657 | 8.0677 | 2.1143 | 0 | 0 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.9288 | 15.8789 | 15.7901 | 15.6107 | 15.3829 | 15.1859 | 15.0255 | 14.8625 | 14.6882 | 14.3956 | 14.1 | 13.7924 | 13.5141 | 13.2587 | 10.3017 | 7.7184 | 5.4683
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.9288 | 15.5816 | 15.1818 | 14.5929 | 13.9057 | 13.2127 | 12.5939 | 12.0024 | 11.409 | 10.7764 | 5.2256 | 2.9785 | 2.8546 | 3.6669 | 0 | 0 | 6.1947
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.9288 | 15.8593 | 15.7228 | 15.4745 | 15.202 | 14.9465 | 14.7572 | 14.5404 | 14.2517 | 13.9872 | 13.7052 | 13.4732 | 13.3434 | 13.3873 | 10.116 | 8.7453 | 7.536
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.9849 | 8.8644 | 8.41 | 8.4027 | 8.2948 | 8.0124 | 7.7357 | 7.5545 | 7.4118 | 7.2942 | 7.2055 | 7.2148 | 7.2087 | 7.2355 | 6.6658 | 5.1941 | 0.18976
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.9849 | 8.8829 | 8.4241 | 8.351 | 8.1828 | 7.837 | 7.3573 | 6.9702 | 6.6134 | 6.2999 | 6.0534 | 5.8987 | 5.7059 | 5.5553 | 4.3675 | 0 | 0
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.9849 | 8.9531 | 8.6782 | 8.6817 | 8.653 | 8.5188 | 8.3698 | 8.2413 | 8.162 | 8.0809 | 7.9902 | 7.8822 | 7.7804 | 7.6967 | 6.4008 | 5.0216 | 4.2058
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.9849 | 8.8139 | 8.2984 | 8.1466 | 7.9508 | 7.5615 | 7.0861 | 6.6748 | 6.375 | 6.1935 | 6.0266 | 5.8936 | 5.8285 | 5.8171 | 0 | 0 | 0
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.9849 | 8.9542 | 8.5769 | 8.5393 | 8.5129 | 8.3511 | 8.1344 | 7.9488 | 7.8359 | 7.7685 | 7.6705 | 7.5651 | 7.4756 | 7.4298 | 5.796 | 5.3017 | 5.2917
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.4201 | 17.4504 | 17.4701 | 17.5089 | 17.4976 | 5.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.4201 | 17.4575 | 17.4827 | 17.5174 | 17.4902 | 12.6166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.4201 | 17.4475 | 17.4952 | 17.5463 | 17.5715 | 17.5634 | 9.3602 | 0.097966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.4201 | 17.4271 | 17.4482 | 17.4655 | 17.4378 | 1.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.4201 | 17.4588 | 17.5187 | 17.5695 | 17.5958 | 15.6227 | 0.59131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.1514 | 6.5715 | 6.4442 | 6.4224 | 6.2906 | 6.1065 | 5.8569 | 5.636 | 5.4376 | 3.1976 | 0.49817 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.1514 | 6.537 | 6.286 | 6.1934 | 5.8424 | 5.5189 | 5.0664 | 4.6277 | 4.1792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.1514 | 6.7879 | 6.7686 | 6.8109 | 6.7567 | 6.7086 | 6.6461 | 6.4683 | 6.3341 | 6.1835 | 6.0534 | 5.9119 | 5.7684 | 5.6543 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.1514 | 6.3425 | 6.0495 | 5.7578 | 5.4509 | 5.0903 | 4.7269 | 4.2101 | 0.051268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.1514 | 6.7101 | 6.6612 | 6.6864 | 6.6526 | 6.6192 | 6.5461 | 6.3277 | 6.1747 | 6.1231 | 6.056 | 6.0008 | 5.7902 | 4.4201 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 32.1779 | 28.0737 | 24.1963 | 20.1625 | 12.0217 | 1.8716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.1779 | 28.2616 | 24.2388 | 20.6738 | 12.2341 | 2.9327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.1779 | 29.4333 | 26.8386 | 23.8526 | 21.3162 | 18.821 | 10.4377 | 1.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.1779 | 28.3574 | 24.8454 | 21.1072 | 8.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.1779 | 28.6337 | 25.0235 | 21.8979 | 15.7698 | 7.5418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.6828 | 13.2188 | 12.7734 | 12.337 | 11.9611 | 11.1395 | 10.4901 | 9.6195 | 7.4427 | 3.1237 | 0.48665 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.6828 | 13.3173 | 12.8938 | 12.5992 | 12.1666 | 11.7758 | 11.0521 | 10.4285 | 5.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.6828 | 13.56 | 13.4505 | 13.3673 | 13.1723 | 13.0048 | 12.8103 | 12.5896 | 12.3598 | 12.0461 | 11.753 | 11.4282 | 11.1012 | 10.806 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.6828 | 13.2145 | 12.763 | 12.303 | 11.9231 | 11.0995 | 10.4474 | 5.406 | 0.050083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.6828 | 13.4981 | 13.3311 | 13.1706 | 12.9767 | 12.7702 | 12.4286 | 11.895 | 11.4966 | 11.1013 | 10.0638 | 7.8041 | 5.6563 | 4.318 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 53.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 53.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 53.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 53.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 53.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Best View | Headroom (MW) | 28.1083 | 28.0399 | 27.937 | 27.8503 | 27.7432 | 27.6084 | 27.426 | 27.3141 | 24.5134 | 16.2523 | 11.2499 | 6.8562 | 2.4719 | 0 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 28.1083 | 28.0186 | 27.9003 | 27.8001 | 27.548 | 27.3105 | 27.0183 | 26.7783 | 20.8675 | 9.4277 | 1.8309 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Falling Short | Headroom (MW) | 28.1083 | 28.1165 | 28.1262 | 28.1251 | 28.0474 | 27.9792 | 27.8997 | 27.8054 | 27.6944 | 27.5515 | 27.4124 | 27.2684 | 27.1371 | 27.0393 | 1.6288 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Leading the Way | Headroom (MW) | 28.1083 | 27.9475 | 27.8113 | 27.5949 | 27.3539 | 27.0977 | 26.8177 | 20.3574 | 10.0036 | 1.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | System Transformation | Headroom (MW) | 28.1083 | 28.116 | 28.1235 | 28.1044 | 28.0527 | 27.9946 | 27.9224 | 27.8249 | 27.6912 | 27.6293 | 27.555 | 25.6077 | 21.5083 | 19.0199 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.4005 | 8.3435 | 8.259 | 8.2127 | 8.1218 | 8.0207 | 7.8954 | 7.8077 | 7.6659 | 7.5246 | 7.4284 | 7.3792 | 7.0342 | 6.9951 | 5.8715 | 5.1664 | 4.4697
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.4005 | 8.3353 | 8.2442 | 8.1826 | 8.071 | 7.9622 | 7.8207 | 7.7073 | 7.5365 | 7.3618 | 7.2376 | 7.1647 | 6.7966 | 6.7443 | 5.4915 | 4.7054 | 3.6793
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.4005 | 8.3932 | 8.3748 | 8.3648 | 8.3157 | 8.2748 | 8.23 | 8.1762 | 8.1212 | 8.0278 | 7.9394 | 7.8424 | 7.7497 | 7.6593 | 6.4061 | 5.5774 | 4.7179
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.4005 | 8.3066 | 8.2106 | 8.1041 | 8.0059 | 7.891 | 7.7712 | 7.6256 | 7.4488 | 7.3361 | 7.238 | 7.173 | 7.1121 | 7.1087 | 6.1583 | 5.0862 | 3.7786
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.4005 | 8.3791 | 8.3444 | 8.3076 | 8.2604 | 8.0746 | 8.023 | 7.944 | 7.5945 | 7.5083 | 7.4152 | 7.3336 | 7.2601 | 6.945 | 5.574 | 4.0868 | 2.2731
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 29.0421 | 20.7605 | 12.8212 | 7.4721 | 3.9268 | 0.72908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 29.0421 | 20.7419 | 12.7923 | 7.3991 | 3.7865 | 1.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 29.0421 | 22.5542 | 16.8319 | 11.6968 | 8.7849 | 6.0008 | 3.2699 | 0.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 29.0421 | 20.049 | 12.2584 | 5.7398 | 1.9556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 29.0421 | 20.8868 | 13.1291 | 7.8369 | 4.4581 | 2.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.70639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.70639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.70639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.70639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.70639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 26.8319 | 26.4588 | 26.0646 | 15.9866 | 7.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 26.8319 | 26.3523 | 25.8579 | 16.8819 | 8.2129 | 2.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 26.8319 | 26.5643 | 26.332 | 18.3278 | 12.1155 | 6.2885 | 0.54321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 26.8319 | 26.1829 | 25.587 | 15.1393 | 6.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 26.8319 | 26.5031 | 26.2061 | 17.3464 | 9.0389 | 3.3631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.1526 | 7.1125 | 7.0197 | 6.973 | 6.8547 | 6.7317 | 6.5898 | 6.4942 | 5.1332 | 0.71622 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.1526 | 7.1141 | 7.0197 | 6.9709 | 6.8216 | 6.6861 | 6.5225 | 6.3828 | 4.1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.1526 | 7.1693 | 7.172 | 7.1731 | 7.1363 | 7.098 | 7.0605 | 7.0111 | 6.9462 | 6.8274 | 6.7096 | 6.588 | 5.1563 | 3.0552 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.1526 | 7.0799 | 7.0013 | 6.8762 | 6.7372 | 6.5847 | 6.4278 | 2.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.1526 | 7.1506 | 7.1476 | 7.126 | 7.0938 | 7.0363 | 6.9905 | 6.9005 | 6.777 | 6.6863 | 5.7087 | 2.4023 | 0.20014 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.3846 | 5.1153 | 4.8254 | 4.5253 | 4.2491 | 3.9555 | 3.6341 | 3.2841 | 2.8913 | 2.6989 | 0.49291 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.3846 | 5.1803 | 4.9195 | 4.7072 | 4.4195 | 4.1558 | 3.7948 | 3.4986 | 3.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.3846 | 5.2929 | 5.1814 | 5.0721 | 4.9088 | 4.7631 | 4.608 | 4.4724 | 4.3417 | 4.1596 | 3.9958 | 3.8115 | 3.626 | 3.4523 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.3846 | 5.1146 | 4.8235 | 4.5079 | 4.2294 | 3.9331 | 3.6072 | 3.2523 | 0.050727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.3846 | 5.2637 | 5.0941 | 4.9322 | 4.7558 | 4.3693 | 4.1874 | 3.99 | 3.7513 | 2.9974 | 2.7953 | 2.6265 | 2.4777 | 2.4091 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.5411 | 10.8399 | 9.9398 | 9.07 | 8.4772 | 7.9652 | 7.3353 | 6.7812 | 6.0576 | 5.4336 | 4.8387 | 4.8115 | 4.7713 | 4.776 | 3.6273 | 3.0644 | 0.18999
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.5411 | 10.7875 | 9.8423 | 8.9026 | 8.2047 | 7.5903 | 6.8312 | 6.1153 | 5.233 | 4.3319 | 3.5092 | 3.273 | 3.0141 | 2.8228 | 0.93105 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.5411 | 11.0437 | 10.5067 | 9.7352 | 9.3077 | 8.8837 | 8.4549 | 8.0351 | 7.5657 | 7.0472 | 6.4896 | 6.0724 | 5.6674 | 5.3621 | 3.2537 | 1.6365 | 0.22869
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.5411 | 10.6424 | 9.7103 | 8.4757 | 7.7479 | 6.9926 | 6.2362 | 5.4733 | 4.6795 | 4.0206 | 3.4797 | 3.349 | 3.3012 | 3.3402 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.5411 | 10.9007 | 10.1324 | 9.2807 | 8.795 | 8.4081 | 7.9399 | 7.4302 | 6.8059 | 6.2445 | 5.5823 | 5.3719 | 5.1913 | 5.1389 | 3.0733 | 2.6597 | 2.4139
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.8825 | 5.0885 | 3.3823 | 2.4543 | 1.2267 | 0.0074993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.8825 | 4.991 | 3.2338 | 2.1342 | 0.21996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.8825 | 5.5817 | 4.9134 | 4.357 | 3.7372 | 3.228 | 2.3932 | 1.7357 | 1.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.8825 | 4.6195 | 2.8785 | 1.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.8825 | 5.4612 | 4.4542 | 3.7383 | 3.0046 | 2.3971 | 1.3182 | 0.49814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.3386 | 19.1633 | 17.3569 | 14.7271 | 12.9197 | 1.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.3386 | 18.93 | 16.8873 | 14.0378 | 11.2799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.3386 | 20.0073 | 19.2521 | 17.3342 | 16.1321 | 5.9912 | 4.8343 | 3.5989 | 2.2651 | 0.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.3386 | 18.3191 | 16.1283 | 12.1499 | 9.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.3386 | 19.5454 | 18.3927 | 16.0548 | 14.4305 | 3.8585 | 2.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.6863 | 6.3218 | 5.7678 | 5.2781 | 4.3594 | 3.5647 | 2.107 | 0.88471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.6863 | 6.3163 | 5.7607 | 5.2493 | 4.0792 | 3.1008 | 1.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.6863 | 6.5055 | 6.2939 | 6.0266 | 5.5345 | 5.1672 | 4.6308 | 4.1571 | 3.6816 | 3.0197 | 2.3682 | 1.7836 | 1.3236 | 0.93547 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.6863 | 6.1549 | 5.553 | 4.7565 | 3.5501 | 1.7485 | 0.023939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.6863 | 6.4364 | 6.1289 | 5.7411 | 5.0757 | 4.5803 | 3.8679 | 3.2125 | 2.5619 | 1.8224 | 0.67383 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.6698 | 17.6442 | 17.58 | 14.9341 | 13.1013 | 1.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.6698 | 17.6199 | 17.1246 | 14.2351 | 11.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.6698 | 17.6791 | 17.6742 | 16.6479 | 16.3589 | 6.0754 | 4.9023 | 3.6495 | 2.2969 | 0.27471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.6698 | 17.577 | 16.3549 | 12.3206 | 9.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.6698 | 17.6652 | 17.6554 | 16.2804 | 14.6333 | 3.9127 | 2.0289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 21.8345 | 10.4598 | 0.70878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 21.8345 | 9.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 21.8345 | 14.9056 | 10.8477 | 0.45437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 21.8345 | 5.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 21.8345 | 12.4772 | 6.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.346 | 9.728 | 9.0052 | 8.5424 | 7.9134 | 1.5852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.346 | 9.6914 | 8.9322 | 8.3958 | 7.5659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.346 | 9.9418 | 9.525 | 9.1532 | 8.7102 | 5.6911 | 4.5922 | 3.4186 | 2.1516 | 0.25733 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.346 | 9.5468 | 8.7678 | 7.9859 | 7.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.346 | 9.8347 | 9.2672 | 8.8395 | 8.3055 | 3.6652 | 1.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.1621 | 11.1242 | 11.0027 | 10.8722 | 10.6466 | 10.3099 | 10.0315 | 9.8175 | 9.5651 | 9.3366 | 9.1542 | 9.1416 | 9.1188 | 9.1089 | 7.5893 | 5.8966 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.1621 | 11.1162 | 10.9708 | 10.8132 | 10.4973 | 10.1141 | 9.6991 | 9.3095 | 8.876 | 8.3727 | 7.9311 | 7.5386 | 7.1234 | 6.7429 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.1621 | 11.182 | 11.1696 | 11.1371 | 11.0124 | 10.8264 | 10.6872 | 10.5365 | 10.3555 | 10.1727 | 9.9823 | 9.7804 | 9.5577 | 9.3182 | 7.1528 | 0.087132 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.1621 | 11.051 | 10.8776 | 10.6024 | 10.2358 | 9.7328 | 9.2847 | 8.8283 | 8.3748 | 7.9329 | 7.5028 | 7.2361 | 7.0916 | 6.9615 | 0 | 0 | 0
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.1621 | 11.176 | 11.1263 | 11.0276 | 10.8397 | 10.5742 | 10.3408 | 10.1105 | 9.8725 | 9.6273 | 9.3401 | 9.0775 | 8.8003 | 8.6378 | 6.3794 | 5.7257 | 0.65791
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.7217 | 10.657 | 10.6345 | 10.6973 | 10.7401 | 10.7573 | 10.7148 | 10.3208 | 10.2215 | 10.1072 | 10.0409 | 10.0658 | 10.084 | 10.1123 | 9.3414 | 5.98 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.7217 | 10.6365 | 10.5873 | 10.6203 | 10.5071 | 10.3966 | 10.2231 | 9.6944 | 9.4659 | 9.158 | 8.93 | 8.8325 | 8.6836 | 8.574 | 0 | 0 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.7217 | 10.7592 | 10.8672 | 10.9887 | 11.0305 | 11.0834 | 11.1151 | 10.9045 | 10.8535 | 10.8063 | 10.7295 | 10.6446 | 10.5615 | 10.4699 | 9.5538 | 0.088364 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.7217 | 10.5315 | 10.4463 | 10.3872 | 10.3245 | 10.2567 | 10.1586 | 9.6235 | 9.4321 | 9.2244 | 9.0264 | 8.8577 | 8.76 | 8.7129 | 0 | 0 | 0
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.7217 | 10.7431 | 10.8378 | 10.9627 | 11.0451 | 11.1142 | 11.1677 | 10.8196 | 10.8098 | 10.7544 | 10.6706 | 10.5569 | 10.4589 | 10.4111 | 9.3409 | 5.8067 | 0.66722
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 28.9181 | 28.6152 | 28.062 | 27.7517 | 27.2074 | 26.6342 | 25.5159 | 24.6449 | 23.5701 | 22.317 | 21.7179 | 21.4974 | 20.9016 | 20.4252 | 14.7811 | 11.6728 | 9.4804
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 28.9181 | 28.5407 | 27.933 | 27.4996 | 26.5778 | 25.6408 | 24.0926 | 22.7187 | 21.1162 | 19.0577 | 17.684 | 16.7162 | 15.4204 | 14.2732 | 5.1604 | 0.91759 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 28.9181 | 28.8337 | 28.7068 | 28.5352 | 28.2038 | 27.8721 | 27.4904 | 27.0879 | 26.6526 | 26.0753 | 25.5053 | 24.9153 | 24.3502 | 23.8614 | 17.8934 | 12.4525 | 8.3164
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 28.9181 | 28.3463 | 27.7307 | 26.9666 | 26.0167 | 24.289 | 22.8327 | 21.2811 | 19.7417 | 18.1047 | 16.9876 | 15.7773 | 14.8339 | 14.0729 | 7.4742 | 4.4439 | 2.7001
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 28.9181 | 28.7791 | 28.5605 | 28.3151 | 27.9393 | 27.5529 | 27.0636 | 26.5008 | 25.8471 | 25.3745 | 24.4964 | 23.6717 | 22.9992 | 22.588 | 15.8262 | 13.3053 | 11.3172
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.2814 | 18.3373 | 17.5086 | 14.8558 | 13.0326 | 1.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.2814 | 18.3373 | 17.0348 | 14.1605 | 11.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.2814 | 18.3373 | 18.3928 | 17.4857 | 16.2731 | 6.0436 | 4.8766 | 3.6303 | 2.2848 | 0.27327 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.2814 | 18.3373 | 16.2692 | 12.256 | 9.3994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.2814 | 18.3373 | 18.3928 | 16.1951 | 14.5566 | 3.8922 | 2.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.3802 | 18.4262 | 18.1992 | 18.2052 | 18.1627 | 18.1111 | 17.973 | 17.9247 | 17.8022 | 17.673 | 17.6689 | 17.8106 | 17.9464 | 18.1104 | 5.5943 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.3802 | 18.418 | 18.1999 | 18.2121 | 17.9577 | 17.743 | 17.4338 | 17.2003 | 16.8879 | 16.4445 | 16.1518 | 16.0161 | 12.263 | 8.8046 | 0 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.3802 | 18.5089 | 18.4803 | 18.5741 | 18.5859 | 18.6197 | 18.6172 | 18.5947 | 18.5609 | 18.45 | 18.3325 | 18.2156 | 18.082 | 17.9764 | 16.0538 | 11.381 | 0.19661
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.3802 | 18.33 | 18.0916 | 17.9678 | 17.7267 | 17.4997 | 17.2196 | 16.9341 | 16.6312 | 16.2914 | 16.0372 | 12.8837 | 10.1787 | 8.0554 | 0 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.3802 | 18.5191 | 18.4245 | 18.5078 | 18.5356 | 18.5653 | 18.5422 | 18.5112 | 18.4475 | 18.3635 | 18.2547 | 18.1793 | 18.1393 | 18.1812 | 15.8919 | 15.0857 | 13.6934
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.4544 | 15.41 | 15.2202 | 15.0653 | 14.7841 | 13.8391 | 13.0813 | 12.6044 | 11.9873 | 11.0397 | 10.6093 | 10.0694 | 9.5043 | 8.9943 | 3.7067 | 0 | 0
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.4544 | 15.3891 | 15.1718 | 14.986 | 14.3492 | 13.8148 | 12.7373 | 11.8934 | 10.9381 | 9.4375 | 8.4995 | 7.8061 | 6.7021 | 5.7221 | 0 | 0 | 0
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.4544 | 15.5718 | 15.6767 | 15.7317 | 15.5888 | 15.5082 | 15.3673 | 15.2588 | 15.1167 | 14.8939 | 14.6909 | 14.4451 | 14.2178 | 13.9985 | 10.1567 | 6.2552 | 0.19667
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.4544 | 15.1604 | 14.8652 | 14.4081 | 13.7999 | 12.5284 | 11.5175 | 10.5586 | 9.6488 | 8.361 | 7.5268 | 6.4908 | 5.6161 | 4.8209 | 0 | 0 | 0
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.4544 | 15.6128 | 15.6914 | 15.681 | 15.548 | 15.4583 | 15.2959 | 15.1793 | 15.0271 | 14.8024 | 14.2066 | 13.6184 | 13.1074 | 12.7546 | 8.3936 | 7.4879 | 6.9349
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 56.7794 | 51.4922 | 43.7257 | 39.5223 | 30.3656 | 15.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 56.7794 | 51.5174 | 43.5927 | 38.7911 | 22.3989 | 7.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 56.7794 | 56.0309 | 56.0402 | 56.3919 | 52.3563 | 48.337 | 39.5475 | 33.9123 | 27.8556 | 19.483 | 11.0661 | 2.2311 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 56.7794 | 47.0656 | 37.4949 | 27.0768 | 11.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 56.7794 | 55.5927 | 53.5723 | 52.2011 | 46.961 | 42.1651 | 30.904 | 23.5676 | 15.463 | 5.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 56.704 | 51.1032 | 45.4806 | 41.4433 | 34.22 | 22.3948 | 8.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 56.704 | 50.5097 | 44.3876 | 39.6999 | 23.0537 | 7.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 56.704 | 56.106 | 57.9599 | 58.4036 | 54.942 | 51.9827 | 47.96 | 40.9674 | 32.1964 | 20.4998 | 7.9831 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 56.704 | 46.2213 | 39.1054 | 27.9047 | 11.9214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 56.704 | 55.6337 | 56.5795 | 56.0055 | 52.4287 | 48.5502 | 42.9192 | 30.966 | 17.8101 | 5.1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 9.4558 | 9.4159 | 9.3027 | 9.2937 | 9.1807 | 9.0293 | 8.7675 | 8.6133 | 8.3095 | 7.8928 | 7.6276 | 7.5784 | 7.5051 | 7.4759 | 4.7553 | 3.0583 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 9.4558 | 9.3974 | 9.29 | 9.2702 | 8.8881 | 8.5163 | 8.023 | 7.6507 | 7.1199 | 6.3073 | 5.6946 | 5.2598 | 4.7626 | 4.3425 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 9.4558 | 9.5396 | 9.6315 | 9.7218 | 9.694 | 9.6798 | 9.6409 | 9.5833 | 9.4668 | 9.2051 | 8.9343 | 8.6381 | 8.3385 | 8.0386 | 4.6599 | 0.088165 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 9.4558 | 9.2908 | 9.1497 | 8.9695 | 8.6265 | 8.263 | 7.8501 | 7.3623 | 6.8443 | 6.1859 | 5.5961 | 5.1135 | 4.7867 | 4.5288 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 9.4558 | 9.5875 | 9.6673 | 9.744 | 9.7741 | 9.7587 | 9.7007 | 9.5996 | 9.4218 | 9.126 | 8.7894 | 8.4357 | 8.1532 | 7.9675 | 3.812 | 2.1868 | 0.66571
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.9448 | 19.3842 | 19.0911 | 19.0242 | 18.9227 | 18.7876 | 18.414 | 18.1882 | 17.7966 | 17.3804 | 16.9558 | 16.7067 | 16.6345 | 16.5923 | 5.5827 | 0 | 0
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.9448 | 19.4428 | 19.1437 | 19.0453 | 18.8156 | 18.6112 | 18.1218 | 17.7776 | 17.1961 | 16.5794 | 15.985 | 15.4335 | 12.2376 | 8.7864 | 0 | 0 | 0
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.9448 | 19.6016 | 19.5429 | 19.5712 | 19.5472 | 19.5019 | 19.2803 | 19.1259 | 18.9469 | 18.787 | 18.6272 | 18.4347 | 18.3553 | 18.288 | 17.6267 | 11.3575 | 0.1962
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.9448 | 19.3026 | 18.9379 | 18.7804 | 18.6273 | 18.4148 | 17.9671 | 17.5921 | 17.0188 | 16.4442 | 15.7946 | 12.857 | 10.1576 | 8.0387 | 0 | 0 | 0
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.9448 | 19.5217 | 19.3305 | 19.3044 | 19.24 | 19.1994 | 18.9658 | 18.8257 | 18.6043 | 18.335 | 17.9982 | 17.6206 | 17.4036 | 17.272 | 16.7632 | 15.4508 | 13.6651
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.5507 | 6.536 | 6.2054 | 5.9866 | 5.6778 | 1.6597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.5507 | 6.5015 | 6.1456 | 5.8965 | 5.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.5507 | 6.5659 | 6.3971 | 6.2301 | 6.0216 | 5.7909 | 4.808 | 3.5793 | 2.2527 | 0.26942 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.5507 | 6.465 | 6.1329 | 5.7876 | 5.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.5507 | 6.5516 | 6.2649 | 6.0667 | 5.5606 | 3.8374 | 1.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.3522 | 7.1924 | 6.939 | 6.7326 | 6.4959 | 1.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.3522 | 7.1406 | 6.8372 | 6.5426 | 6.1845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.3522 | 7.2588 | 7.1088 | 6.924 | 6.7288 | 5.8161 | 4.693 | 3.4937 | 2.1988 | 0.26298 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.3522 | 7.0789 | 6.7491 | 6.3518 | 5.9922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.3522 | 7.2025 | 6.9823 | 6.7294 | 6.4853 | 3.7456 | 1.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.2318 | 18.2323 | 18.173 | 18.2076 | 18.0433 | 17.8547 | 17.063 | 17.0628 | 16.964 | 16.8218 | 16.7449 | 16.8465 | 16.9012 | 16.9812 | 5.5864 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.2318 | 18.2245 | 18.1687 | 18.18 | 17.7952 | 17.4955 | 16.5805 | 16.3711 | 16.0825 | 15.7187 | 15.439 | 15.2867 | 12.2456 | 8.7921 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.2318 | 18.3435 | 18.503 | 18.6571 | 18.6065 | 18.5586 | 18.127 | 18.1273 | 18.1004 | 18.0709 | 18.0244 | 17.9544 | 17.8642 | 17.7866 | 16.6644 | 11.3649 | 0.19633
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.2318 | 18.1022 | 17.9766 | 17.8541 | 17.5317 | 17.1841 | 16.2698 | 16.0193 | 15.8014 | 15.5558 | 15.3125 | 12.8654 | 10.1643 | 8.044 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.2318 | 18.3727 | 18.4978 | 18.6195 | 18.5477 | 18.5359 | 17.9918 | 18.0303 | 18.0351 | 18.0013 | 17.9183 | 17.8144 | 17.7151 | 17.6662 | 16.4707 | 15.4609 | 13.674
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 6.6346 | 6.6102 | 6.4612 | 6.4126 | 6.2567 | 5.4022 | 4.7765 | 4.2877 | 3.6609 | 2.608 | 2.0998 | 1.5072 | 0.58926 | 0 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 6.6346 | 6.5943 | 6.4466 | 6.3849 | 5.887 | 5.4084 | 4.4874 | 3.69 | 2.7454 | 1.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 6.6346 | 6.7175 | 6.8387 | 6.9259 | 6.8936 | 6.889 | 6.8459 | 6.7889 | 6.6794 | 6.4171 | 6.1249 | 5.82 | 5.5222 | 5.2373 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 6.6346 | 6.4441 | 6.2602 | 5.9971 | 5.5412 | 4.3877 | 3.5263 | 2.617 | 1.7004 | 0.27546 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 6.6346 | 6.7563 | 6.8337 | 6.8979 | 6.8759 | 6.8425 | 6.775 | 6.6473 | 6.4778 | 6.1876 | 5.5227 | 4.8728 | 4.0855 | 3.4715 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 6.7564 | 6.6266 | 6.3528 | 6.17 | 5.9412 | 5.6132 | 5.2035 | 5.0055 | 4.7013 | 4.5413 | 4.628 | 5.0048 | 5.3915 | 5.8327 | 3.9363 | 2.3511 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 6.7564 | 6.6084 | 6.3368 | 6.1368 | 5.5257 | 4.8696 | 4.0989 | 3.5038 | 2.7798 | 2.0484 | 1.5781 | 1.4079 | 1.3063 | 1.3127 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 6.7564 | 6.8041 | 6.8233 | 6.8019 | 6.6681 | 6.5123 | 6.3553 | 6.1663 | 5.9457 | 5.6329 | 5.3305 | 5.0181 | 4.7371 | 4.5194 | 1.5746 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 6.7564 | 6.4744 | 6.1768 | 5.7246 | 5.1408 | 4.462 | 3.7746 | 3.0578 | 2.4148 | 1.9168 | 1.6125 | 1.5478 | 1.6756 | 1.9094 | 0 | 0 | 0
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 6.7564 | 6.813 | 6.8231 | 6.7711 | 6.6654 | 6.5031 | 6.3189 | 6.0952 | 5.8125 | 5.5817 | 5.335 | 5.1798 | 5.1679 | 5.356 | 2.8509 | 2.1667 | 0.6663
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.5095 | 7.958 | 7.9512 | 7.7794 | 7.4963 | 7.4299 | 7.1446 | 6.611 | 5.445 | 3.7317 | 2.5707 | 1.497 | 0.58528 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.5095 | 7.9767 | 7.9533 | 7.817 | 7.4001 | 7.2162 | 6.806 | 5.6027 | 3.8525 | 1.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.5095 | 8.1973 | 8.2998 | 8.2621 | 8.1204 | 8.1529 | 8.0432 | 7.7463 | 7.3757 | 6.8727 | 6.2906 | 5.6571 | 5.0853 | 4.5234 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.5095 | 7.8913 | 7.8645 | 7.5899 | 7.191 | 6.9948 | 5.8962 | 4.2516 | 2.6107 | 0.37422 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.5095 | 8.0672 | 8.177 | 8.1156 | 7.9202 | 7.9294 | 7.7647 | 7.2729 | 6.6565 | 5.9792 | 5.1306 | 4.3301 | 3.9654 | 3.4481 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.5655 | 9.3641 | 8.9998 | 8.7396 | 8.3646 | 7.8988 | 7.3104 | 6.906 | 5.9494 | 5.4345 | 5.197 | 5.3035 | 5.4814 | 5.8135 | 2.3737 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.5655 | 9.3128 | 8.9122 | 8.5913 | 7.8128 | 7.0092 | 6.04 | 5.1655 | 3.7198 | 2.3844 | 1.3438 | 0.65055 | 0.068417 | 0 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.5655 | 9.5113 | 9.4498 | 9.3456 | 9.1259 | 8.8602 | 8.5819 | 8.2599 | 7.6918 | 7.0989 | 6.5008 | 5.9063 | 5.3662 | 4.9156 | 0.56528 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.5655 | 9.143 | 8.7203 | 8.1331 | 7.3584 | 6.4735 | 5.516 | 4.4707 | 3.0575 | 2.0181 | 1.176 | 0.68243 | 0.51588 | 0.53616 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.5655 | 9.4804 | 9.3541 | 9.2096 | 8.9508 | 8.6348 | 8.2509 | 7.5585 | 6.6085 | 6.0544 | 5.4461 | 4.3735 | 4.0241 | 4.0357 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.8892 | 5.0943 | 3.3862 | 2.4571 | 1.2281 | 0.0075079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.8892 | 4.9967 | 3.2374 | 2.1366 | 0.22021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.8892 | 5.5881 | 4.919 | 4.362 | 3.7415 | 3.2317 | 2.3959 | 1.7377 | 1.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.8892 | 4.6247 | 2.8818 | 1.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.8892 | 5.4674 | 4.4593 | 3.7426 | 3.008 | 2.3999 | 1.3197 | 0.49871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 33.5364 | 33.4328 | 33.1618 | 33.0072 | 32.2874 | 31.8371 | 30.9028 | 30.1927 | 29.3444 | 27.9069 | 27.1707 | 26.7861 | 26.03 | 25.3848 | 18.7448 | 15.3569 | 13.739
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 33.5364 | 33.4169 | 33.1553 | 32.96 | 31.9802 | 31.335 | 30.1764 | 29.1969 | 28.0616 | 26.1637 | 24.9795 | 24.158 | 22.9959 | 21.998 | 13.6564 | 10.0705 | 9.2649
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 33.5364 | 33.6378 | 33.7016 | 33.7191 | 33.356 | 33.2411 | 33.1174 | 32.9371 | 32.734 | 32.3166 | 31.8995 | 31.4725 | 31.0229 | 30.65 | 25.5093 | 20.6632 | 16.9344
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 33.5364 | 33.2494 | 32.931 | 32.4396 | 31.4512 | 30.0648 | 28.9896 | 27.8312 | 26.7278 | 25.137 | 24.0919 | 22.9499 | 22.0632 | 21.3621 | 15.031 | 12.6397 | 11.2701
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 33.5364 | 33.6403 | 33.668 | 33.6356 | 33.1982 | 33.0484 | 32.8635 | 32.6105 | 32.3131 | 31.9202 | 31.1557 | 30.4344 | 29.8728 | 29.544 | 23.8752 | 21.7774 | 19.9393
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 5.8864 | 1.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 5.8864 | 1.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 5.8864 | 4.3656 | 0.93072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 5.8864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 5.8864 | 3.7548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.7898 | 2.2316 | 0.92047 | 0.28051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.7898 | 2.131 | 0.75515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.7898 | 2.5152 | 1.9161 | 1.4753 | 1.1014 | 0.74056 | 0.096474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.7898 | 1.8816 | 0.52465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.7898 | 2.4258 | 1.5471 | 1.0327 | 0.62821 | 0.23289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.7156 | 10.684 | 10.4582 | 10.284 | 9.9848 | 9.6193 | 9.166 | 8.8778 | 8.4778 | 7.9837 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.7156 | 10.6752 | 10.4382 | 10.2253 | 9.8297 | 9.4161 | 8.886 | 8.4867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.7156 | 10.8544 | 10.9236 | 10.9033 | 10.8542 | 10.82 | 10.7563 | 10.6422 | 10.5086 | 10.3036 | 10.0655 | 9.8173 | 9.5857 | 9.4075 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.7156 | 10.5228 | 10.2212 | 9.7392 | 9.3671 | 8.9548 | 8.5121 | 8.0186 | 7.5666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.7156 | 10.8804 | 10.9303 | 10.8564 | 10.8847 | 10.8872 | 10.8375 | 10.7262 | 10.572 | 10.4107 | 10.2103 | 10.0421 | 9.9803 | 10.0719 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0699 | 14.9319 | 14.73 | 14.5558 | 14.2619 | 13.9425 | 13.5493 | 13.2799 | 13.0247 | 12.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0699 | 14.929 | 14.729 | 14.5322 | 14.1706 | 13.8095 | 13.3581 | 12.9857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0699 | 15.026 | 14.9791 | 14.8931 | 14.7699 | 14.6467 | 14.4971 | 14.3862 | 14.2711 | 14.1054 | 13.9427 | 13.771 | 13.6184 | 13.4917 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0699 | 14.8713 | 14.6523 | 14.3223 | 13.9427 | 13.545 | 13.09 | 12.4422 | 9.7115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0699 | 15.0107 | 14.9323 | 14.7931 | 14.6423 | 14.4818 | 14.2855 | 14.1143 | 13.9479 | 13.8233 | 13.6879 | 13.5819 | 13.558 | 13.6152 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.9401 | 20.2961 | 19.3364 | 18.4098 | 17.2497 | 16.0241 | 14.7514 | 13.6948 | 12.5136 | 11.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.9401 | 20.2763 | 19.2879 | 18.27 | 16.8978 | 15.5524 | 14.1041 | 12.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.9401 | 20.5225 | 19.9786 | 19.3182 | 18.6438 | 18.0159 | 17.4296 | 16.8801 | 16.3387 | 15.6556 | 14.9879 | 14.2952 | 13.7288 | 13.2574 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.9401 | 20.042 | 18.91 | 17.4851 | 16.0093 | 14.509 | 13.1138 | 11.8285 | 9.7481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.9401 | 20.4345 | 19.6854 | 18.7719 | 17.9167 | 17.1257 | 16.3853 | 15.6715 | 14.9454 | 14.1743 | 13.3065 | 12.5169 | 11.9826 | 11.8477 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.953 | 13.6921 | 13.4404 | 13.2614 | 12.7094 | 12.4106 | 12.1869 | 11.9965 | 11.7019 | 11.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.953 | 13.6914 | 13.4252 | 13.192 | 12.5685 | 12.2236 | 11.9355 | 11.6642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.953 | 13.7857 | 13.6331 | 13.4884 | 13.192 | 13.0153 | 12.935 | 12.8104 | 12.6644 | 12.4675 | 12.2662 | 12.0416 | 11.8057 | 11.3924 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.953 | 13.6546 | 13.3167 | 12.9529 | 12.3369 | 11.8973 | 11.6493 | 11.2933 | 9.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.953 | 13.7187 | 13.4835 | 13.3198 | 12.8802 | 12.5333 | 12.4391 | 12.2061 | 11.9886 | 11.78 | 11.5449 | 11.0461 | 10.8063 | 10.6607 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.1473 | 2.1732 | 2.1746 | 2.2022 | 2.1677 | 2.1252 | 2.0625 | 2.026 | 1.967 | 1.9011 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.1473 | 2.1286 | 2.0948 | 2.0748 | 2.0019 | 1.9312 | 1.8362 | 1.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.1473 | 2.1974 | 2.225 | 2.2571 | 2.2327 | 2.2213 | 2.2092 | 2.1888 | 2.1629 | 2.1045 | 2.0458 | 1.9747 | 1.9106 | 1.8625 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.1473 | 2.1003 | 2.0578 | 1.9983 | 1.9463 | 1.8671 | 1.7797 | 1.6641 | 1.5048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.1473 | 2.1847 | 2.2045 | 2.2146 | 2.1998 | 1.9577 | 1.9429 | 1.8937 | 1.8033 | 1.1448 | 1.061 | 0.98122 | 0.91949 | 0.90207 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.1781 | 5.1596 | 5.1061 | 5.0893 | 5.025 | 4.9516 | 4.8632 | 4.7708 | 4.6569 | 4.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.1781 | 5.1526 | 5.0949 | 5.0635 | 4.9748 | 4.889 | 4.7801 | 4.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.1781 | 5.1989 | 5.2193 | 5.2513 | 5.2469 | 5.2475 | 5.2379 | 5.2009 | 5.1522 | 5.0774 | 4.9802 | 4.9088 | 4.837 | 4.7764 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.1781 | 5.1148 | 5.0498 | 4.9699 | 4.8875 | 4.7981 | 4.699 | 4.5599 | 4.3788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.1781 | 5.2021 | 5.2237 | 5.2449 | 5.2517 | 5.2491 | 5.2404 | 5.1779 | 5.0752 | 4.9947 | 4.8808 | 4.8333 | 4.8198 | 4.8599 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.5571 | 8.1137 | 6.7982 | 5.7676 | 4.6876 | 4.3727 | 3.9947 | 3.7278 | 3.5244 | 3.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.5571 | 8.2834 | 6.9739 | 6.1508 | 5.0547 | 4.7458 | 4.3126 | 4.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.5571 | 8.5924 | 7.7312 | 7.0562 | 6.3556 | 6.1846 | 5.9401 | 5.7569 | 5.5752 | 5.352 | 5.1576 | 4.9651 | 4.8098 | 4.7502 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.5571 | 8.1137 | 6.7982 | 5.7676 | 4.6876 | 4.3727 | 3.9947 | 3.7107 | 3.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.5571 | 8.3386 | 7.1425 | 6.3735 | 5.4639 | 5.3416 | 5.1536 | 5.0548 | 4.9053 | 4.7931 | 4.6908 | 4.6314 | 4.6365 | 4.7503 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.3891 | 23.3999 | 23.2726 | 23.1157 | 22.6912 | 22.2428 | 21.7365 | 21.3131 | 20.7783 | 17.5864 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.3891 | 23.3769 | 23.2415 | 23.03 | 22.5073 | 22.0362 | 21.4695 | 21.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.3891 | 23.4958 | 23.6058 | 23.5989 | 23.4818 | 23.3832 | 23.3125 | 23.1645 | 23.0311 | 22.8891 | 22.5533 | 22.2961 | 22.0814 | 21.8818 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.3891 | 23.1791 | 22.9253 | 22.4612 | 21.9687 | 21.4585 | 20.987 | 20.4258 | 9.7196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.3891 | 23.5536 | 23.6852 | 23.6287 | 23.5167 | 23.4296 | 23.3615 | 23.2025 | 23.0693 | 22.8876 | 22.3805 | 22.0082 | 21.7818 | 13.6266 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.905 | 16.142 | 14.6163 | 13.491 | 12.1351 | 10.4362 | 9.2629 | 7.9749 | 6.7788 | 5.1316 | 4.0341 | 2.7167 | 1.582 | 0.52968 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.905 | 16.3721 | 14.9927 | 14.2254 | 12.9371 | 12.0544 | 10.8098 | 9.6007 | 8.2732 | 6.181 | 4.7242 | 3.5799 | 2.2481 | 1.0463 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.905 | 16.6213 | 15.8746 | 15.481 | 14.7963 | 14.3976 | 14.0915 | 13.6558 | 13.1929 | 12.5679 | 11.9657 | 11.3046 | 10.6301 | 9.9964 | 4.335 | 0.12079 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.905 | 16.142 | 14.6163 | 13.491 | 12.1351 | 10.4362 | 9.2629 | 7.98 | 6.7677 | 5.1144 | 3.9996 | 2.6629 | 1.5068 | 0.43407 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.905 | 16.5787 | 15.5117 | 14.8977 | 14.058 | 13.6178 | 13.2975 | 12.7667 | 12.2095 | 11.5389 | 10.3937 | 9.347 | 8.5715 | 8.0139 | 2.5015 | 0.87881 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.9118 | 9.5227 | 8.4778 | 7.568 | 6.5455 | 5.447 | 3.7844 | 2.6719 | 1.4331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.9118 | 9.4957 | 8.43 | 7.4368 | 6.2487 | 5.0476 | 3.2424 | 1.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.9118 | 9.7247 | 9.167 | 8.4978 | 7.8577 | 7.2884 | 6.4854 | 5.9301 | 5.3865 | 4.7324 | 4.1623 | 3.5926 | 3.0266 | 2.5607 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.9118 | 9.3278 | 8.2022 | 6.8243 | 5.4902 | 3.8149 | 2.007 | 0.60632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.9118 | 9.6657 | 8.8835 | 8.0262 | 7.2429 | 6.5339 | 5.3031 | 4.6364 | 3.8926 | 2.7325 | 1.9368 | 1.276 | 0.73672 | 0.42623 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.3374 | 10.1798 | 9.7787 | 8.8872 | 7.852 | 6.7774 | 5.7247 | 4.7595 | 3.6366 | 2.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.3374 | 10.1953 | 9.7828 | 9.0309 | 8.0604 | 7.3081 | 6.3375 | 5.4019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.3374 | 10.249 | 9.9945 | 9.3601 | 8.6969 | 8.0127 | 7.3123 | 6.7378 | 6.0084 | 5.3162 | 4.8319 | 4.4581 | 4.0927 | 3.7817 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.3374 | 10.1798 | 9.7787 | 8.8872 | 7.852 | 6.7774 | 5.7247 | 4.7645 | 3.6526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.3374 | 10.1907 | 9.8108 | 9.0595 | 8.1268 | 7.4263 | 6.5695 | 5.7695 | 4.6866 | 3.8049 | 3.2516 | 3.0647 | 2.879 | 2.7526 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.329 | 7.9639 | 7.5468 | 7.1005 | 5.6075 | 2.4356 | 0.039235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.329 | 8.0943 | 7.7651 | 7.4929 | 6.0446 | 3.7574 | 1.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.329 | 8.2408 | 8.1365 | 8.0279 | 7.1268 | 5.2052 | 3.7166 | 2.8127 | 1.8084 | 0.1487 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.329 | 7.9639 | 7.5468 | 7.1005 | 5.6075 | 2.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.329 | 8.2167 | 8.0579 | 7.8672 | 6.6643 | 4.4458 | 2.5865 | 1.3404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 74.3026 | 72.5099 | 70.4463 | 67.7768 | 63.5455 | 56.8922 | 51.5159 | 46.7415 | 39.2316 | 10.3651 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 74.3026 | 72.9849 | 71.0889 | 69.2218 | 65.169 | 61.001 | 44.8355 | 17.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 74.3026 | 73.6087 | 72.7104 | 71.4278 | 69.0028 | 65.9275 | 63.2369 | 61.123 | 58.6463 | 55.2843 | 52.0387 | 48.6981 | 45.1913 | 42.2351 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 74.3026 | 72.5078 | 70.4477 | 67.7721 | 63.5399 | 56.635 | 51.257 | 37.5392 | 5.7285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 74.3026 | 73.348 | 72.009 | 70.4291 | 67.2363 | 63.726 | 60.3965 | 57.5071 | 53.9767 | 49.2391 | 43.5381 | 31.2724 | 16.8769 | 8.0312 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.1268 | 0.89637 | 0.60191 | 0.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.1268 | 0.87751 | 0.53347 | 0.29469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.1268 | 1.0642 | 1.0171 | 0.96959 | 0.81691 | 0.66822 | 0.48957 | 0.28136 | 0.015445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.1268 | 0.75329 | 0.38727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.1268 | 1.0516 | 0.95231 | 0.85938 | 0.67289 | 0.25628 | 0.021141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.175 | 10.796 | 9.8469 | 8.7544 | 7.4529 | 6.4113 | 5.3337 | 4.3779 | 3.5725 | 3.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.175 | 10.8759 | 9.9382 | 9.0317 | 7.6525 | 6.6108 | 5.3957 | 4.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.175 | 11.0798 | 10.6657 | 10.0568 | 9.3024 | 8.7618 | 8.2306 | 7.7355 | 7.2891 | 6.7595 | 6.2521 | 5.7477 | 5.2665 | 4.8613 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.175 | 10.6946 | 9.6517 | 8.3735 | 6.9462 | 5.7391 | 4.562 | 2.809 | 0.78887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.175 | 11.0524 | 10.3935 | 9.6205 | 8.6659 | 7.8085 | 7.1747 | 6.5204 | 5.8579 | 4.7719 | 4.2495 | 3.8447 | 3.5859 | 3.5965 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.1452 | 0.91104 | 0.61176 | 0.36782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.1452 | 0.89187 | 0.5422 | 0.29951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.1452 | 1.0816 | 1.0337 | 0.98545 | 0.83028 | 0.67915 | 0.49758 | 0.28596 | 0.015698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.1452 | 0.76561 | 0.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.1452 | 1.0688 | 0.96789 | 0.87344 | 0.6839 | 0.26047 | 0.021487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.1526 | 8.2684 | 8.3772 | 8.4673 | 8.4429 | 7.6409 | 7.1466 | 6.4567 | 5.7224 | 4.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.1526 | 8.2741 | 8.3823 | 8.4982 | 8.5142 | 8.421 | 7.9439 | 7.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.1526 | 8.2847 | 8.4119 | 8.5373 | 8.577 | 8.5849 | 8.5762 | 8.4563 | 8.3131 | 8.1512 | 7.9504 | 7.7295 | 7.468 | 7.1848 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.1526 | 8.2684 | 8.3772 | 8.4673 | 8.4429 | 7.6409 | 7.1466 | 6.45 | 5.6316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.1526 | 8.2882 | 8.4131 | 8.5294 | 8.5554 | 8.5116 | 8.4518 | 8.234 | 7.9525 | 7.6255 | 6.8761 | 6.1299 | 5.429 | 4.7793 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.6144 | 6.7525 | 4.5999 | 2.9872 | 0.82743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.6144 | 6.7204 | 4.5374 | 2.8521 | 0.54248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.6144 | 7.2984 | 5.9306 | 4.5306 | 2.9731 | 0.68753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.6144 | 6.4604 | 4.2691 | 2.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.6144 | 6.9439 | 5.0397 | 3.5175 | 1.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.6138 | 13.6517 | 13.5617 | 13.533 | 13.4322 | 13.3682 | 13.2308 | 12.5277 | 11.5934 | 10.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.6138 | 13.6463 | 13.5538 | 13.5083 | 13.3819 | 13.2945 | 13.1147 | 12.3385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.6138 | 13.6829 | 13.6729 | 13.6609 | 13.607 | 13.5904 | 13.5375 | 13.1569 | 12.6454 | 12.0536 | 11.5654 | 11.0277 | 10.4651 | 10.0253 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.6138 | 13.6271 | 13.5358 | 13.4436 | 13.3065 | 13.1965 | 13.0002 | 12.1783 | 5.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.6138 | 13.6696 | 13.6196 | 13.5964 | 13.5137 | 13.4835 | 13.3982 | 12.7288 | 11.8546 | 10.9975 | 10.3705 | 9.7837 | 9.3493 | 7.8253 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.6556 | 6.6239 | 6.5727 | 6.5438 | 6.4565 | 6.3405 | 6.2022 | 6.1111 | 5.9966 | 5.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.6556 | 6.6134 | 6.5274 | 6.4693 | 6.3372 | 6.1704 | 5.9702 | 5.7812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.6556 | 6.6709 | 6.6805 | 6.682 | 6.6167 | 6.5532 | 6.4954 | 6.4276 | 6.3674 | 6.2404 | 6.1036 | 5.9802 | 5.8289 | 5.6956 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.6556 | 6.5743 | 6.4908 | 6.3734 | 6.2324 | 6.0565 | 5.8464 | 5.6235 | 5.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.6556 | 6.6491 | 6.6298 | 6.612 | 6.5329 | 6.4459 | 6.3573 | 6.2594 | 6.1282 | 5.9936 | 5.8468 | 5.7098 | 5.5956 | 5.5342 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.7249 | 9.0243 | 8.0824 | 7.1854 | 6.1025 | 5.1703 | 4.1613 | 3.3293 | 2.52 | 2.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.7249 | 8.9966 | 8.0001 | 7.1035 | 5.8192 | 4.7485 | 3.4988 | 2.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.7249 | 9.3164 | 8.7952 | 8.187 | 7.479 | 6.8702 | 6.2942 | 5.7607 | 5.2609 | 4.7383 | 4.242 | 3.7352 | 3.2314 | 2.8127 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.7249 | 8.8106 | 7.7266 | 6.4669 | 5.1474 | 3.87 | 2.6579 | 1.5089 | 0.42376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.7249 | 9.1992 | 8.4759 | 7.7134 | 6.8301 | 6.0261 | 5.3442 | 4.6642 | 3.9515 | 3.1847 | 2.6935 | 2.2908 | 2.0205 | 2.0128 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.9177 | 0.38811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.9177 | 0.77145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.9177 | 1.2747 | 0.6785 | 0.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.9177 | 0.38811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.9177 | 1.1183 | 0.20877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.6283 | 19.6305 | 19.622 | 19.6101 | 19.5785 | 19.5327 | 19.4768 | 19.4443 | 19.3995 | 19.3588 | 19.3254 | 19.3264 | 19.3286 | 19.3307 | 19.0685 | 18.8463 | 18.0098
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.6283 | 19.6088 | 19.5757 | 19.5481 | 19.4859 | 19.439 | 19.3562 | 19.2906 | 19.1941 | 19.1186 | 19.0461 | 18.9876 | 18.9299 | 18.8775 | 15.5596 | 7.6851 | 5.7704
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.6283 | 19.6363 | 19.6452 | 19.6492 | 19.6384 | 19.623 | 19.6134 | 19.5947 | 19.5655 | 19.5363 | 19.4854 | 19.4328 | 19.3879 | 19.335 | 18.8989 | 18.5974 | 15.6244
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.6283 | 19.5992 | 19.5748 | 19.5257 | 19.4724 | 19.4053 | 19.335 | 19.2395 | 19.1101 | 19.0512 | 18.9725 | 18.9198 | 18.8817 | 18.8484 | 18.3029 | 15.7046 | 13.2708
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.6283 | 19.634 | 19.6359 | 19.6345 | 19.6222 | 19.6139 | 19.5876 | 19.5477 | 19.4761 | 19.4246 | 19.3649 | 19.3033 | 19.2562 | 19.2239 | 18.7872 | 18.6468 | 18.3601
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.1123 | 15.9367 | 14.7765 | 13.5812 | 12.1298 | 10.4861 | 9.2086 | 7.8409 | 6.4558 | 4.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.1123 | 16.2165 | 15.1386 | 14.346 | 12.9328 | 12.0857 | 10.8056 | 9.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.1123 | 16.5671 | 16.0033 | 15.4485 | 14.6828 | 14.3306 | 14.0025 | 13.6324 | 13.1894 | 12.5589 | 12.0468 | 11.5446 | 11.0851 | 10.7464 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.1123 | 15.9347 | 14.7778 | 13.5767 | 12.1244 | 10.4792 | 9.201 | 7.8156 | 5.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.1123 | 16.4058 | 15.6027 | 14.978 | 14.0471 | 13.6723 | 13.3059 | 12.8773 | 12.346 | 11.7138 | 10.8618 | 10.145 | 9.5881 | 7.9125 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.2984 | 9.1565 | 9.0134 | 8.6787 | 8.5207 | 8.2983 | 8.1124 | 8.0098 | 7.8373 | 7.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.2984 | 9.1018 | 8.9115 | 8.5088 | 8.1945 | 7.8385 | 7.5159 | 7.2693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.2984 | 9.205 | 9.1433 | 8.8588 | 8.7506 | 8.607 | 8.531 | 8.4609 | 8.3871 | 8.2239 | 8.0626 | 7.8888 | 7.7017 | 7.555 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.2984 | 9.0134 | 8.7913 | 8.255 | 7.9347 | 7.5113 | 7.2214 | 6.8268 | 4.5945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.2984 | 9.1686 | 9.0619 | 8.7108 | 8.5802 | 8.4119 | 8.3346 | 8.2257 | 8.0723 | 7.9373 | 7.7909 | 6.7989 | 4.9919 | 4.1959 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.0423 | 11.9665 | 11.3737 | 10.9472 | 10.4245 | 9.0873 | 7.9281 | 6.7932 | 5.7728 | 4.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.0423 | 12.1486 | 11.5977 | 11.3896 | 10.8575 | 10.3179 | 9.1281 | 8.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.0423 | 12.4613 | 12.2023 | 12.1425 | 11.9311 | 11.6811 | 11.31 | 10.9862 | 10.6702 | 10.2487 | 9.8071 | 9.4026 | 9.0035 | 8.3094 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.0423 | 11.9665 | 11.3737 | 10.9472 | 10.4245 | 9.0873 | 7.9281 | 6.7789 | 3.9697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.0423 | 12.3047 | 11.9627 | 11.8819 | 11.6658 | 11.409 | 10.9486 | 10.4945 | 9.711 | 8.5667 | 7.6994 | 7.0418 | 6.461 | 5.5653 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 70.6856 | 67.337 | 64.7623 | 62.244 | 59.661 | 55.829 | 52.2884 | 45.6731 | 27.0983 | 7.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 70.6856 | 68.0496 | 59.8597 | 51.8452 | 41.3059 | 38.4725 | 30.9691 | 11.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 70.6856 | 69.166 | 68.1268 | 67.3355 | 66.1644 | 65.242 | 64.0281 | 62.8878 | 61.6839 | 60.2308 | 58.8041 | 55.0052 | 44.3234 | 34.2887 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 70.6856 | 67.337 | 64.7642 | 62.2435 | 59.6597 | 55.8269 | 47.4404 | 25.9294 | 3.9568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 70.6856 | 68.7271 | 67.2377 | 66.2115 | 64.881 | 63.545 | 62.1494 | 60.3488 | 57.937 | 49.0207 | 34.196 | 21.6007 | 11.6573 | 5.5474 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 64.4836 | 61.1969 | 57.2751 | 53.2096 | 47.8811 | 42.2866 | 36.8219 | 31.1677 | 18.1494 | 2.3435 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 64.4836 | 61.8152 | 52.4898 | 43.3858 | 30.5554 | 25.5587 | 19.5964 | 6.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 64.4836 | 62.9252 | 60.9653 | 58.9557 | 56.3498 | 54.039 | 51.4214 | 49.1621 | 46.6796 | 43.6672 | 40.7935 | 37.9033 | 35.1191 | 31.2943 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 64.4836 | 61.0802 | 57.0919 | 52.6704 | 47.1446 | 41.1259 | 29.7234 | 15.2087 | 0.63517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 64.4836 | 62.4777 | 59.6257 | 57.3003 | 53.881 | 50.9402 | 47.8145 | 44.5566 | 40.8188 | 36.2095 | 29.5036 | 22.5604 | 16.8254 | 9.3136 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.7311 | 17.0668 | 16.2062 | 15.5034 | 14.768 | 14.0455 | 13.303 | 12.6761 | 11.9823 | 2.2802 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.7311 | 17.1285 | 16.2166 | 15.6581 | 14.9467 | 14.4443 | 13.7419 | 6.2443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.7311 | 17.2912 | 16.6991 | 16.1895 | 15.6984 | 15.2151 | 14.6766 | 14.2637 | 13.7293 | 13.1847 | 12.7794 | 12.4163 | 12.0755 | 11.8118 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.7311 | 17.0668 | 16.2062 | 15.5034 | 14.768 | 14.0455 | 13.303 | 12.6771 | 0.61802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.7311 | 17.1541 | 16.3083 | 15.7851 | 15.1556 | 14.7273 | 14.1075 | 13.5508 | 12.8187 | 12.2238 | 11.9746 | 11.8281 | 11.7144 | 9.1982 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.4168 | 12.1097 | 11.7224 | 11.4812 | 11.161 | 10.8508 | 10.4383 | 10.1337 | 9.7577 | 9.4961 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.4168 | 12.0373 | 11.5852 | 11.2478 | 10.7425 | 10.2909 | 9.7335 | 9.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.4168 | 12.2086 | 12.001 | 11.8055 | 11.5668 | 11.3523 | 11.1263 | 10.8784 | 10.6323 | 10.3281 | 10.039 | 9.7161 | 9.4042 | 9.1341 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.4168 | 11.9281 | 11.4567 | 10.9332 | 10.4213 | 9.8981 | 9.3932 | 8.8138 | 5.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.4168 | 12.1528 | 11.8638 | 11.6206 | 11.3329 | 10.84 | 10.5759 | 10.2375 | 9.2806 | 9.0498 | 8.7923 | 8.559 | 8.3852 | 7.7715 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 85.2672 | 76.6394 | 74.0114 | 72.2665 | 69.8584 | 67.852 | 64.9945 | 62.643 | 39.5036 | 10.4369 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 85.2672 | 76.3986 | 73.5486 | 71.4802 | 68.5262 | 66.0868 | 45.1463 | 17.3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 85.2672 | 78.7578 | 77.0339 | 75.3915 | 73.4694 | 71.6111 | 69.7811 | 68.0472 | 66.1772 | 64.1825 | 62.5587 | 60.8641 | 59.4596 | 49.9856 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 85.2672 | 75.6153 | 72.7245 | 69.8958 | 67.0685 | 63.4001 | 60.2373 | 37.7995 | 5.7682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 85.2672 | 76.8195 | 74.5482 | 72.7976 | 70.5608 | 68.0855 | 66.0904 | 64.081 | 61.0676 | 58.1037 | 49.8505 | 31.4892 | 16.9939 | 8.0869 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.4329 | 7.9652 | 6.9655 | 6.0654 | 4.8891 | 3.688 | 1.8724 | 0.62369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.4329 | 7.938 | 6.9151 | 5.9278 | 4.552 | 3.226 | 1.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.4329 | 8.2005 | 7.6933 | 7.0626 | 6.3568 | 5.7897 | 5.0523 | 4.5349 | 4.0222 | 3.3665 | 2.7645 | 2.1628 | 1.5724 | 1.0797 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.4329 | 7.7267 | 6.615 | 5.1901 | 3.6667 | 1.5281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.4329 | 8.1463 | 7.44 | 6.6025 | 5.7408 | 5.0168 | 3.9427 | 3.3287 | 2.6274 | 1.6515 | 0.6542 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.1584 | 3.9087 | 3.7308 | 3.5237 | 2.8468 | 2.0858 | 1.8448 | 1.5775 | 1.2833 | 0.96682 | 0.73721 | 0.58726 | 0.5221 | 0.52953 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.1584 | 3.9906 | 3.825 | 3.7266 | 3.0522 | 2.474 | 2.1722 | 1.9426 | 1.6019 | 1.1339 | 0.81063 | 0.59553 | 0.36316 | 0.23234 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.1584 | 4.1108 | 4.1155 | 4.1199 | 3.7479 | 3.3267 | 3.2368 | 3.136 | 3.0022 | 2.8417 | 2.6697 | 2.4974 | 2.3091 | 2.1399 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.1584 | 3.9087 | 3.7308 | 3.5237 | 2.8468 | 2.0858 | 1.8448 | 1.5834 | 1.2645 | 0.94011 | 0.69067 | 0.51791 | 0.42894 | 0.41158 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.1584 | 4.0892 | 4.0838 | 4.0612 | 3.5588 | 3.1469 | 3.0545 | 2.9373 | 2.763 | 2.5868 | 2.0589 | 1.5269 | 1.0317 | 0.64139 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.5431 | 1.4683 | 0.19451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.0766 | 6.7405 | 6.1749 | 5.8847 | 5.0365 | 4.1809 | 3.0413 | 2.0704 | 0.77476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.0766 | 6.6153 | 5.9356 | 5.478 | 4.2591 | 3.0677 | 1.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.0766 | 6.8853 | 6.6173 | 6.4085 | 5.812 | 5.1695 | 4.6871 | 4.1514 | 3.483 | 2.6305 | 1.8441 | 0.47949 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.0766 | 6.4302 | 5.7078 | 4.9468 | 3.6909 | 1.5483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.0766 | 6.789 | 6.3836 | 6.0617 | 5.0106 | 4.2485 | 3.3128 | 2.5697 | 1.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 17.6694 | 17.2291 | 16.5694 | 15.9834 | 15.0371 | 14.0178 | 12.7594 | 11.7406 | 10.337 | 8.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 17.6694 | 17.0577 | 16.2438 | 15.4317 | 13.9775 | 12.5024 | 10.6893 | 8.9927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 17.6694 | 17.4128 | 17.1142 | 16.655 | 15.9982 | 15.2616 | 14.7416 | 14.1756 | 13.4779 | 12.5142 | 11.6131 | 10.1401 | 9.2049 | 8.2658 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 17.6694 | 16.7969 | 15.9108 | 14.6788 | 13.1802 | 10.7214 | 8.9433 | 7.0402 | 4.7381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 17.6694 | 17.2867 | 16.8142 | 16.1826 | 15.0705 | 14.1936 | 13.2375 | 12.4321 | 11.2378 | 9.5857 | 8.2697 | 7.0115 | 5.148 | 4.3271 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.6065 | 22.3044 | 21.9621 | 21.7333 | 21.416 | 21.0551 | 20.6303 | 20.1662 | 19.5407 | 17.5864 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.6065 | 22.285 | 21.9212 | 21.6416 | 21.2418 | 20.8528 | 20.3721 | 19.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.6065 | 22.4991 | 22.4497 | 22.375 | 22.2851 | 22.1974 | 22.0968 | 21.8918 | 21.621 | 21.2627 | 20.9005 | 20.4891 | 20.1677 | 19.8753 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.6065 | 22.1424 | 21.7289 | 21.2531 | 20.8789 | 20.48 | 20.0682 | 19.4906 | 9.7196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.6065 | 22.46 | 22.3338 | 22.1848 | 22.1029 | 22.0355 | 21.9388 | 21.6536 | 21.275 | 20.851 | 20.3341 | 19.8268 | 19.6489 | 13.6266 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 76.6034 | 75.854 | 74.4756 | 73.2639 | 71.1288 | 68.8808 | 66.1544 | 63.7374 | 60.8888 | 18.1545 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 76.6034 | 75.7976 | 74.3851 | 72.9651 | 70.3838 | 67.9264 | 64.8453 | 30.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 76.6034 | 76.5423 | 76.3183 | 75.7632 | 74.8836 | 74.0968 | 73.2091 | 72.0483 | 70.8671 | 69.3786 | 67.6764 | 65.9462 | 64.3537 | 62.915 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 76.6034 | 75.1811 | 73.4704 | 70.9822 | 68.3548 | 65.6592 | 62.844 | 59.2682 | 10.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 76.6034 | 76.5307 | 76.1283 | 75.2124 | 74.1676 | 73.0246 | 71.9501 | 70.3871 | 68.7173 | 67.1929 | 64.5284 | 54.7739 | 29.56 | 14.0667 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 76.6034 | 75.854 | 74.4756 | 73.2639 | 71.1288 | 68.8808 | 66.1544 | 63.7374 | 60.8888 | 18.1545 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 76.6034 | 75.7976 | 74.3851 | 72.9651 | 70.3838 | 67.9264 | 64.8453 | 30.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 76.6034 | 76.5423 | 76.3183 | 75.7632 | 74.8836 | 74.0968 | 73.2091 | 72.0483 | 70.8671 | 69.3786 | 67.6764 | 65.9462 | 64.3537 | 62.915 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 76.6034 | 75.1811 | 73.4704 | 70.9822 | 68.3548 | 65.6592 | 62.844 | 59.2682 | 10.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 76.6034 | 76.5307 | 76.1283 | 75.2124 | 74.1676 | 73.0246 | 71.9501 | 70.3871 | 68.7173 | 67.1929 | 64.5284 | 54.7739 | 29.56 | 14.0667 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 13.319 | 13.2698 | 13.1458 | 13.0919 | 12.8921 | 12.6559 | 12.3823 | 12.2022 | 11.9693 | 11.6252 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.319 | 13.2666 | 13.1421 | 13.0757 | 12.8126 | 12.5446 | 12.2222 | 11.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.319 | 13.372 | 13.4184 | 13.4696 | 13.4453 | 13.4205 | 13.3917 | 13.3392 | 13.2548 | 13.1054 | 12.9592 | 12.8099 | 12.6758 | 12.5658 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.319 | 13.1877 | 13.063 | 12.8665 | 12.6195 | 12.3345 | 12.0423 | 11.7011 | 9.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.319 | 13.3762 | 13.4213 | 13.4509 | 13.4465 | 13.4264 | 13.3688 | 13.2782 | 13.1703 | 13.0379 | 12.9 | 12.7926 | 12.7656 | 12.8815 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 48.7868 | 47.6152 | 45.8656 | 44.4584 | 42.0928 | 39.6542 | 36.9991 | 34.9434 | 32.4865 | 18.4082 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 48.7868 | 47.5497 | 45.7095 | 44.1516 | 41.244 | 38.5014 | 35.3873 | 30.5945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 48.7868 | 48.3218 | 47.7486 | 47.0692 | 45.9777 | 44.9957 | 44.0862 | 43.104 | 42.0097 | 40.4448 | 38.8602 | 37.2215 | 35.725 | 33.8945 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 48.7868 | 46.918 | 44.8658 | 42.2642 | 39.3185 | 36.322 | 33.4228 | 30.3498 | 10.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 48.7868 | 48.1922 | 47.2845 | 46.2227 | 44.8882 | 43.3673 | 42.1891 | 40.6495 | 39.06 | 37.4546 | 35.6705 | 33.4254 | 29.9731 | 14.2633 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 48.7868 | 47.6152 | 45.8656 | 44.4584 | 42.0928 | 39.6542 | 36.9991 | 34.9434 | 32.4865 | 18.4082 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 48.7868 | 47.5497 | 45.7095 | 44.1516 | 41.244 | 38.5014 | 35.3873 | 30.5945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 48.7868 | 48.3218 | 47.7486 | 47.0692 | 45.9777 | 44.9957 | 44.0862 | 43.104 | 42.0097 | 40.4448 | 38.8602 | 37.2215 | 35.725 | 33.8945 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 48.7868 | 46.918 | 44.8658 | 42.2642 | 39.3185 | 36.322 | 33.4228 | 30.3498 | 10.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 48.7868 | 48.1922 | 47.2845 | 46.2227 | 44.8882 | 43.3673 | 42.1891 | 40.6495 | 39.06 | 37.4546 | 35.6705 | 33.4254 | 29.9731 | 14.2633 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.1423 | 10.4556 | 9.7635 | 9.2606 | 8.4233 | 7.6917 | 6.7301 | 5.5549 | 4.8753 | 4.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.1423 | 10.4448 | 9.754 | 9.2184 | 8.2993 | 7.5231 | 6.4929 | 5.2548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.1423 | 10.6652 | 10.2835 | 9.8884 | 9.3961 | 8.9243 | 8.368 | 7.7068 | 7.288 | 6.7784 | 6.2783 | 5.747 | 5.243 | 4.7919 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.1423 | 10.2968 | 9.5418 | 8.7483 | 7.7844 | 6.8129 | 5.7334 | 4.374 | 3.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.1423 | 10.5637 | 10.0237 | 9.5779 | 8.9526 | 8.4852 | 7.8321 | 6.8581 | 6.4569 | 5.9768 | 5.5317 | 5.0917 | 4.7109 | 4.4717 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 67.1335 | 64.2062 | 60.3173 | 57.2716 | 52.9467 | 48.2108 | 42.2565 | 36.7767 | 31.2528 | 18.0225 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 67.1335 | 64.1272 | 60.177 | 56.9024 | 52.0614 | 47.024 | 40.6137 | 29.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 67.1335 | 65.3031 | 63.2072 | 60.8958 | 58.1971 | 54.9679 | 51.9 | 49.0182 | 46.2056 | 43.4901 | 40.9991 | 38.5872 | 36.3161 | 34.0443 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 67.1335 | 63.4003 | 59.24 | 54.5467 | 49.4308 | 41.7919 | 35.3012 | 28.7031 | 9.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 67.1335 | 64.829 | 61.8562 | 59.1149 | 55.8357 | 52.4453 | 48.6536 | 44.8201 | 40.8747 | 37.3443 | 34.3437 | 31.8939 | 29.3451 | 13.9645 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 67.1335 | 64.2062 | 60.3173 | 57.2716 | 52.9467 | 48.2108 | 42.2565 | 36.7767 | 31.2528 | 18.0225 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 67.1335 | 64.1272 | 60.177 | 56.9024 | 52.0614 | 47.024 | 40.6137 | 29.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 67.1335 | 65.3031 | 63.2072 | 60.8958 | 58.1971 | 54.9679 | 51.9 | 49.0182 | 46.2056 | 43.4901 | 40.9991 | 38.5872 | 36.3161 | 34.0443 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 67.1335 | 63.4003 | 59.24 | 54.5467 | 49.4308 | 41.7919 | 35.3012 | 28.7031 | 9.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 67.1335 | 64.829 | 61.8562 | 59.1149 | 55.8357 | 52.4453 | 48.6536 | 44.8201 | 40.8747 | 37.3443 | 34.3437 | 31.8939 | 29.3451 | 13.9645 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.73 | 6.2322 | 5.5893 | 5.1632 | 4.5277 | 3.9606 | 3.2822 | 2.7406 | 1.6957 | 1.1632 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.73 | 6.1987 | 5.5047 | 4.9855 | 4.2449 | 3.5976 | 2.4315 | 1.3775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.73 | 6.4414 | 6.1294 | 5.7943 | 5.3752 | 4.9851 | 4.575 | 4.1871 | 3.5718 | 3.1291 | 2.6843 | 2.2234 | 1.7859 | 1.4039 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.73 | 6.0826 | 5.4155 | 4.6913 | 3.9421 | 2.4695 | 1.3529 | 0.21626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.73 | 6.3243 | 5.8608 | 5.4612 | 4.9322 | 4.5098 | 3.8169 | 3.296 | 2.264 | 1.9365 | 0.67364 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 38.6563 | 38.1222 | 37.2349 | 36.7115 | 35.7513 | 34.8555 | 33.7065 | 32.2116 | 29.9009 | 10.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 38.6563 | 38.0625 | 37.0795 | 36.3853 | 35.1889 | 34.099 | 31.9256 | 17.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 38.6563 | 38.4955 | 38.1883 | 37.8481 | 37.2501 | 36.7225 | 36.1529 | 35.2271 | 33.9298 | 32.5817 | 31.3372 | 30.0358 | 28.7065 | 27.5813 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 38.6563 | 37.8484 | 36.8979 | 35.8231 | 34.6331 | 31.9333 | 29.8221 | 26.9578 | 5.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 38.6563 | 38.3222 | 37.7768 | 37.3159 | 36.5637 | 35.9634 | 34.7846 | 33.3277 | 31.0521 | 29.541 | 26.3814 | 24.4245 | 16.7574 | 7.9744 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.9908 | 17.8844 | 17.7568 | 17.544 | 17.2917 | 17.0118 | 16.4411 | 15.7212 | 15.035 | 10.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.9908 | 17.9326 | 17.8258 | 17.7149 | 17.4835 | 17.2331 | 16.6904 | 16.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.9908 | 17.9975 | 17.9807 | 17.9434 | 17.8606 | 17.7672 | 17.5063 | 17.1754 | 16.7887 | 16.2822 | 15.7302 | 15.2384 | 14.7301 | 14.2169 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.9908 | 17.8844 | 17.7568 | 17.544 | 17.2917 | 17.0118 | 16.4411 | 15.7222 | 5.6589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.9908 | 17.991 | 17.9724 | 17.9093 | 17.8133 | 17.7017 | 17.3523 | 16.8131 | 16.1721 | 15.4869 | 14.683 | 14.2164 | 13.9229 | 7.9337 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.3691 | 7.2914 | 7.2193 | 7.1589 | 7.1041 | 7.052 | 3.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.3691 | 7.2645 | 7.1596 | 7.064 | 6.9374 | 6.8413 | 1.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.3691 | 7.3126 | 7.2768 | 7.2276 | 7.185 | 7.1613 | 7.1315 | 7.1004 | 7.0466 | 3.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.3691 | 7.2385 | 7.1305 | 6.9883 | 6.8633 | 2.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.3691 | 7.2886 | 7.2277 | 7.1557 | 7.0983 | 7.0603 | 7.0152 | 3.4992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.6447 | 7.3672 | 7.1763 | 6.955 | 6.714 | 6.4627 | 6.2072 | 5.9274 | 5.6797 | 5.4809 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.6447 | 7.4335 | 7.233 | 7.0876 | 6.8438 | 6.6017 | 6.3062 | 6.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.6447 | 7.5505 | 7.502 | 7.4611 | 7.3462 | 7.2418 | 7.1316 | 6.9849 | 6.856 | 6.662 | 6.4881 | 6.2722 | 6.0634 | 5.88 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.6447 | 7.3672 | 7.1763 | 6.955 | 6.714 | 6.4627 | 6.2072 | 5.8988 | 4.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.6447 | 7.5059 | 7.4154 | 7.3314 | 7.1898 | 6.7985 | 6.6696 | 6.5024 | 6.2847 | 5.4391 | 5.2568 | 5.0669 | 4.8953 | 4.8081 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.5069 | 11.1542 | 10.8014 | 9.9898 | 9.4962 | 9.2119 | 8.9386 | 8.6341 | 8.3729 | 8.0927 | 7.8738 | 7.7261 | 7.6468 | 7.639 | 6.5321 | 6.1184 | 5.772
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.5069 | 11.2423 | 10.8836 | 10.268 | 9.787 | 9.5407 | 9.2477 | 9.0332 | 8.7311 | 8.2926 | 7.9747 | 7.7549 | 7.5331 | 7.3622 | 5.1489 | 4.0246 | 3.7364
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.5069 | 11.3708 | 11.2142 | 10.7093 | 10.4832 | 10.411 | 10.3466 | 10.2724 | 10.1905 | 10.0083 | 9.8331 | 9.6526 | 9.4629 | 9.331 | 7.5716 | 5.5405 | 3.9528
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.5069 | 11.1542 | 10.8014 | 9.9898 | 9.4962 | 9.2119 | 8.9386 | 8.6273 | 8.3434 | 8.0553 | 7.8206 | 7.6551 | 7.5549 | 7.5273 | 6.1807 | 5.588 | 4.9746
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.5069 | 11.3204 | 11.0769 | 10.5123 | 10.226 | 10.1666 | 10.108 | 10.0279 | 9.9062 | 9.775 | 9.6231 | 9.4905 | 9.3998 | 9.3936 | 7.0553 | 5.9662 | 5.193
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.9614 | 19.9306 | 19.8705 | 19.7858 | 19.6729 | 19.5748 | 19.4909 | 19.401 | 19.3393 | 17.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.9614 | 19.9306 | 19.8643 | 19.7709 | 19.6405 | 19.5307 | 19.4361 | 19.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.9614 | 19.9355 | 19.8863 | 19.8253 | 19.7494 | 19.7004 | 19.6577 | 19.6226 | 19.6125 | 19.6165 | 19.624 | 19.6291 | 19.6417 | 19.6556 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.9614 | 19.9139 | 19.8278 | 19.702 | 19.5438 | 19.4143 | 19.3199 | 19.237 | 9.8428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.9614 | 19.9306 | 19.8594 | 19.7619 | 19.6445 | 19.5653 | 19.5009 | 19.4433 | 19.4204 | 19.4259 | 19.4247 | 19.4353 | 19.447 | 13.7993 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.7102 | 15.598 | 15.4916 | 15.1599 | 14.6202 | 13.9811 | 13.2826 | 12.524 | 11.7654 | 2.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.7102 | 15.6589 | 15.5645 | 15.3861 | 14.9016 | 14.3551 | 13.6624 | 5.9625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.7102 | 15.7448 | 15.7651 | 15.668 | 15.4585 | 15.225 | 14.9632 | 14.6773 | 14.3669 | 13.9614 | 13.5456 | 13.1079 | 12.6619 | 12.2153 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.7102 | 15.598 | 15.4902 | 15.1586 | 14.6202 | 13.9811 | 13.2826 | 12.4949 | 0.59014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.7102 | 15.7344 | 15.7452 | 15.6217 | 15.3682 | 15.0421 | 14.6806 | 14.266 | 13.7992 | 13.3075 | 12.7332 | 12.1742 | 11.6385 | 9.0005 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Best View | Headroom (MW) | 17.2366 | 16.5448 | 16.0169 | 15.7587 | 15.5642 | 15.3542 | 15.1271 | 14.8871 | 14.6505 | 7.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.2366 | 16.6459 | 16.1276 | 15.9825 | 15.7751 | 15.5743 | 15.3144 | 11.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.2366 | 16.8386 | 16.5273 | 16.4447 | 16.3485 | 16.2595 | 16.1682 | 16.0606 | 15.949 | 15.8 | 15.6662 | 15.5188 | 15.3997 | 15.2776 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.2366 | 16.5448 | 16.0169 | 15.7587 | 15.5642 | 15.3542 | 15.1271 | 14.8758 | 3.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.2366 | 16.7322 | 16.3198 | 16.24 | 16.1737 | 16.0877 | 15.9944 | 15.8795 | 15.7389 | 15.6095 | 15.4771 | 15.3593 | 11.6257 | 5.5323 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.155 | 9.0885 | 8.9982 | 8.9519 | 8.8235 | 8.6803 | 8.4819 | 8.3508 | 8.1526 | 7.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.155 | 9.0816 | 8.9913 | 8.9298 | 8.7704 | 8.6079 | 8.382 | 8.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.155 | 9.1596 | 9.1528 | 9.1457 | 9.1001 | 9.0584 | 9.0114 | 8.9389 | 8.8717 | 8.7315 | 8.5938 | 8.4524 | 8.2969 | 8.1578 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.155 | 9.0461 | 8.9451 | 8.8062 | 8.6388 | 8.4567 | 8.2561 | 8.0062 | 7.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.155 | 9.1489 | 9.132 | 9.0976 | 9.0438 | 8.7756 | 8.7031 | 8.5953 | 8.4438 | 8.3207 | 7.6032 | 7.4788 | 7.368 | 7.3311 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.5159 | 20.0627 | 19.569 | 18.6051 | 17.6799 | 15.9805 | 14.4661 | 13.0192 | 11.6068 | 7.1789 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.5159 | 20.2911 | 14.1595 | 7.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.5159 | 20.553 | 20.5618 | 20.2822 | 19.9153 | 19.5443 | 19.0451 | 18.6174 | 18.1153 | 17.6412 | 17.1667 | 16.3223 | 15.5008 | 14.7334 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.5159 | 20.0627 | 19.571 | 18.6046 | 17.6786 | 15.9784 | 14.4628 | 13.0163 | 3.9676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.5159 | 20.5529 | 20.5236 | 20.137 | 19.7167 | 19.34 | 18.7646 | 17.8269 | 16.76 | 15.6671 | 14.8915 | 14.1682 | 11.6891 | 5.5625 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.1658 | 16.9358 | 16.6182 | 16.2427 | 15.7733 | 15.2288 | 14.6226 | 14.0305 | 13.4261 | 12.9392 | 12.5408 | 12.3 | 12.1504 | 12.0824 | 10.4483 | 9.5656 | 8.9989
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.1658 | 16.9598 | 16.6345 | 16.3109 | 15.8305 | 15.2845 | 14.6079 | 13.9256 | 13.1218 | 12.3577 | 11.7523 | 11.1793 | 10.658 | 10.2148 | 7.0643 | 4.5332 | 3.7533
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.1658 | 17.0304 | 16.8646 | 16.6734 | 16.4097 | 16.1268 | 15.8059 | 15.4816 | 15.1362 | 14.7849 | 14.4655 | 14.1276 | 13.7888 | 13.4739 | 10.8796 | 7.5729 | 4.4321
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.1658 | 16.8867 | 16.5312 | 16.0761 | 15.5304 | 14.8937 | 14.2114 | 13.4542 | 12.6565 | 12.0824 | 11.5974 | 11.2547 | 11.0516 | 10.9361 | 9.0523 | 8.1677 | 7.2034
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.1658 | 17.0082 | 16.7572 | 16.4695 | 16.1227 | 15.7457 | 15.3249 | 14.861 | 14.3639 | 13.9662 | 13.5468 | 13.1602 | 12.7814 | 12.526 | 9.1309 | 7.2775 | 6.361
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.004 | 13.8125 | 13.6614 | 13.463 | 13.2265 | 12.9612 | 12.6708 | 12.3399 | 12.0409 | 7.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.004 | 13.8854 | 13.7393 | 13.657 | 13.4087 | 13.1715 | 12.8368 | 11.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.004 | 14.0042 | 14.0175 | 14.0336 | 13.9752 | 13.9186 | 13.8654 | 13.7684 | 13.6681 | 13.489 | 13.3154 | 13.1287 | 12.9299 | 12.7412 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.004 | 13.8125 | 13.6614 | 13.463 | 13.2265 | 12.9612 | 12.6709 | 12.303 | 3.9582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.004 | 13.9882 | 13.9722 | 13.9501 | 13.8821 | 13.5446 | 13.4576 | 13.3182 | 13.1064 | 12.318 | 12.1331 | 11.9609 | 11.6613 | 5.5493 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.8757 | 4.8449 | 4.7674 | 4.7432 | 4.6368 | 4.5172 | 4.3603 | 4.2673 | 4.1327 | 3.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.8757 | 4.8362 | 4.7542 | 4.7032 | 4.5441 | 4.3913 | 3.835 | 3.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.8757 | 4.9196 | 4.9336 | 4.9482 | 4.9086 | 4.8683 | 4.8383 | 4.7908 | 4.7308 | 4.6026 | 4.4783 | 4.3496 | 4.2226 | 4.0947 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.8757 | 4.803 | 4.7223 | 4.6131 | 4.4875 | 3.6314 | 3.1106 | 2.5366 | 1.8701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.8757 | 4.9027 | 4.9048 | 4.8975 | 4.8595 | 4.8182 | 4.5465 | 4.4436 | 4.2876 | 4.1629 | 3.1533 | 2.6738 | 2.203 | 1.8136 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Best View | Headroom (MW) | 42.7085 | 42.7441 | 42.7839 | 42.7713 | 42.7273 | 42.6367 | 42.5449 | 42.4653 | 42.3665 | 42.2499 | 42.1652 | 42.1073 | 42.0712 | 42.0698 | 41.6761 | 41.762 | 41.8757
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 42.7085 | 42.7885 | 42.8446 | 42.8919 | 42.8469 | 42.7766 | 42.6611 | 42.6029 | 42.4749 | 42.2916 | 42.1695 | 42.1227 | 42.0472 | 41.9913 | 41.1105 | 40.7328 | 40.8004
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Falling Short | Headroom (MW) | 42.7085 | 42.8405 | 42.9518 | 43.0555 | 43.1174 | 43.166 | 43.2342 | 43.2961 | 43.3306 | 43.3369 | 43.3392 | 43.3362 | 43.3177 | 43.3102 | 42.4476 | 41.2909 | 40.612
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Leading the Way | Headroom (MW) | 42.7085 | 42.7441 | 42.7839 | 42.7713 | 42.7273 | 42.6367 | 42.5449 | 42.4662 | 42.3704 | 42.2528 | 42.1652 | 42.1044 | 42.0644 | 42.0591 | 41.3669 | 41.413 | 41.5086
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | System Transformation | Headroom (MW) | 42.7085 | 42.8454 | 42.9651 | 43.0637 | 43.1284 | 43.1645 | 43.2139 | 43.256 | 43.2595 | 43.2482 | 43.2238 | 43.2074 | 43.195 | 43.2312 | 41.9409 | 41.5908 | 41.6452
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 64.797 | 63.1302 | 60.6845 | 58.0691 | 54.95 | 51.5223 | 49.1035 | 46.5464 | 44.0738 | 41.2286 | 39.1946 | 37.2956 | 35.8385 | 34.7012 | 23.8202 | 20.024 | 18.2311
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 64.797 | 63.5451 | 61.2215 | 59.3256 | 56.2485 | 53.8742 | 51.1987 | 48.727 | 45.769 | 41.8229 | 38.9664 | 36.6895 | 34.2575 | 32.2032 | 15.7508 | 7.7796 | 5.8413
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 64.797 | 64.1587 | 63.0735 | 61.9481 | 60.3416 | 59.1108 | 58.292 | 57.3074 | 56.2203 | 54.8296 | 53.4689 | 52.0217 | 50.5411 | 49.199 | 35.7397 | 24.3327 | 15.8164
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 64.797 | 63.0483 | 60.547 | 57.8115 | 54.5904 | 51.0442 | 48.5308 | 45.7411 | 42.9147 | 39.9358 | 37.7099 | 35.5868 | 33.9639 | 32.673 | 20.4262 | 15.8975 | 13.4339
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 64.797 | 64.0144 | 62.4068 | 60.8619 | 58.8115 | 57.4701 | 56.5191 | 55.2479 | 53.7803 | 52.3093 | 49.9383 | 47.7152 | 45.8717 | 44.5908 | 30.1278 | 25.2862 | 21.9255
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.8883 | 14.8373 | 14.6726 | 14.6066 | 14.3033 | 13.9558 | 13.5499 | 13.2878 | 12.957 | 12.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.8883 | 14.8307 | 14.6681 | 14.5789 | 14.1798 | 13.7787 | 13.2995 | 12.9247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.8883 | 14.9685 | 15.0445 | 15.1065 | 15.0577 | 15.0008 | 14.941 | 14.8492 | 14.7438 | 14.5099 | 14.2604 | 14.0131 | 13.7829 | 13.6057 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.8883 | 14.6958 | 14.5088 | 14.2237 | 13.8583 | 13.4463 | 13.0076 | 12.5413 | 9.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.8883 | 14.9744 | 15.0292 | 15.0589 | 15.0431 | 14.9924 | 14.9174 | 14.8113 | 14.6552 | 14.4447 | 14.2033 | 14.0291 | 13.9849 | 13.9764 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.6649 | 10.4539 | 9.9799 | 9.4886 | 8.7442 | 7.9255 | 6.8484 | 5.8299 | 4.7857 | 3.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.6649 | 10.4535 | 9.9832 | 9.4441 | 8.5637 | 7.6581 | 6.4483 | 5.2241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.6649 | 10.6081 | 10.3985 | 10.076 | 9.6804 | 9.2893 | 8.7705 | 8.2094 | 7.6709 | 7.054 | 6.4342 | 5.775 | 5.1163 | 4.4969 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.6649 | 10.3498 | 9.8197 | 8.9948 | 8.0291 | 7.0064 | 5.8111 | 4.2709 | 3.1568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.6649 | 10.6002 | 10.3376 | 9.8875 | 9.3959 | 8.8951 | 8.2344 | 7.4208 | 6.6177 | 6.0108 | 5.3185 | 4.7254 | 4.3744 | 4.2425 | 0 | 0 | 0
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.4983 | 9.4147 | 9.3465 | 9.3267 | 9.181 | 8.4969 | 8.0615 | 7.7319 | 7.3636 | 7.0789 | 6.85 | 6.6782 | 6.5341 | 6.4085 | 5.2286 | 4.06 | 3.6816
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.4983 | 9.2933 | 9.0605 | 8.8924 | 8.5068 | 7.6492 | 6.9325 | 6.2534 | 5.6036 | 5.0659 | 4.619 | 4.2601 | 3.9807 | 3.7628 | 2.3132 | 1.7879 | 1.9276
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.4983 | 9.4286 | 9.3866 | 9.3561 | 9.1868 | 8.5085 | 8.1263 | 7.8015 | 7.4788 | 7.2015 | 6.9257 | 6.6167 | 6.3375 | 6.0662 | 4.6134 | 3.1371 | 2.2761
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.4983 | 9.2026 | 8.965 | 8.689 | 8.3253 | 7.1693 | 6.4896 | 5.8366 | 5.2898 | 4.9285 | 4.6138 | 4.3745 | 4.2847 | 4.2497 | 3.2671 | 3.0228 | 2.9972
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.4983 | 9.4015 | 9.3317 | 9.2504 | 9.055 | 8.3902 | 7.9336 | 7.4604 | 6.9956 | 6.7039 | 6.3655 | 6.0329 | 5.8478 | 5.764 | 3.8187 | 3.4133 | 3.379
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 32.4847 | 31.9937 | 31.6572 | 31.387 | 31.3103 | 31.2775 | 30.8723 | 30.6862 | 30.5622 | 30.5553 | 30.5615 | 30.5741 | 30.5867 | 30.3332 | 18.2269 | 11.2381 | 8.4049
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.4847 | 31.9931 | 31.6574 | 31.386 | 31.3076 | 31.274 | 30.8666 | 30.6774 | 30.55 | 26.5689 | 23.8067 | 21.9032 | 19.3498 | 17.1624 | 0 | 0 | 0
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.4847 | 32.1068 | 31.8697 | 31.618 | 31.553 | 31.4928 | 31.169 | 31.0331 | 30.9188 | 30.8593 | 30.8025 | 30.7471 | 30.7084 | 30.7048 | 24.8504 | 13.2265 | 4.6077
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.4847 | 31.9444 | 31.605 | 31.2757 | 31.1888 | 31.1131 | 30.6561 | 30.4483 | 27.5501 | 23.8468 | 21.6412 | 18.7634 | 17.0501 | 15.6681 | 2.4419 | 0 | 0
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.4847 | 31.9974 | 31.6673 | 31.399 | 31.3247 | 31.2978 | 30.9019 | 30.7131 | 30.6001 | 30.6219 | 30.6445 | 30.6642 | 30.6773 | 30.7056 | 19.7337 | 15.1258 | 10.9933
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 51.2084 | 49.6987 | 47.5743 | 46.385 | 45.3928 | 44.0405 | 41.2709 | 39.2683 | 36.8806 | 34.1095 | 32.7011 | 32.1399 | 31.2131 | 30.5663 | 18.367 | 11.3245 | 8.4695
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 51.2084 | 49.4379 | 47.1448 | 45.5862 | 43.8748 | 41.9919 | 38.2141 | 35.1482 | 31.5263 | 26.7731 | 23.9897 | 22.0715 | 19.4985 | 17.2944 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 51.2084 | 50.2774 | 49.2619 | 48.3957 | 47.8861 | 47.1645 | 45.8552 | 44.8442 | 43.7467 | 42.3652 | 41.1428 | 39.8632 | 38.6329 | 37.6322 | 25.0414 | 13.3282 | 4.6431
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 51.2084 | 48.8505 | 46.3698 | 43.9161 | 42.2472 | 38.667 | 34.7159 | 31.2218 | 27.7619 | 24.0301 | 21.8075 | 18.9077 | 17.1812 | 15.7885 | 2.4607 | 0 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 51.2084 | 49.9993 | 48.4723 | 47.3379 | 46.868 | 46.1623 | 44.5758 | 42.9769 | 41.3384 | 40.0314 | 38.2356 | 36.5542 | 35.2138 | 34.5 | 19.8854 | 15.242 | 11.0778
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.7208 | 15.1798 | 14.8994 | 14.8134 | 14.6023 | 14.0542 | 13.2755 | 12.8294 | 12.2208 | 11.4591 | 11.3079 | 11.5512 | 11.7806 | 12.1439 | 8.8575 | 5.5333 | 3.458
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.7208 | 15.0354 | 14.6916 | 14.4141 | 13.7837 | 12.8494 | 11.2511 | 10.016 | 8.5464 | 6.264 | 5.0508 | 4.2307 | 3.0582 | 2.0509 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.7208 | 15.3608 | 15.3828 | 15.3523 | 15.2356 | 14.8402 | 14.3709 | 14.007 | 13.591 | 12.9185 | 12.3734 | 11.8132 | 11.2541 | 10.7581 | 4.9525 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.7208 | 14.8136 | 14.4028 | 13.8176 | 13.2132 | 11.4167 | 9.6459 | 8.2489 | 6.8676 | 4.9916 | 3.9606 | 2.3178 | 1.4983 | 0.82023 | 0 | 0 | 0
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.7208 | 15.3025 | 15.3326 | 15.2683 | 15.1896 | 14.7925 | 14.1925 | 13.483 | 12.8708 | 12.0745 | 11.2349 | 10.4383 | 9.7908 | 9.447 | 2.9015 | 0.72093 | 0
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 56.5289 | 56.4535 | 56.2233 | 56.2458 | 55.4343 | 54.5375 | 53.5184 | 52.8198 | 51.9366 | 50.9234 | 50.2169 | 50.1841 | 50.1112 | 50.1916 | 46.5251 | 43.4782 | 41.9915
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 56.5289 | 56.2321 | 55.7808 | 55.4953 | 53.8926 | 52.5504 | 50.5453 | 48.7565 | 46.7034 | 43.8735 | 41.6404 | 40.7367 | 39.4621 | 38.4325 | 29.9167 | 26.4503 | 25.7593
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 56.5289 | 56.6051 | 56.6882 | 56.749 | 55.9549 | 55.2042 | 54.4582 | 53.752 | 52.9518 | 51.9286 | 50.828 | 49.9518 | 49.0927 | 48.3229 | 41.8954 | 36.4978 | 32.3704
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 56.5289 | 55.9561 | 55.4252 | 54.7531 | 53.2231 | 50.8939 | 48.9574 | 47.017 | 45.0681 | 42.7437 | 41.0335 | 39.8696 | 39.0376 | 38.4068 | 31.831 | 29.7289 | 28.7794
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 56.5289 | 56.6067 | 56.6751 | 56.7003 | 55.8134 | 55.1192 | 54.2629 | 53.3071 | 52.1761 | 50.9393 | 49.112 | 48.19 | 47.4596 | 47.0779 | 40.3612 | 38.5252 | 36.9525
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 28.5873 | 28.5097 | 28.4476 | 28.434 | 28.2938 | 27.6114 | 27.1788 | 26.8527 | 26.4873 | 26.206 | 25.9808 | 25.8132 | 25.6733 | 25.5522 | 24.3866 | 23.2292 | 22.8703
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 28.5873 | 28.3876 | 28.1598 | 27.997 | 27.615 | 26.7572 | 26.0405 | 25.361 | 24.7106 | 24.1729 | 23.7267 | 23.3691 | 23.0918 | 22.8766 | 21.4339 | 20.9253 | 21.0904
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 28.5873 | 28.5236 | 28.4878 | 28.4636 | 28.2997 | 27.623 | 27.2442 | 26.9229 | 26.6035 | 26.3296 | 26.0572 | 25.751 | 25.4748 | 25.2062 | 23.7639 | 22.2937 | 21.4441
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 28.5873 | 28.2963 | 28.0637 | 27.7922 | 27.4323 | 26.2733 | 25.5936 | 24.9402 | 24.3936 | 24.034 | 23.7214 | 23.4848 | 23.3994 | 23.3693 | 22.4005 | 22.1777 | 22.1759
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 28.5873 | 28.4964 | 28.4326 | 28.3573 | 28.1671 | 27.5039 | 27.0499 | 26.5789 | 26.116 | 25.8274 | 25.4916 | 25.1613 | 24.9799 | 24.9008 | 22.9592 | 22.5736 | 22.5634
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.2827 | 12.2555 | 12.1943 | 12.1677 | 12.0216 | 11.8663 | 11.6734 | 11.5362 | 11.3192 | 11.0549 | 10.8533 | 10.734 | 10.6417 | 10.5779 | 9.107 | 8.3512 | 8.1053
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.2827 | 12.2394 | 12.1626 | 12.1171 | 11.9277 | 11.7449 | 11.5203 | 11.3328 | 11.0646 | 10.7251 | 10.4572 | 10.2877 | 10.1469 | 10.0559 | 0 | 0 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.2827 | 12.3179 | 12.3582 | 12.3856 | 12.3471 | 12.3029 | 12.2648 | 12.2166 | 12.1606 | 12.0365 | 11.9153 | 11.7728 | 11.6423 | 11.5198 | 9.8814 | 8.26 | 4.5509
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.2827 | 12.1866 | 12.1021 | 11.9537 | 11.7598 | 11.5518 | 11.3417 | 11.0873 | 10.7985 | 10.5624 | 10.3736 | 10.2429 | 10.1784 | 10.1782 | 2.4118 | 0 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.2827 | 12.2947 | 12.2985 | 12.2937 | 12.2358 | 12.1803 | 12.1078 | 12.0109 | 11.8695 | 11.7499 | 11.5974 | 11.4616 | 11.3603 | 11.3271 | 9.3529 | 8.4971 | 7.8884
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.4426 | 13.3455 | 13.1541 | 13.1279 | 12.9119 | 12.7618 | 12.1903 | 11.7731 | 11.2726 | 10.5083 | 10.2897 | 10.2968 | 9.9218 | 9.5949 | 6.1615 | 4.7174 | 3.904
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.4426 | 13.289 | 13.0446 | 12.9068 | 12.3489 | 11.9357 | 11.0524 | 10.2887 | 9.4154 | 8.2051 | 7.559 | 7.1223 | 6.3369 | 5.6252 | 0 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.4426 | 13.4781 | 13.5072 | 13.558 | 13.4235 | 13.3831 | 13.3265 | 13.217 | 13.0926 | 12.9269 | 12.7659 | 12.5768 | 12.4093 | 12.2708 | 9.0589 | 3.5856 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.4426 | 13.1305 | 12.8204 | 12.4466 | 11.7461 | 10.3978 | 9.3872 | 8.2923 | 7.4968 | 6.48 | 5.3492 | 4.5862 | 3.9906 | 3.445 | 0 | 0 | 0
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.4426 | 13.4742 | 13.4829 | 13.4922 | 13.1335 | 13.1088 | 12.8285 | 12.7036 | 11.8627 | 11.7663 | 11.2886 | 10.8485 | 10.4879 | 10.2926 | 7.1796 | 6.7518 | 5.9167
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.7021 | 14.5493 | 14.3745 | 14.2645 | 14.1042 | 13.8136 | 13.575 | 13.4364 | 13.2506 | 12.9957 | 12.8807 | 12.9413 | 13.0221 | 13.1552 | 2.1097 | 0 | 0
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.7021 | 14.5321 | 14.3374 | 14.2036 | 13.8075 | 13.3607 | 12.9162 | 12.5574 | 12.1472 | 3.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.7021 | 14.6464 | 14.6082 | 14.5755 | 14.4983 | 14.3635 | 14.2882 | 14.1817 | 14.0732 | 13.8632 | 13.6465 | 13.4217 | 13.2085 | 13.0342 | 0 | 0 | 0
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.7021 | 14.4296 | 14.1935 | 13.9055 | 13.5296 | 13.0256 | 12.6174 | 12.1967 | 11.812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.7021 | 14.6294 | 14.5573 | 14.4788 | 14.3846 | 14.225 | 14.1048 | 13.9641 | 13.7941 | 13.6092 | 13.4188 | 13.2517 | 13.1587 | 13.1814 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.2455 | 7.202 | 7.1512 | 6.5736 | 5.8829 | 5.0894 | 3.6767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.2455 | 7.1865 | 7.1032 | 6.5155 | 5.7629 | 4.9104 | 1.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.2455 | 7.2176 | 7.1732 | 6.6602 | 6.1528 | 5.3634 | 5.1028 | 4.9244 | 4.7473 | 3.4394 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.2455 | 7.1674 | 7.0556 | 6.3558 | 5.5739 | 2.2588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.2455 | 7.2127 | 7.1592 | 6.5861 | 5.904 | 5.1165 | 4.8431 | 3.2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.5871 | 24.001 | 20.7825 | 17.9241 | 15.2263 | 11.6115 | 7.653 | 4.5679 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.5871 | 23.9379 | 20.4419 | 17.759 | 14.3649 | 11.1681 | 6.3496 | 2.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.5871 | 25.0267 | 23.0912 | 21.0451 | 19.1361 | 17.1709 | 14.7213 | 12.5974 | 10.6899 | 8.6563 | 6.6697 | 4.6846 | 2.8757 | 1.3266 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.5871 | 23.3406 | 19.8023 | 16.0482 | 12.5136 | 7.9709 | 3.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.5871 | 24.4751 | 21.729 | 19.4577 | 17.1917 | 15.1545 | 12.2773 | 9.578 | 7.4794 | 5.629 | 3.2978 | 1.213 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.4203 | 13.9752 | 13.6735 | 13.6124 | 13.5139 | 13.248 | 12.8945 | 12.1171 | 11.541 | 11.1683 | 10.8308 | 10.5787 | 10.3037 | 10.0608 | 9.0831 | 9.5375 | 10.5227
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.4203 | 13.8927 | 13.5286 | 13.2986 | 12.9751 | 12.6086 | 12.0408 | 11.0902 | 10.2576 | 9.6257 | 9.1644 | 8.8986 | 8.4276 | 8.0238 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.4203 | 14.1319 | 14.0458 | 14.0212 | 13.9855 | 13.8584 | 13.6858 | 13.2284 | 12.8907 | 12.6395 | 12.374 | 12.0882 | 11.7495 | 11.3964 | 9.0736 | 1.7877 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.4203 | 13.7945 | 13.4032 | 13.081 | 12.8509 | 12.4684 | 11.9686 | 10.9382 | 10.1889 | 9.7493 | 9.3193 | 8.9176 | 8.5636 | 8.2589 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.4203 | 13.9731 | 13.7855 | 13.6165 | 13.531 | 13.401 | 13.2214 | 12.5547 | 12.1385 | 11.9309 | 11.6399 | 11.3195 | 10.926 | 10.5469 | 8.2694 | 8.3376 | 9.3975
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.3368 | 12.1617 | 11.9555 | 11.9049 | 11.7839 | 11.6271 | 11.3923 | 11.3056 | 11.1763 | 7.8617 | 6.2642 | 5.0414 | 3.9213 | 2.4624 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.3368 | 12.1183 | 11.8627 | 11.7079 | 11.346 | 10.9831 | 10.5063 | 8.0646 | 4.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.3368 | 12.2692 | 12.2219 | 12.1995 | 12.1171 | 12.0375 | 11.9382 | 11.8165 | 11.6716 | 11.4452 | 11.2335 | 11.007 | 10.8058 | 9.2418 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.3368 | 12.0239 | 11.7538 | 11.451 | 11.1076 | 10.7198 | 7.8601 | 4.427 | 1.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.3368 | 12.2572 | 12.1795 | 12.1242 | 12.0705 | 11.9882 | 11.8772 | 11.7138 | 11.5211 | 11.3516 | 11.1834 | 11.0507 | 9.6612 | 9.1285 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.3652 | 4.0564 | 3.652 | 3.2222 | 2.6629 | 2.1308 | 1.5066 | 1.0054 | 0.43292 | 0 | 0 | 0 | 0.089184 | 0.58183 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.3652 | 3.98 | 3.4508 | 2.9573 | 1.9591 | 1.081 | 0.069904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.3652 | 4.2204 | 4.1031 | 3.8826 | 3.5419 | 3.2239 | 2.8912 | 2.555 | 2.1742 | 1.5824 | 0.98292 | 0.44891 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.3652 | 3.738 | 3.1305 | 2.3218 | 1.3446 | 0.32469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.3652 | 4.1562 | 3.903 | 3.5472 | 3.1213 | 2.7818 | 2.396 | 1.9145 | 1.3785 | 0.82159 | 0.18574 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.6358 | 15.4382 | 15.2237 | 14.6487 | 14.4174 | 14.1698 | 13.9111 | 13.2821 | 13.0678 | 12.941 | 12.9013 | 12.995 | 13.2029 | 13.4706 | 12.6034 | 11.9593 | 11.0234
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.6358 | 15.3678 | 15.0289 | 14.4137 | 14.0004 | 13.6109 | 13.1678 | 12.4293 | 11.9585 | 11.4323 | 11.0417 | 10.811 | 10.6083 | 9.58 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.6358 | 15.4808 | 15.3286 | 14.8617 | 14.6771 | 14.5112 | 14.3491 | 13.9598 | 13.7335 | 13.4366 | 13.1459 | 12.8472 | 12.5677 | 12.3395 | 10.1685 | 1.1767 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.6358 | 15.2603 | 14.8855 | 14.0727 | 13.6307 | 13.1777 | 12.7493 | 11.9186 | 11.4489 | 11.1404 | 10.8916 | 10.7525 | 10.5032 | 9.252 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.6358 | 15.4478 | 15.2492 | 14.6967 | 14.5002 | 14.3182 | 14.1209 | 13.5288 | 13.2514 | 13.0432 | 12.8201 | 12.6426 | 12.5254 | 12.5214 | 9.7604 | 7.732 | 6.5477
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.8759 | 11.6174 | 11.3253 | 11.0834 | 10.9937 | 9.8593 | 3.8866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.8759 | 11.5524 | 11.1657 | 10.8866 | 10.6769 | 9.2784 | 1.9356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.8759 | 11.6715 | 11.4751 | 11.2898 | 11.2181 | 10.9214 | 10.5907 | 10.4813 | 7.5556 | 3.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.8759 | 11.4647 | 11.0706 | 10.6619 | 10.1869 | 2.3877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.8759 | 11.6127 | 11.3194 | 11.083 | 10.6854 | 10.1781 | 8.6272 | 3.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.1386 | 4.8503 | 4.5284 | 4.211 | 3.8813 | 3.5271 | 3.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.1386 | 4.7871 | 4.363 | 4.011 | 3.4849 | 2.938 | 1.9244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.1386 | 4.9044 | 4.6778 | 4.4585 | 4.2052 | 3.9463 | 3.6707 | 3.368 | 3.0108 | 2.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.1386 | 4.6989 | 4.2505 | 3.7438 | 3.1822 | 2.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.1386 | 4.853 | 4.535 | 4.2266 | 3.9067 | 3.5843 | 3.2337 | 2.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.902 | 9.4521 | 9.1044 | 8.7476 | 8.3446 | 7.1758 | 6.4103 | 5.9014 | 5.2306 | 4.1844 | 3.7433 | 3.2794 | 2.781 | 2.3644 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.902 | 9.3953 | 8.8947 | 8.463 | 7.3854 | 6.656 | 5.4933 | 4.5474 | 3.4354 | 1.7622 | 0.78231 | 0.080497 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.902 | 9.6749 | 9.648 | 9.533 | 9.2886 | 9.1049 | 9.0056 | 8.8699 | 8.7136 | 8.433 | 8.1675 | 7.8736 | 7.5731 | 7.3255 | 2.6285 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.902 | 9.1343 | 8.5404 | 7.7577 | 6.7524 | 5.2558 | 4.2157 | 3.1567 | 2.1774 | 0.84809 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.902 | 9.6002 | 9.4 | 9.1347 | 8.7037 | 8.5094 | 8.4035 | 8.2444 | 8.0478 | 7.8184 | 7.1939 | 6.6119 | 6.1478 | 5.8973 | 0.29729 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.2246 | 19.093 | 18.7699 | 18.6941 | 18.2247 | 17.5623 | 15.0826 | 13.4206 | 11.4566 | 7.854 | 6.2581 | 5.0365 | 3.9175 | 2.46 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.2246 | 19.0753 | 18.7579 | 18.5628 | 17.1653 | 14.7169 | 11.1077 | 8.0568 | 4.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.2246 | 19.2981 | 19.3755 | 19.4252 | 19.3348 | 19.2363 | 19.1123 | 18.9094 | 18.1672 | 16.1848 | 14.7591 | 12.4734 | 11.1279 | 9.2328 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.2246 | 18.8858 | 18.5036 | 17.9831 | 15.6114 | 11.4851 | 7.8525 | 4.4227 | 1.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.2246 | 19.3426 | 19.3857 | 19.3928 | 19.3641 | 19.2692 | 18.998 | 17.6932 | 16.4552 | 15.1152 | 12.9318 | 11.0708 | 9.6518 | 9.1196 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.7544 | 16.7797 | 15.5952 | 14.6875 | 14.4681 | 13.4934 | 12.78 | 12.1721 | 11.4961 | 10.4733 | 9.9835 | 9.3718 | 8.7608 | 8.2091 | 3.659 | 1.2307 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.7544 | 16.6987 | 15.3795 | 14.5265 | 14.1284 | 13.6999 | 12.7977 | 12.014 | 11.074 | 9.5456 | 8.6116 | 7.9226 | 6.8245 | 5.8408 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.7544 | 16.8369 | 16.1328 | 15.5144 | 15.4066 | 15.3085 | 15.202 | 15.0461 | 14.8366 | 14.5506 | 14.2496 | 13.917 | 13.5778 | 13.3462 | 9.4146 | 5.6261 | 2.6563
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.7544 | 16.5539 | 15.2432 | 14.0569 | 13.6236 | 12.4644 | 11.591 | 10.6838 | 9.8198 | 8.5631 | 7.7739 | 6.7915 | 5.9531 | 5.1897 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.7544 | 16.8917 | 15.8718 | 15.1787 | 15.1873 | 15.1312 | 15.0446 | 14.8876 | 14.6904 | 14.4279 | 13.7656 | 13.1288 | 12.585 | 12.1874 | 7.7414 | 6.2865 | 5.0567
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Best View | Headroom (MW) | 27.1216 | 2.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 27.1216 | 1.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 27.1216 | 10.8836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 27.1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 27.1216 | 6.3642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.1091 | 9.8324 | 9.0184 | 7.8619 | 6.5363 | 1.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.1091 | 9.7857 | 9.0357 | 7.9388 | 6.2898 | 2.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.1091 | 9.9782 | 9.5821 | 8.8532 | 7.9764 | 6.9518 | 4.8313 | 2.9703 | 1.1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.1091 | 9.6443 | 8.7534 | 7.2545 | 4.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.1091 | 9.9484 | 9.4554 | 8.4699 | 7.3385 | 5.1157 | 2.3956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0396 | 14.2646 | 13.4344 | 13.1163 | 12.6465 | 11.8647 | 11.0777 | 11.0267 | 10.7029 | 10.4138 | 10.3996 | 10.5287 | 10.6489 | 10.8028 | 10.6097 | 10.828 | 11.12
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0396 | 14.2952 | 13.3785 | 13.0787 | 12.4831 | 11.8517 | 10.9704 | 10.8144 | 10.3342 | 9.7868 | 9.5568 | 9.4241 | 9.2317 | 9.1352 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0396 | 14.5592 | 14.0583 | 13.8602 | 13.5715 | 13.081 | 12.5487 | 12.4659 | 12.2532 | 11.9755 | 11.7926 | 11.5948 | 11.4236 | 11.3045 | 10.0949 | 1.7941 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0396 | 14.1581 | 13.2727 | 12.8055 | 12.2361 | 11.3631 | 10.4629 | 10.0663 | 9.6565 | 9.2521 | 9.1008 | 9.045 | 9.0639 | 9.111 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0396 | 14.3888 | 13.6098 | 13.3936 | 13.0352 | 12.6164 | 11.9756 | 11.9777 | 11.7187 | 11.4247 | 11.3469 | 11.2605 | 11.2079 | 11.2241 | 9.6859 | 9.6829 | 9.9812
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 26.0752 | 20.6071 | 16.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 26.0752 | 19.761 | 10.4769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 26.0752 | 23.592 | 23.6866 | 21.6397 | 4.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 26.0752 | 16.2664 | 0.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 26.0752 | 22.5973 | 20.3846 | 7.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.0341 | 8.8106 | 8.4932 | 7.6818 | 4.4059 | 0.044466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.0341 | 8.7301 | 8.336 | 7.9233 | 4.1048 | 0.55785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.0341 | 8.9498 | 8.8814 | 8.7218 | 8.3711 | 6.4658 | 3.4207 | 0.84367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.0341 | 8.5802 | 8.1654 | 6.2969 | 2.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.0341 | 8.9371 | 8.8388 | 8.6306 | 6.2642 | 3.7153 | 0.099288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.1642 | 5.4314 | 2.6566 | 0.18535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.1642 | 5.557 | 2.6719 | 0.50746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.1642 | 6.2351 | 4.3054 | 2.41 | 0.91891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.1642 | 5.2695 | 2.4079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.1642 | 5.702 | 3.0066 | 0.93738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.5678 | 4.7132 | 3.7632 | 3.0368 | 1.8895 | 1.194 | 0.65915 | 0.22517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.5678 | 4.731 | 3.759 | 2.8985 | 1.4483 | 0.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.5678 | 4.9703 | 4.3711 | 3.7988 | 2.9734 | 2.4945 | 2.1177 | 1.7434 | 1.2382 | 0.85737 | 0.52571 | 0.16756 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.5678 | 4.6 | 3.5683 | 2.4268 | 0.93098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.5678 | 4.821 | 4.0011 | 3.1869 | 2.0088 | 1.4964 | 1.0675 | 0.64497 | 0.050241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.0547 | 6.055 | 6.028 | 5.9926 | 5.9704 | 5.2866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.0547 | 6.0378 | 5.9945 | 5.9403 | 5.8839 | 5.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.0547 | 6.0649 | 6.0652 | 6.0472 | 6.0197 | 6.0008 | 5.9889 | 5.9617 | 3.3679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.0547 | 6.0265 | 5.9796 | 5.9016 | 5.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.0547 | 6.0563 | 6.0388 | 6.0128 | 5.9652 | 5.9428 | 5.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.8362 | 11.4118 | 10.727 | 10.4087 | 9.8191 | 8.9865 | 7.7613 | 7.0239 | 4.9654 | 3.2922 | 2.0317 | 1.1544 | 0.20839 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.8362 | 11.3608 | 10.2495 | 9.3678 | 8.1796 | 7.0224 | 5.2208 | 3.9178 | 0.97176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.8362 | 11.5046 | 11.0843 | 10.9064 | 10.7467 | 10.3594 | 9.631 | 8.9909 | 7.6285 | 6.1858 | 4.7067 | 3.0603 | 1.351 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.8362 | 11.1687 | 9.6019 | 8.2334 | 7.1932 | 5.9646 | 4.2787 | 2.6415 | 0.031707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.8362 | 11.44 | 10.8051 | 10.3547 | 10.0203 | 9.488 | 8.6366 | 7.9041 | 5.7643 | 3.9855 | 1.895 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.6273 | 11.9962 | 11.5885 | 10.2684 | 7.9255 | 2.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.6273 | 12.0161 | 11.5594 | 10.3418 | 7.5058 | 3.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.6273 | 12.4603 | 12.2774 | 11.3102 | 10.4066 | 8.2957 | 5.7653 | 3.5445 | 1.3213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.6273 | 11.7988 | 11.2991 | 9.4855 | 5.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.6273 | 12.1546 | 11.9644 | 10.8689 | 9.6057 | 6.1047 | 2.8588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.5755 | 10.6727 | 10.758 | 10.5799 | 10.6171 | 10.5101 | 10.3538 | 10.176 | 9.9895 | 9.816 | 9.621 | 9.4586 | 9.2826 | 9.1252 | 8.7093 | 2.407 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.5755 | 10.6478 | 10.7092 | 10.5514 | 10.5557 | 10.4488 | 10.2187 | 10.0036 | 9.7252 | 9.4662 | 9.2377 | 9.1258 | 8.8674 | 8.649 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.5755 | 10.6963 | 10.8228 | 10.7303 | 10.8026 | 10.8167 | 10.7856 | 10.7317 | 10.6955 | 10.6587 | 10.5949 | 10.4916 | 10.373 | 10.2391 | 9.1026 | 1.1946 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.5755 | 10.6257 | 10.7048 | 10.4898 | 10.5083 | 10.3981 | 10.1759 | 9.901 | 9.6375 | 9.4586 | 9.2413 | 9.0033 | 8.8 | 8.6421 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.5755 | 10.69 | 10.806 | 10.6923 | 10.7718 | 10.7636 | 10.6952 | 10.6041 | 10.5235 | 10.4201 | 10.2754 | 10.0962 | 9.8603 | 9.6248 | 8.4527 | 7.8502 | 6.6478
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.225 | 5.4431 | 4.2237 | 3.9195 | 3.4199 | 2.8172 | 1.8387 | 1.2952 | 0.70892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.225 | 5.3514 | 4.0074 | 3.4937 | 2.4485 | 1.4112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.225 | 5.6825 | 4.9662 | 4.7018 | 4.3141 | 3.8184 | 3.3766 | 3.0607 | 2.7384 | 2.2198 | 1.7182 | 1.2411 | 0.81699 | 0.50111 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.225 | 5.1111 | 3.7281 | 2.8716 | 1.8549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.225 | 5.5563 | 4.5306 | 4.1766 | 3.7425 | 3.2554 | 2.7748 | 2.4345 | 2.0989 | 1.7166 | 0.92933 | 0.32196 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 24.8787 | 14.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 24.8787 | 13.2352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 24.8787 | 19.5139 | 11.9648 | 8.4045 | 1.9668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 24.8787 | 8.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 24.8787 | 18.5836 | 7.2599 | 1.8061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.9856 | 12.559 | 12.1243 | 11.4549 | 9.5289 | 8.0088 | 5.6911 | 3.3793 | 1.7325 | 0.47453 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.9856 | 12.3447 | 11.5663 | 10.7962 | 8.2983 | 6.2702 | 3.3039 | 0.70051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.9856 | 12.7231 | 12.4913 | 12.0655 | 10.6669 | 9.382 | 7.8978 | 6.5703 | 5.4351 | 4.2927 | 3.2027 | 2.1495 | 1.1595 | 0.28711 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.9856 | 12.1582 | 11.3743 | 10.1667 | 7.6255 | 4.4003 | 1.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.9856 | 12.6658 | 12.3802 | 11.8473 | 10.0644 | 8.7434 | 7.0146 | 5.2328 | 3.9614 | 3.1389 | 2.0079 | 1.2084 | 0.60095 | 0.35194 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.0371 | 16.9918 | 16.8337 | 16.7116 | 16.5928 | 10.086 | 3.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.0371 | 16.9555 | 16.7652 | 16.6024 | 15.9264 | 9.4917 | 1.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.0371 | 17.021 | 16.9677 | 16.8964 | 16.8137 | 16.7455 | 14.1315 | 10.989 | 7.7293 | 3.7193 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.0371 | 16.928 | 16.7436 | 16.506 | 12.9169 | 2.4426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.0371 | 17.0016 | 16.8955 | 16.7812 | 16.6724 | 13.8164 | 8.8255 | 3.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 31.7211 | 7.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 31.7211 | 5.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 31.7211 | 15.1888 | 4.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 31.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 31.7211 | 10.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.1287 | 7.5913 | 7.1751 | 6.7423 | 6.477 | 5.4644 | 4.6757 | 4.1326 | 3.4401 | 2.3585 | 1.853 | 1.2944 | 0.71045 | 0.20129 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.1287 | 7.5392 | 6.9716 | 6.4651 | 5.5376 | 4.8981 | 3.7312 | 2.7735 | 1.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.1287 | 7.8005 | 7.6711 | 7.4596 | 7.2734 | 7.1481 | 6.9884 | 6.8079 | 6.6075 | 6.2818 | 5.9767 | 5.6398 | 5.3029 | 5.0099 | 0.5388 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.1287 | 7.2778 | 6.5967 | 5.7535 | 4.8913 | 3.5553 | 2.4855 | 1.4271 | 0.43913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.1287 | 7.727 | 7.4255 | 7.0653 | 6.7465 | 6.6198 | 6.4602 | 6.2598 | 6.0215 | 5.7574 | 5.106 | 4.4826 | 3.9738 | 3.6575 | 0 | 0 | 0
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.1326 | 1.0126 | 0.85335 | 0.82254 | 0.79544 | 0.037359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.1326 | 0.9386 | 0.69983 | 0.56386 | 0.41925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.1326 | 1.0347 | 0.96986 | 0.95757 | 0.95221 | 0.20872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.1326 | 0.85951 | 0.59046 | 0.35598 | 0.24051 | 0.11045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.1326 | 0.95511 | 0.80247 | 0.69906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.1455 | 1.0242 | 0.86306 | 0.8319 | 0.80449 | 0.037784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.1455 | 0.94928 | 0.7078 | 0.57028 | 0.42402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.1455 | 1.0465 | 0.9809 | 0.96846 | 0.96304 | 0.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.1455 | 0.86929 | 0.59718 | 0.36003 | 0.24325 | 0.11171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.1455 | 0.96597 | 0.8116 | 0.70702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.3387 | 19.2495 | 14.0349 | 7.6869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.3387 | 19.2256 | 13.6946 | 7.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.3387 | 19.2802 | 18.2322 | 13.3772 | 7.7595 | 2.6748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.3387 | 19.185 | 13.0777 | 5.3665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.3387 | 19.2563 | 15.4748 | 10.1321 | 2.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.7159 | 14.6264 | 14.0716 | 7.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.7159 | 14.6046 | 13.7304 | 7.8046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.7159 | 14.6878 | 14.6778 | 13.4121 | 7.7797 | 2.6818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.7159 | 14.5479 | 13.1118 | 5.3805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.7159 | 14.6755 | 14.6207 | 10.1586 | 2.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.2009 | 20.3422 | 14.6538 | 8.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.2009 | 20.3822 | 14.2985 | 8.1276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.2009 | 20.5927 | 19.0362 | 13.9671 | 8.1017 | 2.7928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.2009 | 20.2784 | 13.6544 | 5.6032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.2009 | 20.4256 | 16.1573 | 10.5789 | 2.9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 27.2496 | 27.2259 | 27.1377 | 27.0774 | 26.9416 | 26.7525 | 26.498 | 26.3188 | 26.0701 | 25.8739 | 25.7824 | 25.8121 | 25.8534 | 25.9734 | 6.6159 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 27.2496 | 27.1996 | 27.0916 | 26.9873 | 26.7221 | 26.4088 | 25.9995 | 25.6255 | 25.1562 | 24.6299 | 24.2213 | 23.9401 | 23.6953 | 23.5497 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 27.2496 | 27.2861 | 27.3108 | 27.3048 | 27.2224 | 27.1333 | 27.0293 | 26.9089 | 26.7682 | 26.5537 | 26.3466 | 26.1262 | 25.924 | 25.7781 | 24.0943 | 22.7073 | 13.6819
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 27.2496 | 27.1493 | 27.0288 | 26.8025 | 26.5003 | 26.132 | 25.7261 | 25.2752 | 24.7637 | 24.2388 | 23.9171 | 23.7511 | 23.7582 | 23.7566 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 27.2496 | 27.2713 | 27.2655 | 27.2216 | 27.1147 | 26.9696 | 26.808 | 26.6001 | 26.3183 | 26.0555 | 25.7778 | 25.5451 | 25.3704 | 25.3668 | 23.3308 | 18.0505 | 12.5816
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.8027 | 23.5292 | 23.2692 | 23.0519 | 22.5032 | 21.9777 | 20.9532 | 20.0618 | 18.4744 | 15.5853 | 13.667 | 11.9714 | 10.3526 | 9.4628 | 3.665 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.8027 | 23.4345 | 23.0981 | 22.772 | 21.9738 | 21.2594 | 20.0269 | 18.9144 | 17.0996 | 13.7483 | 11.4003 | 9.2901 | 7.2644 | 6.0019 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.8027 | 23.6678 | 23.6164 | 23.4747 | 23.1206 | 22.7051 | 22.312 | 21.9588 | 21.278 | 19.9195 | 18.7428 | 17.4214 | 16.4243 | 15.4883 | 10.5141 | 6.599 | 3.5777
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.8027 | 23.2755 | 22.8527 | 22.272 | 21.4802 | 19.8762 | 18.6706 | 17.2283 | 15.5043 | 12.6047 | 10.7966 | 8.6282 | 6.8063 | 5.6725 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.8027 | 23.6341 | 23.5084 | 23.3088 | 22.6657 | 22.2623 | 21.5515 | 21.0192 | 19.206 | 17.0266 | 14.9181 | 12.9041 | 12.0164 | 11.3715 | 6.6155 | 3.6287 | 1.453
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 26.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 26.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 26.8839 | 2.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 26.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 26.8839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.7219 | 8.8336 | 8.606 | 8.4851 | 8.0971 | 7.6827 | 6.8123 | 6.096 | 5.2817 | 3.8311 | 2.2985 | 1.689 | 0.7042 | 0 | 0 | 0 | 0
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.7219 | 8.8403 | 8.6369 | 8.4983 | 8.0116 | 7.5361 | 6.5834 | 5.7529 | 4.8169 | 3.192 | 1.5111 | 0.77931 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.7219 | 9.1747 | 9.2198 | 9.2345 | 9.1604 | 9.0886 | 8.9975 | 8.8614 | 8.7141 | 8.3941 | 7.7987 | 7.3925 | 7.0258 | 6.6897 | 2.5034 | 0 | 0
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.7219 | 8.6669 | 8.448 | 8.1047 | 7.6269 | 6.4478 | 5.5648 | 4.6102 | 3.6757 | 2.2938 | 0.95181 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.7219 | 8.9864 | 9.0196 | 9.0071 | 8.9309 | 8.8263 | 8.6802 | 8.5071 | 8.297 | 8.0055 | 6.719 | 6.1037 | 5.5775 | 5.2377 | 0.54893 | 0 | 0
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.469 | 13.4943 | 13.4918 | 13.5049 | 13.4339 | 13.3377 | 13.1783 | 13.0446 | 12.8576 | 12.6088 | 12.4197 | 12.3069 | 12.179 | 12.0532 | 10.8501 | 10.3792 | 10.396
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.469 | 13.4795 | 13.4897 | 13.483 | 13.3579 | 13.2335 | 13.0425 | 12.8696 | 12.6446 | 12.3351 | 12.0997 | 11.9448 | 11.7709 | 11.6177 | 10.1317 | 9.448 | 9.4005
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.469 | 13.5028 | 13.5221 | 13.5836 | 13.5946 | 13.6144 | 13.6187 | 13.6203 | 13.6005 | 13.5315 | 13.4618 | 13.39 | 13.3107 | 13.2189 | 12.2867 | 11.4508 | 10.9126
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.469 | 13.3698 | 13.2912 | 13.2057 | 13.1054 | 12.9908 | 12.8159 | 12.6018 | 12.3622 | 12.1442 | 11.941 | 11.8085 | 11.6934 | 11.596 | 10.6999 | 10.3777 | 10.2926
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.469 | 13.5461 | 13.6166 | 13.6629 | 13.6954 | 13.6929 | 13.661 | 13.6191 | 13.5421 | 13.461 | 13.3678 | 13.29 | 13.213 | 13.1804 | 12.1275 | 11.7606 | 11.4355
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.6131 | 18.5845 | 14.6538 | 8.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.6131 | 18.6885 | 14.2985 | 8.1276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.6131 | 19.2333 | 17.5841 | 13.9671 | 8.1017 | 2.7928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.6131 | 18.4462 | 13.6544 | 5.6032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.6131 | 18.8668 | 16.1573 | 10.5789 | 2.9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.3043 | 4.2742 | 4.2238 | 4.1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.3043 | 4.2629 | 4.1862 | 4.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.3043 | 4.2885 | 4.2806 | 4.2462 | 4.177 | 2.7196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.3043 | 4.246 | 4.195 | 4.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.3043 | 4.2722 | 4.2492 | 4.2017 | 2.8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.0381 | 3.6803 | 3.2589 | 2.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.0381 | 3.6718 | 3.2177 | 2.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.0381 | 3.8699 | 3.6762 | 3.4797 | 2.3659 | 2.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.0381 | 3.5995 | 3.1636 | 2.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.0381 | 3.7791 | 3.4585 | 3.229 | 1.7025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.1167 | 2.6718 | 2.1623 | 1.7815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.1167 | 2.6361 | 2.052 | 1.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.1167 | 2.8275 | 2.5456 | 2.2641 | 1.8805 | 1.5265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.1167 | 2.5558 | 2.0085 | 1.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.1167 | 2.7107 | 2.2349 | 1.906 | 1.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.91 | 2.4946 | 2.0189 | 1.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.91 | 2.4613 | 1.9159 | 1.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.91 | 2.64 | 2.3768 | 2.1139 | 1.7558 | 1.4252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.91 | 2.3863 | 1.8753 | 1.3533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.91 | 2.531 | 2.0867 | 1.7796 | 1.3221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 41.6503 | 39.9002 | 39.3438 | 39.114 | 37.9968 | 36.7543 | 34.3282 | 32.3569 | 30.0323 | 26.0423 | 22.1484 | 20.4485 | 17.9118 | 15.6377 | 0 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 41.6503 | 39.8877 | 39.4124 | 39.0842 | 37.5944 | 36.1177 | 33.3912 | 31.0001 | 28.2376 | 23.6311 | 19.2271 | 17.0764 | 14.1258 | 11.5739 | 0 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 41.6503 | 40.6784 | 40.8915 | 41.1293 | 41.056 | 40.9957 | 40.8172 | 40.5269 | 40.1532 | 39.2034 | 37.693 | 36.541 | 35.4329 | 34.4023 | 21.3765 | 8.4909 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 41.6503 | 39.2016 | 38.4773 | 37.4131 | 35.9437 | 32.988 | 30.4481 | 27.6414 | 24.8567 | 21.1306 | 17.5668 | 14.8879 | 12.6424 | 10.7548 | 0 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 41.6503 | 40.3911 | 40.662 | 40.7669 | 40.7225 | 40.4846 | 40.0526 | 39.5264 | 38.8191 | 37.8994 | 34.9021 | 33.3454 | 32.0097 | 31.3129 | 16.1448 | 9.9596 | 5.1229
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.95 | 12.946 | 12.8987 | 12.8912 | 12.7975 | 12.6956 | 12.5343 | 12.4191 | 12.2847 | 12.0368 | 11.0174 | 10.3088 | 9.2102 | 8.2374 | 0.61478 | 0 | 0
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.95 | 12.9477 | 12.9037 | 12.8848 | 12.7601 | 12.6329 | 12.4393 | 12.2733 | 12.0859 | 11.7741 | 9.9189 | 9.0341 | 7.781 | 6.6988 | 0 | 0 | 0
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.95 | 12.9811 | 13.0193 | 13.059 | 13.0836 | 13.1039 | 13.1006 | 13.0905 | 13.0722 | 12.993 | 12.9168 | 12.8309 | 12.7355 | 12.661 | 10.8053 | 5.4088 | 1.548
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.95 | 12.89 | 12.8267 | 12.7291 | 12.5836 | 12.4278 | 12.2431 | 12.0415 | 11.8582 | 10.794 | 9.2718 | 8.1092 | 7.1384 | 6.3231 | 0.12296 | 0 | 0
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.95 | 12.9852 | 13.0137 | 13.0296 | 13.0494 | 13.0368 | 12.9995 | 12.9536 | 12.8914 | 12.8118 | 12.7232 | 12.6557 | 12.6074 | 12.6409 | 8.4276 | 5.8126 | 3.8116
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.442 | 17.6537 | 17.2764 | 17.0681 | 16.7387 | 15.6361 | 14.6591 | 13.9145 | 13.0262 | 11.6384 | 10.8227 | 9.9743 | 9.1026 | 8.3201 | 2.0977 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.442 | 17.6306 | 17.1763 | 16.8787 | 16.0966 | 15.3527 | 14.0317 | 12.9255 | 11.6643 | 3.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.442 | 17.952 | 17.841 | 17.7689 | 17.5739 | 17.3855 | 17.1092 | 16.8579 | 16.5585 | 16.0511 | 15.5399 | 14.9753 | 14.4267 | 13.9065 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.442 | 17.387 | 16.8161 | 16.2404 | 15.4663 | 13.981 | 12.7201 | 11.5075 | 10.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.442 | 17.7904 | 17.5972 | 17.4199 | 17.1775 | 16.9517 | 16.5853 | 16.2299 | 15.7847 | 15.2552 | 14.2847 | 13.3707 | 12.6334 | 12.1064 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.9242 | 10.8408 | 10.6697 | 10.597 | 10.4225 | 10.1098 | 9.6848 | 9.4222 | 9.0959 | 8.5966 | 8.449 | 8.6167 | 8.7968 | 9.1168 | 2.0931 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.9242 | 10.8062 | 10.6116 | 10.4996 | 9.9255 | 9.3084 | 8.5281 | 7.8574 | 7.1029 | 3.5452 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.9242 | 10.9842 | 11.0396 | 11.091 | 11.038 | 10.9398 | 10.8136 | 10.6565 | 10.4638 | 10.0576 | 9.698 | 9.341 | 9.0021 | 8.7256 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.9242 | 10.6359 | 10.38 | 10.0218 | 9.4898 | 8.8227 | 8.0334 | 7.2088 | 6.4311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.9242 | 10.9623 | 10.9824 | 10.9917 | 10.9558 | 10.8348 | 10.6389 | 10.3891 | 10.0915 | 9.6869 | 9.3447 | 9.0637 | 8.9247 | 9.0167 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.3916 | 11.9049 | 10.8022 | 10.4747 | 9.8813 | 9.0434 | 7.8104 | 7.0684 | 4.9968 | 3.3131 | 2.0445 | 1.1617 | 0.20971 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.3916 | 11.658 | 10.3144 | 9.4271 | 8.2314 | 7.0669 | 5.2538 | 3.9426 | 0.97792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.3916 | 12.1345 | 11.6457 | 11.3983 | 10.9064 | 10.425 | 9.692 | 9.0479 | 7.6768 | 6.2249 | 4.7365 | 3.0797 | 1.3595 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.3916 | 11.2394 | 9.6627 | 8.2855 | 7.2387 | 6.0024 | 4.3058 | 2.6583 | 0.031907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.3916 | 12.0162 | 11.1935 | 10.5837 | 10.0838 | 9.5481 | 8.6913 | 7.9541 | 5.8008 | 4.0108 | 1.907 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.0229 | 7.9293 | 7.6488 | 7.5349 | 7.2861 | 6.9457 | 6.5095 | 6.3144 | 6.0001 | 5.6928 | 5.6807 | 6.0237 | 6.3686 | 6.8391 | 2.1077 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.0229 | 7.8886 | 7.5695 | 7.3562 | 6.6757 | 5.9697 | 5.1372 | 4.5039 | 3.7019 | 2.7153 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.0229 | 8.0901 | 8.1253 | 8.1257 | 8.0058 | 7.8542 | 7.7049 | 7.5213 | 7.2927 | 6.9093 | 6.5155 | 6.0998 | 5.719 | 5.3948 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.0229 | 7.7302 | 7.3883 | 6.8966 | 6.2542 | 5.5053 | 4.742 | 3.9534 | 3.1953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.0229 | 8.0973 | 8.0934 | 8.025 | 7.9206 | 7.7553 | 7.574 | 7.3277 | 7.0226 | 6.6798 | 6.3056 | 5.9832 | 5.8237 | 5.9306 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 38.6212 | 37.1531 | 35.3317 | 33.9233 | 32.5207 | 30.8222 | 28.5074 | 27.1329 | 24.0111 | 20.2086 | 18.1296 | 17.7551 | 17.6836 | 18.2315 | 0.89338 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 38.6212 | 36.6634 | 34.3516 | 32.0389 | 29.0261 | 26.1883 | 21.2682 | 16.5156 | 9.5183 | 1.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 38.6212 | 37.8556 | 37.2527 | 36.2252 | 35.112 | 34.0433 | 32.6733 | 31.4045 | 29.3377 | 26.8887 | 24.3983 | 21.6724 | 18.4295 | 15.048 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 38.6212 | 35.8105 | 33.1085 | 29.5546 | 26.7663 | 23.2138 | 17.5117 | 11.8933 | 5.5502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 38.6212 | 37.5547 | 36.486 | 34.8782 | 33.7615 | 32.6798 | 31.1442 | 29.6853 | 26.6735 | 23.9503 | 20.7849 | 17.0037 | 14.6169 | 13.7256 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.7699 | 23.2817 | 22.9496 | 22.4967 | 22.2416 | 21.0823 | 20.1161 | 19.353 | 18.4417 | 17.0657 | 16.3606 | 15.684 | 14.9771 | 14.3696 | 8.4312 | 4.7016 | 1.9083
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.7699 | 23.2602 | 22.8331 | 22.2916 | 21.4812 | 20.6489 | 19.205 | 17.9638 | 16.6277 | 14.4987 | 13.1195 | 12.1354 | 10.7139 | 9.4491 | 0.35411 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.7699 | 23.823 | 23.8092 | 23.56 | 23.4203 | 23.2041 | 22.9423 | 22.6258 | 22.2975 | 21.7679 | 21.2622 | 20.7312 | 20.2367 | 19.7952 | 13.9124 | 7.8726 | 3.4676
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.7699 | 22.9216 | 22.3542 | 21.4411 | 20.7283 | 19.1626 | 17.812 | 16.3886 | 15.0878 | 13.3011 | 12.0524 | 10.6598 | 9.5568 | 8.6122 | 1.7418 | 0.10193 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.7699 | 23.5272 | 23.4416 | 23.0976 | 23.045 | 22.868 | 22.5931 | 22.2614 | 21.9071 | 21.4537 | 20.6105 | 19.8092 | 19.1119 | 18.6543 | 12.0352 | 9.7495 | 8.3899
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 65.458 | 64.2696 | 63.1458 | 62.5935 | 61.5945 | 59.4176 | 57.183 | 55.7721 | 53.9502 | 48.5046 | 43.5146 | 42.6157 | 42.444 | 43.7592 | 2.1443 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 65.458 | 64.1385 | 62.8443 | 62.0048 | 59.3271 | 56.5603 | 51.0477 | 39.6406 | 22.8459 | 3.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 65.458 | 65.0286 | 64.9567 | 64.8962 | 64.3984 | 63.7649 | 63.0732 | 62.3073 | 61.3999 | 59.7522 | 58.1297 | 53.092 | 44.2344 | 36.118 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 65.458 | 63.3948 | 61.8358 | 59.941 | 57.3825 | 53.7003 | 42.0315 | 28.5462 | 13.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 65.458 | 64.8297 | 64.5453 | 64.1971 | 63.6717 | 62.9282 | 61.9796 | 60.8946 | 59.5641 | 57.9755 | 50.4375 | 40.8123 | 35.0834 | 32.944 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 19.4484 | 19.0982 | 18.5885 | 18.2733 | 18.1058 | 15.2769 | 5.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 19.4484 | 18.8825 | 18.1996 | 17.6875 | 15.5419 | 8.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 19.4484 | 19.1953 | 18.9371 | 18.683 | 18.51 | 18.3546 | 18.2194 | 16.0925 | 11.0639 | 4.5385 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 19.4484 | 18.7548 | 18.1106 | 17.3904 | 10.7575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 19.4484 | 18.9899 | 18.4752 | 18.0928 | 17.8213 | 17.6334 | 14.5212 | 7.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.0704 | 10.8514 | 10.5323 | 10.3053 | 9.9882 | 9.6197 | 9.1265 | 8.7023 | 8.1994 | 7.824 | 7.5867 | 6.9632 | 7.0029 | 7.0989 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.0704 | 10.7819 | 10.4043 | 10.0832 | 9.5356 | 8.9876 | 8.2777 | 7.6116 | 6.8579 | 6.0383 | 5.3876 | 4.3604 | 1.3369 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.0704 | 10.9679 | 10.8388 | 10.7067 | 10.4706 | 10.2637 | 9.9748 | 9.638 | 9.33 | 8.8835 | 8.4274 | 7.9495 | 7.4831 | 6.4749 | 2.6449 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.0704 | 10.6622 | 10.2347 | 9.7103 | 9.161 | 8.5658 | 7.8897 | 7.1049 | 6.3284 | 5.7775 | 5.336 | 5.042 | 4.8855 | 4.8231 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.0704 | 10.914 | 10.721 | 10.483 | 10.1969 | 9.5787 | 9.2163 | 8.5123 | 7.9909 | 7.5471 | 6.522 | 6.0944 | 5.8097 | 5.0587 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 91.1631 | 90.0508 | 79.7591 | 71.9955 | 58.9156 | 41.3054 | 18.2611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 91.1631 | 89.6417 | 77.656 | 68.2913 | 49.8528 | 30.2969 | 1.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 91.1631 | 90.818 | 90.2491 | 87.0683 | 77.6925 | 66.9349 | 55.1281 | 41.739 | 28.6377 | 7.4689 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 91.1631 | 86.8056 | 74.3858 | 59.6152 | 42.1048 | 12.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 91.1631 | 90.4383 | 86.5537 | 80.2383 | 70.2504 | 58.4639 | 45.292 | 27.6489 | 5.3198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.4357 | 7.144 | 6.6229 | 6.2242 | 5.7636 | 5.3895 | 4.5847 | 2.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.4357 | 7.1092 | 6.5399 | 6.0773 | 5.5406 | 5.1349 | 4.1369 | 0.88442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.4357 | 7.254 | 6.9622 | 6.6932 | 6.3688 | 6.1473 | 5.9076 | 5.593 | 5.2653 | 4.7199 | 3.4457 | 0.93526 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.4357 | 7.0397 | 6.4861 | 5.8959 | 5.3857 | 4.6442 | 1.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.4357 | 7.1629 | 6.7166 | 6.3346 | 5.9157 | 5.6079 | 5.2924 | 4.8493 | 4.3632 | 1.9212 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.2666 | 5.138 | 4.8264 | 4.2651 | 3.4318 | 2.5409 | 1.5508 | 0.33532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.2666 | 4.9742 | 4.5082 | 3.7246 | 2.5781 | 1.4891 | 0.18588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.2666 | 5.1951 | 5.094 | 4.659 | 4.049 | 3.3361 | 2.7161 | 1.9125 | 0.8084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.2666 | 4.7721 | 4.2218 | 3.0988 | 1.9381 | 0.52159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.2666 | 5.161 | 4.9714 | 4.3568 | 3.5668 | 2.7663 | 1.949 | 0.70274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.7122 | 3.6901 | 3.6167 | 3.565 | 3.4792 | 3.4016 | 3.2989 | 3.2398 | 3.1486 | 3.0681 | 3.0286 | 3.0485 | 3.086 | 3.1471 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.7122 | 3.6638 | 3.5663 | 3.4789 | 3.3498 | 3.2475 | 3.113 | 3.0144 | 2.877 | 2.732 | 2.636 | 2.5984 | 1.3017 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.7122 | 3.7251 | 3.7169 | 3.7074 | 3.636 | 3.5981 | 3.5492 | 3.4992 | 3.4485 | 3.3401 | 3.237 | 3.1336 | 3.0256 | 2.9411 | 1.6682 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.7122 | 3.6372 | 3.5433 | 3.4143 | 3.2932 | 3.1823 | 3.073 | 2.9553 | 2.8289 | 2.7392 | 2.6839 | 2.6621 | 2.6815 | 2.7347 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.7122 | 3.6961 | 3.6584 | 3.6124 | 3.527 | 3.4562 | 3.4011 | 3.3104 | 3.2235 | 3.117 | 3.0063 | 2.9086 | 2.831 | 2.8131 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.1009 | 6.932 | 6.7054 | 6.4762 | 5.5954 | 4.5131 | 3.6161 | 2.8338 | 1.8269 | 0.075098 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.1009 | 6.8942 | 6.6386 | 6.3526 | 5.392 | 4.2775 | 3.3216 | 2.4514 | 1.3524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.1009 | 7.0589 | 7.0182 | 6.9157 | 6.3709 | 5.5493 | 5.3107 | 5.0577 | 4.7293 | 4.1447 | 3.5064 | 2.4749 | 1.4072 | 0.53813 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.1009 | 6.7957 | 6.5106 | 6.069 | 5.0964 | 2.94 | 2.053 | 1.1287 | 0.11362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.1009 | 6.9888 | 6.8761 | 6.669 | 5.9122 | 5.0182 | 4.5 | 4.1597 | 3.3225 | 1.8543 | 0.048207 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.2601 | 5.1958 | 4.9692 | 4.3912 | 3.5333 | 2.6161 | 1.5966 | 0.34524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.2601 | 5.1213 | 4.6415 | 3.8348 | 2.6544 | 1.5332 | 0.19137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.2601 | 5.2034 | 5.1179 | 4.7968 | 4.1688 | 3.4348 | 2.7965 | 1.9691 | 0.83231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.2601 | 4.9133 | 4.3467 | 3.1904 | 1.9954 | 0.53702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.2601 | 5.1725 | 5.0269 | 4.4856 | 3.6723 | 2.8481 | 2.0067 | 0.72353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.6075 | 3.626 | 3.6257 | 3.6334 | 3.5757 | 2.8081 | 2.3664 | 1.8995 | 1.3511 | 0.50044 | 0.029616 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.6075 | 3.5831 | 3.5495 | 3.5171 | 3.445 | 3.3312 | 2.8473 | 2.3467 | 1.804 | 0.89664 | 0.32734 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.6075 | 3.6292 | 3.6413 | 3.6581 | 3.6068 | 3.5538 | 3.4947 | 3.4263 | 3.3595 | 3.2544 | 3.1508 | 3.0323 | 2.9057 | 2.7852 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.6075 | 3.5668 | 3.5435 | 3.4899 | 3.4119 | 2.5933 | 2.1008 | 1.5546 | 0.92351 | 0.028318 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.6075 | 3.6029 | 3.5921 | 3.5815 | 3.5077 | 3.4252 | 3.3274 | 3.2169 | 3.0975 | 2.9493 | 2.4152 | 1.8806 | 1.3608 | 0.85997 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.6979 | 8.4075 | 8.1584 | 7.9697 | 7.6587 | 7.2784 | 5.8677 | 4.8736 | 3.7562 | 1.4622 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.6979 | 8.3756 | 8.1059 | 7.868 | 7.5076 | 7.1139 | 5.5599 | 4.4904 | 3.2937 | 0.85787 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.6979 | 8.5499 | 8.4974 | 8.4 | 8.2411 | 8.0156 | 7.3773 | 7.1855 | 7.0119 | 6.494 | 5.8775 | 4.5224 | 3.2881 | 2.1638 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.6979 | 8.3093 | 8.042 | 7.6715 | 7.3183 | 5.875 | 4.0714 | 2.8633 | 1.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.6979 | 8.4755 | 8.3734 | 8.2237 | 8.0247 | 7.5463 | 6.7146 | 6.4657 | 5.7591 | 3.1682 | 1.267 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.5987 | 6.2564 | 5.7001 | 5.3033 | 4.7301 | 3.3102 | 2.0946 | 0.94052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.5987 | 6.1983 | 5.5807 | 5.1003 | 4.2602 | 3.3802 | 1.89 | 0.40405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.5987 | 6.4613 | 6.3013 | 6.133 | 5.7856 | 5.4212 | 5.0405 | 4.5427 | 3.7276 | 2.6703 | 1.5742 | 0.42728 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.5987 | 6.0345 | 5.4189 | 4.6721 | 3.8392 | 2.1218 | 0.68436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.5987 | 6.3765 | 6.0716 | 5.7623 | 5.3141 | 4.86 | 4.3403 | 3.6303 | 2.2469 | 0.87773 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.5634 | 5.4276 | 5.0984 | 4.5054 | 3.6252 | 2.6841 | 1.6382 | 0.35422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.5634 | 5.2545 | 4.7622 | 3.9345 | 2.7234 | 1.573 | 0.19635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.5634 | 5.4878 | 5.381 | 4.9215 | 4.2772 | 3.5241 | 2.8692 | 2.0203 | 0.85395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.5634 | 5.041 | 4.4597 | 3.2734 | 2.0473 | 0.55099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.5634 | 5.4519 | 5.2515 | 4.6023 | 3.7678 | 2.9221 | 2.0589 | 0.74234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.7675 | 10.6879 | 10.5127 | 10.3725 | 10.1161 | 9.8043 | 9.0794 | 8.4614 | 7.7291 | 6.6717 | 6.1607 | 5.357 | 2.2588 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.7675 | 10.629 | 10.4002 | 10.1787 | 9.6676 | 9.1375 | 8.1687 | 7.2917 | 6.3483 | 4.8201 | 0.33353 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.7675 | 10.7804 | 10.749 | 10.6765 | 10.5012 | 10.3319 | 10.1588 | 9.9881 | 9.8171 | 9.5099 | 9.2357 | 8.9624 | 8.7001 | 8.4723 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.7675 | 10.5134 | 10.2374 | 9.8222 | 9.2931 | 7.9854 | 7.028 | 6.0504 | 5.0549 | 1.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.7675 | 10.76 | 10.6965 | 10.5678 | 10.3701 | 10.1289 | 9.8802 | 9.6226 | 9.3289 | 9.0266 | 8.372 | 7.7923 | 7.2772 | 6.0975 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.8503 | 7.8159 | 7.7133 | 7.6923 | 7.5623 | 7.336 | 6.4837 | 5.9037 | 5.1584 | 4.0733 | 3.4504 | 3.0356 | 2.2223 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.8503 | 7.7539 | 7.6007 | 7.4824 | 7.123 | 6.7359 | 5.6582 | 4.8695 | 3.953 | 2.405 | 0.33076 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.8503 | 7.9078 | 7.9543 | 7.9913 | 7.9492 | 7.8703 | 7.6013 | 7.485 | 7.352 | 7.1151 | 6.8465 | 6.5773 | 6.3064 | 6.0405 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.8503 | 7.6189 | 7.3958 | 7.1011 | 6.7383 | 5.6424 | 4.5794 | 3.6813 | 2.7037 | 1.3618 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.8503 | 7.8878 | 7.9261 | 7.9171 | 7.8838 | 7.7906 | 7.4431 | 7.2642 | 7.0574 | 6.7891 | 6.1327 | 5.4761 | 4.8856 | 4.3978 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 22.6385 | 21.4484 | 20.2791 | 19.286 | 16.7973 | 13.7438 | 7.8421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 22.6385 | 21.2861 | 20.0027 | 18.7587 | 15.9784 | 12.827 | 1.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 22.6385 | 22.1018 | 21.8584 | 21.3692 | 19.935 | 17.8169 | 15.3859 | 14.3289 | 13.1995 | 9.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 22.6385 | 20.9144 | 19.5868 | 17.6632 | 14.8825 | 7.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 22.6385 | 21.7541 | 21.2348 | 20.4038 | 18.4812 | 15.4427 | 11.925 | 10.5391 | 6.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 100.353 | 97.3064 | 92.0311 | 89.0627 | 74.5852 | 52.2913 | 23.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 100.353 | 97.2165 | 91.8941 | 86.4545 | 63.112 | 38.3549 | 1.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 100.353 | 98.4896 | 95.4941 | 93.0813 | 90.5342 | 84.7373 | 69.7903 | 52.8402 | 36.2544 | 9.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 100.353 | 96.4682 | 91.2301 | 75.4708 | 53.3032 | 16.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 100.353 | 97.6732 | 93.0628 | 90.2753 | 86.9109 | 74.0134 | 57.3382 | 35.0026 | 6.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.1821 | 12.6787 | 12.586 | 12.4309 | 12.2494 | 11.947 | 11.3983 | 11.2064 | 10.9983 | 10.2491 | 9.4994 | 8.9095 | 8.4942 | 8.3828 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.1821 | 12.6586 | 12.5493 | 12.3616 | 12.1252 | 11.7976 | 11.2134 | 10.962 | 10.6897 | 9.8484 | 9.0205 | 8.3565 | 1.6891 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.1821 | 12.859 | 12.8911 | 12.8121 | 12.7631 | 12.6144 | 12.3381 | 12.249 | 12.1455 | 11.7515 | 11.308 | 10.8184 | 10.2866 | 9.9438 | 3.3416 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.1821 | 12.5461 | 12.4125 | 12.074 | 11.8421 | 11.4218 | 10.837 | 10.5194 | 10.2494 | 9.6147 | 9.033 | 8.5237 | 8.0693 | 6.8112 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.1821 | 12.7298 | 12.7225 | 12.5927 | 12.5348 | 12.3506 | 11.9873 | 11.8656 | 11.7359 | 11.1849 | 10.5031 | 9.8798 | 9.5057 | 9.4973 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 100.353 | 97.3064 | 92.0311 | 89.0627 | 74.5852 | 52.2913 | 23.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 100.353 | 97.2165 | 91.8941 | 86.4545 | 63.112 | 38.3549 | 1.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 100.353 | 98.4896 | 95.4941 | 93.0813 | 90.5342 | 84.7373 | 69.7903 | 52.8402 | 36.2544 | 9.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 100.353 | 96.4682 | 91.2301 | 75.4708 | 53.3032 | 16.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 100.353 | 97.6732 | 93.0628 | 90.2753 | 86.9109 | 74.0134 | 57.3382 | 35.0026 | 6.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.9873 | 20.7698 | 19.6983 | 18.7182 | 17.2531 | 15.9514 | 14.4659 | 12.8918 | 11.3217 | 9.6443 | 8.7296 | 8.0757 | 7.4218 | 7.0072 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.9873 | 20.7413 | 19.6602 | 18.6299 | 17.0729 | 15.7184 | 14.151 | 12.4545 | 10.7558 | 8.8909 | 7.8315 | 7.0394 | 1.6793 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.9873 | 20.9331 | 20.3678 | 19.5584 | 18.6536 | 17.6802 | 16.7662 | 15.8322 | 14.9024 | 13.831 | 12.9776 | 12.103 | 11.2811 | 10.596 | 3.3223 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.9873 | 20.6045 | 19.5272 | 18.1435 | 16.5204 | 14.7232 | 13.1004 | 11.279 | 9.7514 | 8.3082 | 7.5142 | 7.0194 | 6.7705 | 6.6789 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.9873 | 20.882 | 20.0341 | 19.1188 | 17.922 | 16.9468 | 15.8375 | 14.4933 | 13.2138 | 12.0426 | 11.3962 | 10.7885 | 10.3019 | 10.1402 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.8423 | 7.7045 | 7.3805 | 7.1603 | 6.7948 | 6.3404 | 5.7419 | 4.3926 | 3.2207 | 2.4024 | 1.7943 | 1.441 | 1.2931 | 1.3248 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.8423 | 7.6492 | 7.2801 | 6.982 | 6.3144 | 5.6037 | 4.7172 | 3.0181 | 1.5106 | 0.031897 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.8423 | 7.8223 | 7.7877 | 7.7142 | 7.4852 | 7.2583 | 6.9909 | 6.1502 | 5.4076 | 4.5609 | 3.725 | 2.8157 | 1.9862 | 1.2488 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.8423 | 7.4933 | 7.0917 | 6.5366 | 5.8478 | 5.0974 | 4.2501 | 2.4136 | 0.91393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.8423 | 7.8541 | 7.7975 | 7.6633 | 7.4347 | 7.1493 | 6.8136 | 5.4686 | 4.3939 | 3.5702 | 2.6816 | 1.8366 | 1.3268 | 1.1785 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 28.82 | 27.8718 | 26.1273 | 24.8165 | 22.6951 | 18.2461 | 12.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 28.82 | 27.6912 | 25.6854 | 24.1072 | 19.9595 | 15.0541 | 0.74354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 28.82 | 28.6563 | 28.4679 | 28.1418 | 25.9517 | 23.4803 | 20.842 | 16.3613 | 13.0324 | 4.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 28.82 | 26.9444 | 24.9231 | 22.131 | 18.6745 | 8.5517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 28.82 | 28.5952 | 28.1263 | 27.4013 | 25.9873 | 24.4839 | 22.7002 | 17.698 | 3.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.7561 | 3.6464 | 3.4862 | 3.3883 | 3.3373 | 3.276 | 3.1966 | 3.1301 | 2.9904 | 2.8897 | 2.8472 | 2.8716 | 2.2042 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.7561 | 3.5777 | 3.3627 | 3.2022 | 3.0986 | 3.0199 | 2.8974 | 2.8055 | 2.6845 | 2.537 | 0.32546 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.7561 | 3.6772 | 3.597 | 3.5184 | 3.4656 | 3.4186 | 3.3781 | 3.3408 | 3.2894 | 3.1807 | 3.0882 | 2.9734 | 2.8745 | 2.7839 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.7561 | 3.5371 | 3.3344 | 3.1079 | 3.0158 | 2.9335 | 2.8403 | 2.7031 | 2.5204 | 1.7128 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.7561 | 3.6119 | 3.4502 | 3.3309 | 3.247 | 3.1898 | 3.1307 | 3.06 | 2.9684 | 2.8514 | 2.7303 | 2.6275 | 2.5486 | 2.5367 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.8743 | 2.7947 | 2.6842 | 2.5752 | 2.4219 | 2.3056 | 2.1764 | 2.0392 | 1.8634 | 1.7143 | 1.5964 | 1.535 | 1.502 | 1.497 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.8743 | 2.8062 | 2.6722 | 2.576 | 2.1428 | 1.5564 | 0.92417 | 0.15635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.8743 | 2.8529 | 2.8256 | 2.7976 | 2.3761 | 1.887 | 1.3864 | 0.87343 | 0.80829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.8743 | 2.777 | 2.6755 | 2.5331 | 2.362 | 2.2166 | 2.0617 | 1.8844 | 1.6807 | 1.5391 | 1.4164 | 1.3426 | 1.3045 | 1.2886 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.8743 | 2.8352 | 2.78 | 2.7335 | 2.6258 | 2.5669 | 2.4959 | 2.3902 | 2.2485 | 2.1131 | 1.983 | 1.845 | 1.733 | 1.6722 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.7293 | 12.7723 | 12.8039 | 12.8409 | 12.8735 | 12.8866 | 12.6549 | 12.5168 | 11.8136 | 11.6451 | 11.6091 | 11.5932 | 11.5836 | 11.6174 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.7293 | 12.7661 | 12.7997 | 12.8259 | 12.8278 | 12.8152 | 12.559 | 12.3886 | 11.6561 | 11.4182 | 11.3157 | 10.3742 | 1.3366 | 0 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.7293 | 12.7835 | 12.8348 | 12.8882 | 12.9274 | 12.9641 | 12.8256 | 12.7608 | 12.4052 | 12.2414 | 12.1192 | 11.9932 | 11.8562 | 11.7295 | 2.6443 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.7293 | 12.7541 | 12.774 | 12.7781 | 12.7642 | 12.7403 | 12.4515 | 12.2552 | 11.6108 | 11.4354 | 11.3583 | 11.2536 | 8.9537 | 5.3899 | 0 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.7293 | 12.7819 | 12.8301 | 12.8762 | 12.9161 | 12.9383 | 12.7335 | 12.5915 | 11.9019 | 11.738 | 11.6813 | 11.6381 | 11.5869 | 11.6089 | 0 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.4733 | 11.9767 | 11.3135 | 11.3779 | 11.4159 | 11.4554 | 11.0169 | 10.6638 | 10.2906 | 9.5156 | 9.1025 | 8.7057 | 7.9697 | 7.2333 | 0 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.4733 | 11.9722 | 11.3059 | 11.3631 | 11.3933 | 11.4318 | 10.9869 | 10.6272 | 10.2467 | 9.4576 | 9.0333 | 8.6316 | 1.676 | 0 | 0 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.4733 | 12.128 | 11.7044 | 11.7716 | 11.8184 | 11.8641 | 11.8378 | 11.8347 | 11.8293 | 11.796 | 11.7662 | 11.7248 | 11.6916 | 11.6671 | 3.3156 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.4733 | 11.9319 | 11.3088 | 11.3153 | 11.3325 | 10.6627 | 10.2261 | 9.8349 | 9.4582 | 8.6898 | 8.289 | 7.5445 | 6.808 | 6.0934 | 0 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.4733 | 11.9925 | 11.3598 | 11.4286 | 11.4957 | 11.5483 | 11.5104 | 11.5288 | 11.5347 | 11.5184 | 11.1412 | 10.7621 | 10.4021 | 10.0555 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.5439 | 6.2045 | 5.6528 | 5.2593 | 4.6908 | 3.2827 | 2.0772 | 0.93271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.5439 | 6.1469 | 5.5344 | 5.058 | 4.2248 | 3.3522 | 1.8743 | 0.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.5439 | 6.4077 | 6.2489 | 6.082 | 5.7376 | 5.3762 | 4.9987 | 4.505 | 3.6967 | 2.6482 | 1.5611 | 0.42374 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.5439 | 5.9844 | 5.3739 | 4.6334 | 3.8073 | 2.1041 | 0.67868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.5439 | 6.3236 | 6.0212 | 5.7144 | 5.2699 | 4.8196 | 4.3043 | 3.6002 | 2.2282 | 0.87044 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.2292 | 6.9456 | 6.4389 | 6.0513 | 5.6035 | 5.2398 | 4.7887 | 4.3015 | 3.7332 | 2.6879 | 1.4035 | 0.42082 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.2292 | 6.9117 | 6.3582 | 5.9085 | 5.3867 | 4.9923 | 4.4832 | 3.9223 | 2.9285 | 1.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.2292 | 7.0525 | 6.7689 | 6.5073 | 6.1919 | 5.9765 | 5.7435 | 5.4377 | 5.1191 | 4.5888 | 4.133 | 3.6546 | 2.9777 | 2.1801 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.2292 | 6.8442 | 6.306 | 5.7322 | 5.2361 | 4.8063 | 4.3334 | 3.6991 | 2.3429 | 0.77239 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.2292 | 6.9639 | 6.5301 | 6.1586 | 5.7514 | 5.4522 | 5.1454 | 4.7147 | 4.242 | 3.5559 | 2.6958 | 1.4695 | 0.69499 | 0.27917 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.2817 | 5.9559 | 5.4264 | 5.0486 | 4.5029 | 3.1512 | 1.994 | 0.89534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.2817 | 5.9006 | 5.3127 | 4.8554 | 4.0556 | 3.2179 | 1.7992 | 0.38465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.2817 | 6.151 | 5.9986 | 5.8384 | 5.5078 | 5.1608 | 4.7984 | 4.3245 | 3.5486 | 2.5421 | 1.4986 | 0.40676 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.2817 | 5.7446 | 5.1586 | 4.4478 | 3.6548 | 2.0199 | 0.65149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.2817 | 6.0703 | 5.78 | 5.4855 | 5.0588 | 4.6265 | 4.1318 | 3.4559 | 2.139 | 0.83558 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.32765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.32765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.32765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.32765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.32765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.8612 | 10.7725 | 10.5644 | 10.4408 | 10.2526 | 10.0018 | 9.7067 | 9.5389 | 9.2523 | 9.0015 | 8.9084 | 9.036 | 9.1431 | 9.3453 | 7.2989 | 5.6428 | 4.1702
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.8612 | 10.7382 | 10.4992 | 10.3276 | 9.8882 | 9.4481 | 8.9107 | 8.4882 | 7.933 | 7.1836 | 6.6673 | 6.357 | 6.0752 | 5.8932 | 2.5477 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.8612 | 10.8794 | 10.8607 | 10.8411 | 10.746 | 10.6503 | 10.5448 | 10.4192 | 10.2623 | 9.9865 | 9.7138 | 9.4168 | 9.1343 | 8.9087 | 5.5454 | 2.0147 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.8612 | 10.6306 | 10.3684 | 10.0158 | 9.5856 | 9.0885 | 8.5825 | 8.0313 | 7.4684 | 6.9391 | 6.5388 | 6.3094 | 6.2092 | 6.2441 | 4.2226 | 3.3008 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.8612 | 10.8509 | 10.7965 | 10.715 | 10.6071 | 10.4666 | 10.3062 | 10.1011 | 9.8311 | 9.5685 | 9.2852 | 9.0408 | 8.892 | 8.8975 | 4.8113 | 2.9547 | 1.8929
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 74.4361 | 72.1891 | 71.2527 | 70.4783 | 68.2722 | 60.6812 | 54.3344 | 49.4211 | 42.5996 | 34.6218 | 29.2447 | 25.378 | 21.8288 | 18.928 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 74.4361 | 72.0834 | 71.0181 | 70.0977 | 64.118 | 58.0151 | 49.4857 | 41.9481 | 32.1672 | 19.1155 | 9.5018 | 2.2888 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 74.4361 | 73.16 | 73.0921 | 72.8378 | 72.0627 | 71.1878 | 70.3335 | 68.9984 | 66.2356 | 61.9642 | 57.5642 | 52.8289 | 48.3954 | 44.0248 | 1.5165 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 74.4361 | 71.5252 | 70.2896 | 66.4087 | 60.1138 | 50.0089 | 41.5705 | 32.5642 | 22.7551 | 12.4423 | 4.1687 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 74.4361 | 72.5536 | 72.314 | 71.852 | 71.0264 | 69.1212 | 66.0152 | 62.8433 | 57.9326 | 51.4522 | 44.2219 | 37.9871 | 32.9616 | 30.4546 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 34.3031 | 34.2713 | 34.2108 | 34.0696 | 33.9318 | 33.5407 | 33.2907 | 33.0711 | 32.7674 | 32.4456 | 32.2811 | 32.1316 | 31.98 | 31.8435 | 30.8239 | 30.4248 | 30.3701
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 34.3031 | 34.2559 | 34.1906 | 34.0354 | 33.8402 | 33.6042 | 33.3046 | 33.0038 | 32.595 | 32.1209 | 31.811 | 31.5504 | 31.218 | 30.9239 | 29.4759 | 29.0199 | 29.1345
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 34.3031 | 34.2953 | 34.3004 | 34.2097 | 34.1328 | 33.989 | 33.8918 | 33.7877 | 33.64 | 33.4842 | 33.3546 | 33.2186 | 33.0839 | 32.957 | 31.9139 | 30.9359 | 30.3596
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 34.3031 | 34.2148 | 34.118 | 33.8927 | 33.6969 | 33.2454 | 32.9435 | 32.6096 | 32.2143 | 31.7978 | 31.5115 | 31.2243 | 31.0025 | 30.7993 | 29.6903 | 29.4878 | 29.6041
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 34.3031 | 34.2962 | 34.2862 | 34.158 | 34.0517 | 33.8964 | 33.7756 | 33.6354 | 33.4164 | 33.2266 | 33.0129 | 32.8078 | 32.6107 | 32.4666 | 31.3221 | 31.11 | 31.0832
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.0171 | 9.7769 | 9.404 | 9.2244 | 8.7391 | 7.7204 | 6.9749 | 6.3292 | 5.1379 | 3.0281 | 1.6059 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.0171 | 9.5247 | 8.933 | 8.4602 | 7.6575 | 6.802 | 5.6685 | 4.687 | 3.1894 | 0.84683 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.0171 | 9.899 | 9.8062 | 9.7344 | 9.3532 | 8.9822 | 8.662 | 8.3461 | 7.8731 | 7.2277 | 6.6314 | 6.0046 | 5.3925 | 4.8261 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.0171 | 9.3199 | 8.6935 | 7.9456 | 7.2042 | 5.8755 | 4.8307 | 3.6733 | 1.7101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.0171 | 9.7417 | 9.4797 | 9.2115 | 8.7787 | 8.1214 | 7.6764 | 7.2045 | 6.3305 | 5.3687 | 4.4773 | 3.6543 | 2.9774 | 1.9754 | 0 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.2252 | 17.1309 | 16.8729 | 16.7707 | 16.5163 | 15.5015 | 14.7975 | 14.2761 | 13.555 | 12.4851 | 11.94 | 11.2829 | 10.6248 | 10.0375 | 4.9701 | 2.5367 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.2252 | 17.0444 | 16.7199 | 16.4651 | 15.9258 | 15.358 | 14.3302 | 13.4491 | 12.3782 | 10.7507 | 9.7138 | 8.9171 | 7.748 | 6.7002 | 0 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.2252 | 17.2256 | 17.2021 | 17.1703 | 17.0202 | 16.885 | 16.7601 | 16.6202 | 16.4245 | 16.0827 | 15.7462 | 15.3607 | 14.9907 | 14.6583 | 9.83 | 5.0711 | 1.6727
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.2252 | 16.9433 | 16.5804 | 16.1224 | 15.572 | 14.2414 | 13.2746 | 12.2767 | 11.1699 | 9.793 | 8.8907 | 7.7543 | 6.8055 | 6.0159 | 0.46152 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.2252 | 17.224 | 17.1484 | 17.0526 | 16.8756 | 16.6761 | 16.4867 | 16.2169 | 15.8684 | 15.5203 | 14.7745 | 14.0687 | 13.4389 | 13.0019 | 7.4821 | 5.4051 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.32647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.32647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.32647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.32647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.32647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 0.33039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 0.33039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 0.33039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 0.33039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 0.33039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.4535 | 14.2106 | 13.9753 | 13.9005 | 13.7783 | 12.8936 | 12.331 | 11.8578 | 11.27 | 10.3384 | 9.9107 | 9.3034 | 8.6899 | 8.1518 | 3.9782 | 0.65556 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.4535 | 14.1654 | 13.8933 | 13.7115 | 13.3041 | 12.9208 | 12.1197 | 11.3751 | 10.5207 | 9.1338 | 8.2954 | 7.6362 | 6.6499 | 5.7492 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.4535 | 14.2996 | 14.2244 | 14.1775 | 14.0883 | 13.9932 | 13.8759 | 13.7444 | 13.616 | 13.3457 | 13.0805 | 12.8084 | 12.5447 | 11.9613 | 7.7809 | 3.775 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.4535 | 14.0444 | 13.7511 | 13.416 | 13.0195 | 11.8824 | 11.1006 | 10.2439 | 9.3646 | 8.1898 | 7.479 | 6.5251 | 5.6696 | 4.9219 | 0.050692 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.4535 | 14.2496 | 14.1199 | 14.0135 | 13.8991 | 13.7811 | 13.4305 | 13.245 | 12.6488 | 11.7237 | 10.5623 | 10.0142 | 9.5356 | 9.2054 | 3.276 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.2182 | 10.0572 | 9.7712 | 9.591 | 9.0124 | 8.4717 | 7.4637 | 5.8942 | 4.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.2182 | 10.0258 | 9.7133 | 9.4745 | 8.8231 | 8.2451 | 7.1814 | 5.5276 | 3.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.2182 | 10.2102 | 10.1655 | 10.0856 | 9.7629 | 9.415 | 9.0735 | 8.3626 | 7.6734 | 6.8146 | 5.9224 | 5.1227 | 4.4031 | 3.7105 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.2182 | 9.9574 | 9.6557 | 9.252 | 8.5972 | 7.1998 | 6.1562 | 3.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.2182 | 10.1417 | 10.0359 | 9.8915 | 9.4391 | 8.8657 | 8.4165 | 7.2791 | 6.1987 | 4.5898 | 3.0427 | 2.029 | 1.2482 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.0512 | 8.0312 | 7.9727 | 7.9385 | 7.818 | 7.6513 | 7.4424 | 7.2917 | 5.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.0512 | 8.0231 | 7.9645 | 7.9141 | 7.7703 | 7.5917 | 7.3671 | 7.1951 | 3.3502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.0512 | 8.0907 | 8.1031 | 8.1174 | 8.0921 | 8.069 | 8.0162 | 7.9522 | 7.8796 | 7.7608 | 7.6316 | 7.4815 | 7.3317 | 6.8618 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.0512 | 7.987 | 7.9186 | 7.8007 | 7.6486 | 7.4844 | 7.2876 | 3.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.0512 | 8.0846 | 8.0896 | 8.0852 | 8.0511 | 8.0012 | 7.9479 | 7.8643 | 7.7567 | 7.639 | 6.6843 | 3.9811 | 1.693 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.6401 | 5.6592 | 5.1863 | 5.2431 | 5.1761 | 5.0475 | 4.7716 | 4.6389 | 4.4708 | 4.208 | 4.2169 | 4.515 | 4.7915 | 5.1722 | 3.7547 | 2.7063 | 1.8687
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.6401 | 5.619 | 5.1168 | 5.0687 | 4.6195 | 4.1597 | 3.527 | 2.9408 | 2.2889 | 1.3492 | 0.71202 | 0.35275 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.6401 | 5.7917 | 5.6549 | 5.7553 | 5.753 | 5.7488 | 5.6782 | 5.5587 | 5.4455 | 5.156 | 4.8677 | 4.5616 | 4.2505 | 4.0152 | 0.74976 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.6401 | 5.478 | 4.9447 | 4.6533 | 4.2052 | 3.7162 | 3.1094 | 2.3804 | 1.742 | 1.0653 | 0.57529 | 0.29004 | 0.21124 | 0.31547 | 0 | 0 | 0
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.6401 | 5.789 | 5.5192 | 5.6035 | 5.6431 | 5.6303 | 5.5134 | 5.291 | 5.0774 | 4.8381 | 4.5855 | 4.3646 | 4.257 | 4.3746 | 0.39132 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.3153 | 10.2232 | 9.828 | 9.6579 | 9.3286 | 8.9718 | 7.9318 | 6.9776 | 5.688 | 2.2109 | 1.1068 | 0.21504 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.3153 | 10.1491 | 9.6716 | 9.3453 | 8.7629 | 8.1864 | 6.9152 | 5.7253 | 4.1705 | 0.26677 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.3153 | 10.3026 | 10.0894 | 9.9449 | 9.6272 | 9.3496 | 8.8477 | 8.3853 | 7.7824 | 6.1382 | 5.2551 | 4.3131 | 3.3286 | 2.0017 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.3153 | 10.0452 | 9.5199 | 8.9994 | 8.3806 | 7.0602 | 5.7729 | 4.2738 | 2.8234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.3153 | 10.288 | 9.9876 | 9.7506 | 9.3832 | 9.055 | 8.4266 | 7.7558 | 6.466 | 2.967 | 1.6498 | 0.40722 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.6009 | 7.5938 | 7.5292 | 7.4044 | 7.2262 | 6.8111 | 6.0929 | 5.4754 | 4.9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.6009 | 7.5736 | 7.499 | 7.3349 | 7.1022 | 6.6532 | 5.8842 | 5.1896 | 3.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.6009 | 7.6726 | 7.7088 | 7.6411 | 7.5917 | 7.3014 | 6.8907 | 6.5315 | 6.2512 | 5.9325 | 5.6141 | 5.2811 | 4.9431 | 4.6109 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.6009 | 7.5128 | 7.4241 | 7.1307 | 6.9029 | 6.2918 | 5.4998 | 3.5666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.6009 | 7.6558 | 7.6755 | 7.5821 | 7.4967 | 7.1818 | 6.6423 | 6.0934 | 5.6709 | 5.3584 | 5.0491 | 4.0563 | 1.725 | 0 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.7084 | 8.6752 | 8.5037 | 8.5103 | 8.3706 | 8.1622 | 7.4911 | 7.0433 | 6.5209 | 5.7014 | 5.4884 | 5.5543 | 5.2249 | 4.9898 | 1.2416 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.7084 | 8.631 | 8.4351 | 8.3235 | 7.8511 | 7.36 | 6.366 | 5.5367 | 4.6056 | 3.2409 | 2.4867 | 1.9951 | 1.1423 | 0.42109 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.7084 | 8.8188 | 8.9057 | 8.9645 | 8.9264 | 8.8682 | 8.7876 | 8.6722 | 8.5125 | 8.2506 | 7.9839 | 7.6968 | 7.432 | 7.235 | 3.2208 | 0.018537 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.7084 | 8.5234 | 8.3224 | 7.9922 | 7.5636 | 6.3285 | 5.4045 | 4.4475 | 3.5636 | 2.4201 | 1.7995 | 1.0149 | 0.40353 | 0 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.7084 | 8.8377 | 8.9254 | 8.9661 | 8.9589 | 8.8915 | 8.7663 | 8.6027 | 8.3753 | 8.1984 | 7.6364 | 7.1246 | 6.7396 | 6.5567 | 2.5301 | 1.3106 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 75.2652 | 75.2401 | 69.085 | 62.5952 | 54.4886 | 53.4401 | 52.4215 | 51.6462 | 49.8465 | 48.0393 | 46.181 | 44.7385 | 42.7109 | 40.8228 | 32.1767 | 28.2164 | 28.9492
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 75.2652 | 75.0338 | 68.69 | 61.6323 | 52.8753 | 51.4714 | 50.0566 | 48.8114 | 46.5246 | 43.9021 | 41.2795 | 39.1266 | 36.375 | 33.8216 | 21.5891 | 16.1365 | 13.537
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 75.2652 | 75.3919 | 75.307 | 75.2184 | 75.0397 | 74.9521 | 74.7647 | 74.5 | 74.1377 | 73.701 | 73.2765 | 72.4232 | 71.5435 | 70.7076 | 63.7746 | 57.0508 | 52.0223
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 75.2652 | 74.7215 | 73.7605 | 72.6141 | 71.8287 | 70.4583 | 69.0304 | 67.6167 | 66.2025 | 64.3821 | 62.9909 | 61.4426 | 60.1221 | 58.4519 | 51.2726 | 49.4312 | 49.9982
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 75.2652 | 75.4205 | 75.2968 | 74.9692 | 74.8753 | 74.9074 | 74.7825 | 73.9356 | 73.1808 | 71.9818 | 71.0387 | 70.1049 | 69.2231 | 68.1977 | 59.9252 | 58.2317 | 57.1599
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 60.7962 | 59.3197 | 54.4655 | 49.4676 | 27.7243 | 20.2308 | 9.9638 | 3.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 60.7962 | 58.6616 | 53.1911 | 46.8081 | 13.5069 | 0.38307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 60.7962 | 61.2103 | 60.1441 | 56.6444 | 55.0241 | 53.7022 | 51.9272 | 49.6346 | 46.5874 | 41.5638 | 36.5048 | 31.0711 | 25.6326 | 21.2302 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 60.7962 | 56.7523 | 50.6817 | 40.4354 | 32.9489 | 22.2293 | 12.1325 | 1.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 60.7962 | 61.1246 | 59.1762 | 54.7551 | 53.4005 | 51.9633 | 49.6511 | 46.4029 | 41.516 | 37.0515 | 30.4828 | 24.6036 | 20.9263 | 20.3643 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.7747 | 13.7345 | 13.5882 | 13.5953 | 13.5474 | 13.4711 | 13.3292 | 13.2329 | 13.1079 | 12.7805 | 12.6779 | 12.6537 | 12.6017 | 12.555 | 12.2233 | 12.3369 | 12.8816
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.7747 | 13.7014 | 13.4769 | 13.3723 | 13.1898 | 13.0159 | 12.7557 | 12.5378 | 12.3154 | 11.8449 | 11.6287 | 11.4995 | 11.3251 | 11.169 | 10.2345 | 10.0282 | 10.382
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.7747 | 13.781 | 13.719 | 13.7225 | 13.688 | 13.6688 | 13.6404 | 13.6103 | 13.5816 | 13.4564 | 13.3915 | 13.3111 | 13.2288 | 13.1569 | 12.0384 | 10.6859 | 10.0422
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.7747 | 13.6171 | 13.3445 | 13.1399 | 12.946 | 12.7438 | 12.5313 | 12.3086 | 12.1233 | 11.7823 | 11.6085 | 11.4579 | 11.3553 | 11.31 | 10.787 | 11.003 | 11.5428
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.7747 | 13.7813 | 13.6483 | 13.6039 | 13.5802 | 13.54 | 13.4858 | 13.4291 | 13.3908 | 13.158 | 13.0771 | 12.9747 | 12.8861 | 12.8356 | 11.3651 | 11.1403 | 11.3586
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.1878 | 8.1803 | 8.1106 | 7.9762 | 7.7842 | 7.3371 | 6.5635 | 5.8983 | 4.9909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.1878 | 8.1584 | 8.0781 | 7.9014 | 7.6507 | 7.1669 | 6.3386 | 5.5903 | 3.3145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.1878 | 8.265 | 8.304 | 8.2311 | 8.178 | 7.8652 | 7.4228 | 7.0359 | 6.7339 | 6.3906 | 6.0476 | 5.6889 | 5.3248 | 4.967 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.1878 | 8.093 | 7.9974 | 7.6814 | 7.436 | 6.7776 | 5.9245 | 3.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.1878 | 8.247 | 8.2683 | 8.1676 | 8.0757 | 7.7364 | 7.1552 | 6.5639 | 6.1089 | 5.7722 | 5.439 | 3.9387 | 1.675 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.0666 | 10.9547 | 10.8235 | 10.7868 | 10.7289 | 10.645 | 10.5507 | 10.5211 | 10.3981 | 10.339 | 10.3486 | 10.4497 | 10.5326 | 10.6735 | 10.1383 | 9.7011 | 9.1256
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.0666 | 10.9346 | 10.7906 | 10.705 | 10.5252 | 10.3488 | 10.1433 | 9.9773 | 9.7362 | 9.4713 | 9.2878 | 9.1865 | 9.0862 | 9.0553 | 7.6661 | 7.0915 | 6.8311
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.0666 | 11.0003 | 10.9629 | 10.9349 | 10.8795 | 10.8269 | 10.7668 | 10.692 | 10.6217 | 10.507 | 10.3951 | 10.285 | 10.1765 | 10.0996 | 9.0212 | 8.2687 | 7.3683
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.0666 | 10.8767 | 10.7161 | 10.557 | 10.3943 | 10.2052 | 10.008 | 9.8089 | 9.5511 | 9.37 | 9.2401 | 9.1724 | 9.1599 | 9.1934 | 8.3567 | 7.9963 | 7.3477
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.0666 | 10.9866 | 10.933 | 10.887 | 10.8427 | 10.7848 | 10.7204 | 10.63 | 10.5145 | 10.4453 | 10.3525 | 10.2783 | 10.2372 | 10.2734 | 9.239 | 8.8235 | 8.1575
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.6098 | 14.6765 | 14.7371 | 14.8048 | 14.8569 | 14.9 | 13.2566 | 9.3348 | 5.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.6098 | 14.6687 | 14.7224 | 14.7809 | 14.8262 | 14.8679 | 12.2668 | 7.9969 | 3.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.6098 | 14.6854 | 14.7645 | 14.8401 | 14.8966 | 14.9561 | 15.0176 | 15.0708 | 15.1251 | 14.3123 | 12.389 | 10.5089 | 8.7112 | 7.0167 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.6098 | 14.6589 | 14.7138 | 14.7508 | 14.7926 | 12.5674 | 8.3741 | 3.5794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.6098 | 14.678 | 14.7471 | 14.8138 | 14.8664 | 14.9203 | 14.9745 | 15.0143 | 12.9129 | 10.2016 | 6.8352 | 4.071 | 1.7312 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.95074 | 0.62016 | 0.11244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.95074 | 0.54433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.95074 | 0.80685 | 0.62054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.95074 | 0.33112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.95074 | 0.77201 | 0.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.1981 | 16.1048 | 15.7696 | 15.784 | 15.7519 | 15.7209 | 15.6532 | 14.9759 | 13.5457 | 10.0395 | 8.9551 | 8.1959 | 7.2243 | 6.3487 | 0.4147 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.1981 | 16.0552 | 15.6735 | 15.627 | 15.5601 | 15.5121 | 14.0904 | 12.7826 | 10.9367 | 6.8913 | 5.3065 | 4.0807 | 2.6813 | 1.4222 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.1981 | 16.1382 | 15.9365 | 15.9507 | 15.9038 | 15.8733 | 15.8306 | 15.7699 | 15.7155 | 14.1044 | 13.0745 | 11.9606 | 10.8041 | 9.3224 | 2.2015 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.1981 | 16.0279 | 15.6739 | 15.5813 | 15.5069 | 14.2129 | 12.7567 | 11.067 | 9.2001 | 5.8248 | 4.6787 | 3.3401 | 2.163 | 1.0216 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.1981 | 16.0753 | 15.7449 | 15.7172 | 15.6458 | 15.5837 | 15.304 | 14.9625 | 13.4427 | 9.7796 | 7.6819 | 6.2488 | 5.1125 | 4.2775 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.6185 | 14.5111 | 14.3227 | 14.215 | 13.9111 | 13.372 | 12.2951 | 9.3375 | 5.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.6185 | 14.4916 | 14.2943 | 14.151 | 13.7719 | 13.1917 | 12.0376 | 7.9993 | 3.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.6185 | 14.6192 | 14.6096 | 14.6003 | 14.5143 | 14.2826 | 13.9944 | 13.6784 | 13.3175 | 12.8983 | 12.3927 | 10.512 | 8.7137 | 7.0188 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.6185 | 14.3599 | 14.1484 | 13.8183 | 13.4328 | 12.0587 | 8.3766 | 3.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.6185 | 14.6058 | 14.5998 | 14.5533 | 14.4586 | 14.168 | 13.7978 | 13.3568 | 12.8723 | 10.2046 | 6.8372 | 4.0721 | 1.7317 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.4741 | 13.4263 | 13.3385 | 13.2925 | 13.137 | 12.9486 | 12.3659 | 9.3594 | 5.1721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.4741 | 13.4187 | 13.3299 | 13.2676 | 13.0801 | 12.8774 | 12.2678 | 8.018 | 3.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.4741 | 13.5038 | 13.5092 | 13.5238 | 13.5069 | 13.4796 | 13.435 | 13.3652 | 13.2907 | 13.1492 | 12.4217 | 10.5366 | 8.7341 | 7.0352 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.4741 | 13.3679 | 13.2611 | 13.1131 | 12.9252 | 11.9955 | 8.3962 | 3.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.4741 | 13.4836 | 13.4742 | 13.4495 | 13.416 | 13.3552 | 13.0669 | 12.9744 | 12.843 | 10.2285 | 6.8532 | 4.0817 | 1.7358 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.5143 | 8.3796 | 8.077 | 7.8472 | 7.6245 | 7.3889 | 7.1438 | 6.9017 | 6.6458 | 5.8419 | 5.5394 | 4.4026 | 3.9443 | 2.4769 | 0 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.5143 | 8.3635 | 8.037 | 7.7769 | 7.4647 | 7.1246 | 6.7303 | 6.2926 | 4.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.5143 | 8.4056 | 8.1965 | 8.0219 | 7.8411 | 7.6619 | 7.4721 | 7.2652 | 7.059 | 6.2958 | 6.0459 | 4.9141 | 4.655 | 3.6052 | 0 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.5143 | 8.3239 | 7.966 | 7.63 | 7.2817 | 6.8957 | 6.2385 | 4.453 | 1.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.5143 | 8.3863 | 8.1032 | 7.8719 | 7.639 | 7.403 | 7.1611 | 6.6255 | 6.3054 | 5.9874 | 5.6048 | 5.2363 | 4.872 | 4.6796 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.6722 | 11.7437 | 11.782 | 11.8961 | 11.9264 | 11.9385 | 11.9476 | 12.0149 | 12.0135 | 10.0248 | 8.942 | 8.1839 | 7.2138 | 6.3394 | 0.41409 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.6722 | 11.6507 | 11.6123 | 11.6139 | 11.5532 | 11.5022 | 11.4002 | 11.3696 | 10.9207 | 6.8813 | 5.2987 | 4.0747 | 2.6773 | 1.4201 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.6722 | 11.7687 | 11.8551 | 11.96 | 11.969 | 11.9604 | 12.0037 | 12.0444 | 12.0738 | 12.0058 | 11.9706 | 11.923 | 10.7883 | 9.3088 | 2.1983 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.6722 | 11.6045 | 11.5534 | 11.4916 | 11.4422 | 11.3464 | 11.2757 | 11.0507 | 9.1866 | 5.8163 | 4.6718 | 3.3352 | 2.1598 | 1.0201 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.6722 | 11.6998 | 11.7247 | 11.7574 | 11.7161 | 11.669 | 11.6542 | 11.6344 | 11.5634 | 9.7653 | 7.6706 | 6.2397 | 5.105 | 4.2712 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.9085 | 11.8591 | 10.9804 | 9.3549 | 8.3955 | 7.6049 | 6.419 | 5.3655 | 4.2832 | 2.7659 | 1.9089 | 1.2842 | 0.66615 | 0.14837 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.9085 | 11.8375 | 10.9371 | 9.4543 | 8.3179 | 7.4619 | 6.1218 | 4.8525 | 3.4027 | 1.3927 | 0.092291 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.9085 | 11.9624 | 11.4655 | 10.208 | 9.5407 | 8.9402 | 8.3414 | 7.8063 | 7.1945 | 6.4179 | 5.7171 | 4.972 | 4.3744 | 3.8782 | 0.66437 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.9085 | 11.7418 | 10.8406 | 8.9765 | 7.7487 | 5.8854 | 4.4967 | 3.1383 | 1.8818 | 0.19216 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.9085 | 11.9516 | 11.1886 | 9.7709 | 8.9023 | 8.3019 | 7.625 | 6.8998 | 6.0631 | 5.1569 | 4.0611 | 3.0321 | 2.4395 | 1.9993 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 18.9947 | 18.5085 | 15.6147 | 15.3964 | 13.9514 | 12.3069 | 7.6075 | 3.6434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 18.9947 | 17.6052 | 13.8394 | 12.2252 | 9.1658 | 6.2423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 18.9947 | 19.0801 | 17.7029 | 17.5577 | 16.0172 | 14.6258 | 12.4509 | 10.3489 | 7.6251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 18.9947 | 16.8649 | 12.9502 | 10.0518 | 6.8535 | 0.55055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 18.9947 | 18.4751 | 15.9408 | 14.9199 | 12.8412 | 10.9298 | 6.9744 | 3.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 22.0863 | 20.8731 | 18.1547 | 16.28 | 10.6596 | 2.8659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 22.0863 | 20.4654 | 17.5122 | 14.8776 | 8.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 22.0863 | 22.9376 | 23.2285 | 22.9494 | 20.9459 | 17.1938 | 12.3734 | 5.9267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 22.0863 | 18.9657 | 15.8269 | 10.3922 | 3.5499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 22.0863 | 22.3645 | 22.1874 | 21.0812 | 18.1723 | 12.7748 | 5.4935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Generation Headroom
Associated GSP Group | Substation | Supply Level | Voltage Level (kV) | Scenario | Units | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.9783 | 14.8831 | 14.8612 | 14.5738 | 14.2682 | 13.9365 | 13.6027 | 13.2512 | 12.9239 | 12.5545 | 12.0051 | 11.434 | 10.7912 | 10.2854 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.9783 | 14.8858 | 14.8705 | 14.5798 | 14.2724 | 13.9306 | 13.5695 | 13.1433 | 12.7164 | 12.2179 | 9.6651 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.9783 | 14.958 | 15.0139 | 15.047 | 15.0635 | 15.068 | 15.0579 | 15.034 | 14.9511 | 14.8051 | 14.5605 | 14.3053 | 13.9676 | 13.7685 | 13.6323 | 13.3064 | 3.5218
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.9783 | 14.8825 | 14.847 | 14.5574 | 14.2505 | 13.9371 | 13.6108 | 13.3049 | 12.9586 | 12.6264 | 12.0633 | 11.4148 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | BANBURY ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.9783 | 14.9401 | 14.9982 | 14.9494 | 14.8527 | 14.6974 | 14.5228 | 14.3101 | 14.0495 | 13.7109 | 13.2121 | 12.7438 | 9.8578 | 3.129 | 0 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 31.9052 | 31.7619 | 31.6321 | 31.3189 | 31.015 | 30.7238 | 30.4493 | 30.1435 | 29.857 | 29.6163 | 27.4559 | 27.3089 | 26.9361 | 26.5746 | 24.8369 | 22.0316 | 13.4392
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 31.9052 | 31.7606 | 31.6271 | 31.3132 | 31.0085 | 30.7084 | 30.4104 | 30.0614 | 29.7252 | 29.5137 | 27.3456 | 26.9435 | 26.3737 | 25.9521 | 23.8601 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 31.9052 | 31.8269 | 31.7814 | 31.7481 | 31.6913 | 31.6282 | 31.5555 | 31.4566 | 31.3008 | 31.0815 | 30.8113 | 30.5414 | 30.2138 | 30.0302 | 30.0012 | 29.8581 | 29.3651
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 31.9052 | 31.7514 | 31.5991 | 31.2716 | 30.9601 | 30.6625 | 30.3889 | 30.1457 | 29.8717 | 29.6456 | 29.4924 | 27.3269 | 26.8471 | 26.331 | 23.4879 | 0 | 0
Berkswell 132kV | CAMPION HILLS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 31.9052 | 31.7986 | 31.7156 | 31.6018 | 31.4564 | 31.2822 | 31.0882 | 30.8398 | 30.5189 | 30.1526 | 29.7958 | 29.5565 | 27.4679 | 27.405 | 26.9421 | 25.4499 | 23.2018
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.7471 | 17.3793 | 17.0734 | 16.4493 | 15.8653 | 15.3207 | 13.7869 | 13.3423 | 12.3906 | 10.9125 | 8.993 | 6.9082 | 4.3688 | 2.4341 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.7471 | 17.3863 | 17.0972 | 16.4646 | 15.8743 | 13.7957 | 12.9761 | 11.2206 | 8.4155 | 4.8274 | 0.68268 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.7471 | 17.5167 | 17.4297 | 17.3413 | 17.2309 | 17.0762 | 16.8546 | 16.4496 | 15.7017 | 13.8122 | 12.6584 | 11.0686 | 8.9396 | 7.4423 | 5.4232 | 2.1115 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.7471 | 17.3807 | 17.067 | 16.4146 | 15.8203 | 13.8149 | 13.4271 | 12.5573 | 10.8932 | 8.911 | 5.8634 | 2.0374 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | CLAVERDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.7471 | 17.4664 | 17.2866 | 17.0434 | 16.766 | 16.3488 | 15.7915 | 13.8447 | 12.5645 | 10.0954 | 7.0745 | 4.1055 | 0.5079 | 0 | 0 | 0 | 0
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.3584 | 19.3348 | 19.3038 | 19.2461 | 19.181 | 19.1074 | 19.0231 | 18.962 | 18.9019 | 18.8496 | 18.7929 | 18.733 | 18.6904 | 18.6514 | 18.3904 | 17.688 | 17.4017
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.3584 | 19.3378 | 19.3096 | 19.2551 | 19.1938 | 19.1244 | 19.0454 | 18.9836 | 18.9277 | 18.8741 | 18.8203 | 18.7566 | 18.6997 | 18.644 | 18.3578 | 17.673 | 17.3613
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.3584 | 19.3436 | 19.3279 | 19.3086 | 19.2957 | 19.2822 | 19.2684 | 19.2533 | 19.2343 | 19.2145 | 19.1946 | 19.1754 | 19.1569 | 19.1424 | 19.0973 | 19.0554 | 18.9554
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.3584 | 19.3376 | 19.3076 | 19.2485 | 19.1845 | 19.1114 | 19.0243 | 18.9642 | 18.9037 | 18.8473 | 18.7855 | 18.7269 | 18.6764 | 18.6289 | 18.3001 | 17.636 | 17.2149
Berkswell 132kV | COURTAULDS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.3584 | 19.3436 | 19.3248 | 19.2974 | 19.2639 | 19.2239 | 19.1792 | 19.1419 | 19.1037 | 19.0663 | 19.029 | 18.9957 | 18.9623 | 18.9336 | 18.7952 | 18.564 | 18.3066
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 22.1892 | 22.0806 | 21.9571 | 21.6744 | 21.3861 | 21.1034 | 20.8439 | 20.5616 | 20.3072 | 20.1146 | 19.9051 | 19.6385 | 19.4547 | 19.2623 | 16.392 | 14.26 | 10.6875
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.1892 | 22.0833 | 21.9597 | 21.6789 | 21.3926 | 21.1221 | 20.8673 | 20.6026 | 20.3691 | 20.1934 | 20.0255 | 19.7958 | 19.6467 | 19.4873 | 16.4979 | 14.6701 | 11.4929
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.1892 | 22.1306 | 22.0763 | 22.0202 | 21.9611 | 21.9032 | 21.8441 | 21.7889 | 21.7233 | 21.6738 | 21.6363 | 21.6094 | 21.5949 | 21.5971 | 21.769 | 21.9967 | 21.5026
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.1892 | 22.0758 | 21.9372 | 21.6441 | 21.3487 | 21.0603 | 20.7879 | 20.5283 | 20.2846 | 20.0767 | 19.8755 | 19.6918 | 19.5004 | 19.2862 | 16.1921 | 13.6241 | 9.6467
Berkswell 132kV | Courthouse Green 33/11kv S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.1892 | 22.112 | 22.0296 | 21.91 | 21.7694 | 21.6206 | 21.4767 | 21.3354 | 21.2024 | 21.0987 | 21.0131 | 20.9548 | 20.9238 | 20.9248 | 20.6143 | 19.3863 | 16.5505
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Best View | Headroom (MW) | 16.563 | 16.3584 | 16.3211 | 16.2433 | 16.163 | 16.0857 | 15.9941 | 15.916 | 15.8399 | 15.7725 | 15.7033 | 15.6271 | 15.5702 | 15.5162 | 14.5994 | 14.0678 | 13.276
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 16.563 | 16.3582 | 16.3204 | 16.242 | 16.1619 | 16.0872 | 15.9977 | 15.9273 | 15.8619 | 15.8036 | 15.7477 | 15.66 | 15.5877 | 15.5176 | 14.5738 | 13.825 | 13.0287
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 16.563 | 16.5464 | 16.3506 | 16.3311 | 16.3102 | 16.2883 | 16.2675 | 16.2425 | 16.2108 | 16.182 | 16.1539 | 16.1284 | 16.1041 | 16.0822 | 16.0374 | 15.9496 | 15.798
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 16.563 | 16.3577 | 16.3178 | 16.2391 | 16.1585 | 16.0795 | 15.9856 | 15.915 | 15.848 | 15.7747 | 15.6981 | 15.6244 | 15.5565 | 15.4927 | 14.4548 | 13.6535 | 12.7337
Berkswell 132kV | Courthouse Green 33/6 6kv S Stn | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 16.563 | 16.3623 | 16.3365 | 16.3018 | 16.2603 | 16.2161 | 16.1662 | 16.1192 | 16.0684 | 16.0163 | 15.9669 | 15.9197 | 15.8759 | 15.836 | 15.5939 | 14.6405 | 14.4232
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 142.8431 | 136.4724 | 131.291 | 89.5186 | 86.5887 | 79.7174 | 74.3252 | 64.0649 | 52.718 | 43.2372 | 33.4738 | 21.6604 | 12.5727 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 142.8431 | 136.6397 | 131.541 | 89.5264 | 86.7702 | 80.2715 | 75.1117 | 65.5885 | 55.454 | 46.7118 | 38.3876 | 27.1814 | 18.1448 | 4.9972 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 142.8431 | 140.1238 | 136.2473 | 133.62 | 131.3235 | 128.8513 | 130.0823 | 127.6995 | 124.976 | 122.9594 | 86.0472 | 85.5118 | 84.9174 | 84.346 | 82.2112 | 80.1344 | 72.4508
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 142.8431 | 136.3717 | 130.6876 | 89.4686 | 86.0199 | 78.6506 | 73.1284 | 63.3422 | 52.1408 | 41.9604 | 32.0035 | 22.0318 | 11.4448 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY CENTRAL 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 142.8431 | 137.7704 | 134.514 | 129.2565 | 123.7171 | 88.3675 | 87.6376 | 85.5172 | 82.164 | 78.4727 | 74.762 | 71.3707 | 68.3768 | 66.1857 | 46.2894 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 71.1547 | 66.6825 | 62.9866 | 52.9932 | 42.9051 | 32.0129 | 22.2759 | 10.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 71.1547 | 66.7858 | 63.0887 | 53.2732 | 43.4024 | 32.8252 | 23.2647 | 12.2733 | 1.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 71.1547 | 68.5705 | 66.9829 | 65.4501 | 64.1608 | 62.5805 | 61.3331 | 59.8644 | 58.1667 | 56.6914 | 55.3695 | 54.3561 | 53.7543 | 53.579 | 58.4782 | 62.1336 | 49.6775
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 71.1547 | 66.5101 | 62.2591 | 51.759 | 41.4716 | 30.4512 | 20.0574 | 8.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY SOUTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 71.1547 | 67.7705 | 65.4879 | 61.88 | 57.9277 | 52.468 | 47.5038 | 41.9857 | 36.3697 | 31.79 | 27.5042 | 24.4203 | 21.9432 | 20.3112 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 97.9514 | 93.0638 | 87.8931 | 79.1494 | 69.8791 | 60.049 | 42.57 | 5.8649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 97.9514 | 92.6837 | 87.2607 | 76.9635 | 66.608 | 51.5162 | 12.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 97.9514 | 96.4777 | 93.3861 | 92.479 | 87.4552 | 86.3924 | 85.8949 | 83.449 | 78.9209 | 71.6984 | 62.4391 | 52.7453 | 37.694 | 14.1014 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 97.9514 | 92.513 | 86.7422 | 75.7698 | 65.1117 | 51.6316 | 17.7498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 97.9514 | 93.7991 | 92.056 | 86.2495 | 81.8366 | 75.8878 | 71.4165 | 61.9142 | 48.4931 | 4.1847 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 20.9069 | 20.7555 | 20.561 | 20.1205 | 19.708 | 19.3182 | 19.0241 | 17.0304 | 16.7965 | 16.2938 | 15.5736 | 14.7273 | 13.8047 | 13.0601 | 10.0967 | 5.8748 | 0.48244
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 20.9069 | 20.7233 | 20.4921 | 19.9634 | 19.4905 | 18.9608 | 16.861 | 15.9848 | 14.641 | 13.0625 | 11.2776 | 9.3539 | 7.2208 | 5.6933 | 0 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 20.9069 | 20.8324 | 20.7527 | 20.6626 | 20.5799 | 20.4803 | 20.3628 | 20.2004 | 19.9385 | 19.5717 | 19.1622 | 18.8519 | 17.0582 | 16.8395 | 16.5789 | 15.9603 | 14.4655
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 20.9069 | 20.7154 | 20.4675 | 19.9147 | 19.4386 | 18.9763 | 16.9552 | 16.4868 | 15.5662 | 14.5595 | 13.1603 | 11.5013 | 9.4795 | 7.7612 | 0.36713 | 0 | 0
Berkswell 132kV | COVENTRY WEST 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 20.9069 | 20.791 | 20.6583 | 20.4449 | 20.2044 | 19.9137 | 19.6041 | 19.1939 | 18.8452 | 16.7703 | 15.9793 | 15.0982 | 14.0371 | 13.2641 | 10.9112 | 7.1446 | 2.3955
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 17.9701 | 17.9216 | 17.9037 | 17.8079 | 17.7065 | 17.5895 | 17.4588 | 17.339 | 17.1751 | 17.0501 | 16.9178 | 16.7781 | 16.6524 | 16.5242 | 15.814 | 15.2503 | 14.2246
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 17.9701 | 17.9238 | 17.9102 | 17.8164 | 17.7176 | 17.6023 | 17.4777 | 17.3623 | 17.2176 | 17.099 | 16.9771 | 16.8355 | 16.6995 | 16.5616 | 15.8054 | 15.2026 | 14.2122
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 17.9701 | 17.9296 | 17.9237 | 17.885 | 17.8482 | 17.8119 | 17.7735 | 17.7343 | 17.6944 | 17.6477 | 17.6032 | 17.5583 | 17.5126 | 17.4695 | 17.2985 | 17.209 | 17.0444
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 17.9701 | 17.9199 | 17.8997 | 17.8001 | 17.695 | 17.5738 | 17.4376 | 17.3146 | 17.1384 | 17.0042 | 16.8637 | 16.7242 | 16.5833 | 16.4461 | 15.6526 | 14.8582 | 14.0647
Berkswell 132kV | COX STREET 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 17.9701 | 17.9274 | 17.9271 | 17.8711 | 17.8084 | 17.7334 | 17.6534 | 17.577 | 17.4836 | 17.4027 | 17.3188 | 17.236 | 17.1516 | 17.0739 | 16.6377 | 16.2877 | 15.9072
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.3337 | 17.2612 | 17.2242 | 17.0708 | 16.9376 | 16.8202 | 16.736 | 16.6873 | 15.8411 | 15.8008 | 15.7286 | 15.6108 | 15.5084 | 15.3947 | 14.4743 | 13.0594 | 11.1783
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.3337 | 17.2617 | 17.2237 | 17.0717 | 16.9396 | 16.8255 | 16.7419 | 16.691 | 15.847 | 15.8165 | 15.7636 | 15.6737 | 15.5959 | 15.506 | 14.6481 | 13.3168 | 11.6263
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.3337 | 17.3181 | 17.2948 | 17.2845 | 17.2686 | 17.2538 | 17.2388 | 17.2276 | 17.2098 | 17.1982 | 17.1917 | 17.1935 | 17.2028 | 17.2188 | 17.3776 | 17.4852 | 17.2658
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.3337 | 17.2571 | 17.2082 | 17.05 | 16.9162 | 16.802 | 16.7209 | 16.685 | 15.8369 | 15.7868 | 15.7108 | 15.6205 | 15.5182 | 15.3944 | 14.297 | 12.7657 | 10.7041
Berkswell 132kV | DILLOTFORD AVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.3337 | 17.2814 | 17.2693 | 17.2176 | 17.1596 | 17.0934 | 17.0331 | 16.9815 | 16.9266 | 16.8862 | 16.8527 | 16.8301 | 16.8175 | 16.8142 | 16.7103 | 15.6634 | 14.9069
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 19.6347 | 19.6088 | 19.5769 | 19.5154 | 19.4546 | 19.3779 | 19.3207 | 19.2592 | 19.198 | 19.1419 | 19.0861 | 19.0233 | 18.9712 | 18.9197 | 18.6141 | 18.1559 | 17.4729
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 19.6347 | 19.6103 | 19.5779 | 19.5169 | 19.4554 | 19.3813 | 19.3225 | 19.2628 | 19.2066 | 19.154 | 19.1042 | 19.0365 | 18.9782 | 18.9186 | 18.5828 | 18.0555 | 17.4084
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 19.6347 | 19.6169 | 19.5981 | 19.5799 | 19.5588 | 19.5395 | 19.5184 | 19.4959 | 19.4705 | 19.4471 | 19.4258 | 19.406 | 19.3849 | 19.3683 | 19.3211 | 19.2583 | 19.1414
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 19.6347 | 19.6081 | 19.5726 | 19.509 | 19.4469 | 19.3695 | 19.3093 | 19.2512 | 19.1936 | 19.1352 | 19.0741 | 19.0135 | 18.9516 | 18.8884 | 18.4766 | 17.5923 | 17.276
Berkswell 132kV | DUNLOP 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 19.6347 | 19.6144 | 19.5896 | 19.557 | 19.521 | 19.4753 | 19.4375 | 19.3962 | 19.3561 | 19.3157 | 19.277 | 19.2416 | 19.2079 | 19.1794 | 19.0106 | 18.7314 | 18.4367
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.184 | 12.4176 | 12.2963 | 12.1213 | 11.9557 | 11.7826 | 11.5981 | 11.3712 | 11.0696 | 10.6515 | 10.138 | 9.6011 | 8.9476 | 8.4403 | 6.9141 | 4.8045 | 2.3984
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.184 | 12.42 | 12.3046 | 12.1263 | 11.9581 | 11.601 | 11.1616 | 10.5668 | 9.7029 | 8.6105 | 7.3544 | 6.0522 | 4.5372 | 3.4028 | 0 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.184 | 13.0937 | 12.3947 | 12.3397 | 12.2823 | 12.2148 | 12.131 | 12 | 11.7837 | 11.4471 | 11.0146 | 10.5584 | 9.9796 | 9.556 | 8.8979 | 7.9168 | 6.7121
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.184 | 12.4188 | 12.2958 | 12.1158 | 11.9463 | 11.67 | 11.3727 | 11.0421 | 10.513 | 9.9055 | 8.9887 | 7.8471 | 6.3875 | 5.088 | 0.40592 | 0 | 0
Berkswell 132kV | GAYDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.184 | 12.4401 | 12.3492 | 12.2606 | 12.1626 | 12.0326 | 11.8654 | 11.5736 | 11.036 | 10.3291 | 9.5135 | 8.708 | 7.7358 | 7.0239 | 5.1757 | 2.431 | 0
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.7294 | 18.7099 | 18.7047 | 18.6461 | 18.6121 | 17.361 | 17.3458 | 17.2797 | 17.1306 | 16.8495 | 16.4155 | 15.9348 | 15.3385 | 14.8566 | 13.262 | 11.0055 | 8.4102
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.7294 | 18.7114 | 18.7098 | 18.6485 | 18.613 | 17.3428 | 17.2007 | 16.8514 | 16.1983 | 15.3126 | 14.2319 | 13.0927 | 11.7669 | 10.6962 | 6.7687 | 1.4734 | 0
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.7294 | 18.777 | 18.7316 | 18.7434 | 18.75 | 18.7501 | 18.7396 | 18.699 | 18.6264 | 17.4097 | 17.2965 | 17.0533 | 16.6358 | 16.3095 | 15.7899 | 14.8386 | 13.6679
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.7294 | 18.7188 | 18.7175 | 18.6549 | 18.6163 | 17.3574 | 17.2982 | 17.1529 | 16.7987 | 16.3311 | 15.5377 | 14.5266 | 13.2238 | 11.9776 | 7.4422 | 2.3335 | 0
Berkswell 132kV | HARBURY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.7294 | 18.7231 | 18.7405 | 18.7264 | 18.7111 | 18.6704 | 18.6247 | 17.3737 | 17.2198 | 16.7285 | 16.0056 | 15.2649 | 14.3558 | 13.6791 | 11.8628 | 9.0658 | 5.6714
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 79.0826 | 70.9857 | 69.0487 | 64.1633 | 59.8423 | 55.0249 | 50.0999 | 44.2515 | 36.8646 | 27.1787 | 12.7116 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 79.0826 | 71.0682 | 69.3328 | 64.3546 | 59.9663 | 51.5281 | 41.5435 | 28.2737 | 9.4649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 79.0826 | 78.6359 | 71.5575 | 71.1206 | 70.6644 | 69.8161 | 68.6228 | 66.3405 | 62.1256 | 55.4891 | 46.7581 | 37.5946 | 25.9708 | 17.5672 | 5.5475 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 79.0826 | 71.1836 | 69.3106 | 64.2557 | 59.8639 | 52.9935 | 45.7484 | 37.7471 | 25.5365 | 11.7775 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HARBURY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 79.0826 | 71.7103 | 70.8923 | 69.1759 | 67.4938 | 64.607 | 60.9794 | 54.6461 | 43.1026 | 27.9387 | 10.1535 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 15.044 | 15.0313 | 15.0099 | 14.9614 | 14.9067 | 14.8471 | 14.964 | 14.8399 | 14.7217 | 14.2945 | 14.279 | 14.2458 | 14.2255 | 14.2127 | 13.6794 | 13.3508 | 12.8825
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 15.044 | 15.0292 | 15.008 | 14.9581 | 14.9057 | 14.8379 | 14.9598 | 14.8444 | 14.7285 | 14.2967 | 14.2792 | 14.2247 | 14.1601 | 14.0825 | 13.2138 | 12.6033 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 15.044 | 15.0362 | 15.0278 | 15.0174 | 15.0123 | 15.0078 | 15.1939 | 15.2044 | 15.2142 | 15.2163 | 15.2106 | 15.2041 | 15.1998 | 15.2003 | 15.1726 | 15.2108 | 15.1282
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 15.044 | 15.028 | 15.0056 | 14.9524 | 14.8964 | 14.8287 | 14.9585 | 14.8245 | 14.6971 | 14.2663 | 14.2164 | 14.1403 | 14.0697 | 14.0019 | 13.2011 | 12.6097 | 0
Berkswell 132kV | HAWKESMILL LANE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 15.044 | 15.0336 | 15.022 | 15.0023 | 14.9772 | 14.9438 | 15.1296 | 15.0744 | 15.0022 | 14.9404 | 14.9098 | 14.8803 | 14.8504 | 14.8265 | 14.2917 | 14.1459 | 13.8509
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 24.4515 | 24.2807 | 24.0946 | 23.6692 | 23.3116 | 22.9068 | 23.0409 | 22.6428 | 22.2731 | 21.9787 | 21.6613 | 21.2728 | 20.9927 | 20.7042 | 18.7207 | 14.8349 | 10.3371
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 24.4515 | 24.2824 | 24.0962 | 23.6711 | 23.3149 | 22.9182 | 23.0557 | 22.6737 | 22.325 | 22.0392 | 21.7644 | 21.3984 | 21.1205 | 20.8343 | 18.7926 | 14.87 | 10.7219
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 24.4515 | 24.3556 | 24.2837 | 24.2054 | 24.1702 | 24.1118 | 24.4655 | 24.4199 | 24.3576 | 24.3119 | 24.2797 | 24.2607 | 24.258 | 24.2731 | 24.422 | 24.51 | 23.7933
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 24.4515 | 24.2753 | 24.0728 | 23.6238 | 23.2521 | 22.8424 | 23.028 | 22.6634 | 22.3094 | 21.9942 | 21.6789 | 21.3475 | 21.0163 | 20.6609 | 16.9903 | 13.6515 | 8.6139
Berkswell 132kV | HOLBROOK LANE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 24.4515 | 24.3267 | 24.2096 | 24.0349 | 23.8988 | 23.6959 | 24.0225 | 23.8288 | 23.6386 | 23.4762 | 23.3346 | 23.2207 | 23.1367 | 23.0926 | 22.4938 | 20.7821 | 18.734
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.0024 | 21.8335 | 21.7142 | 21.3946 | 21.0927 | 20.8027 | 20.5409 | 20.2554 | 20.0121 | 19.8321 | 19.6413 | 19.398 | 19.2418 | 19.0858 | 16.675 | 14.4256 | 10.924
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.0024 | 21.8328 | 21.71 | 21.3948 | 21.0986 | 20.82 | 20.5688 | 20.3076 | 20.0867 | 19.9216 | 19.7713 | 19.5718 | 19.4494 | 19.318 | 16.876 | 14.9149 | 11.8241
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.0024 | 21.8945 | 21.8508 | 21.8092 | 21.7548 | 21.7002 | 21.6464 | 21.5991 | 21.5515 | 21.5173 | 21.4973 | 21.4948 | 21.5103 | 21.5428 | 21.9189 | 22.2628 | 21.8295
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.0024 | 21.8233 | 21.6788 | 21.3467 | 21.0401 | 20.7461 | 20.4709 | 20.2185 | 19.9908 | 19.801 | 19.6274 | 19.4678 | 19.3116 | 19.1378 | 16.4524 | 13.8761 | 10.0119
Berkswell 132kV | HOLYHEAD ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.0024 | 21.8658 | 21.7866 | 21.6646 | 21.5254 | 21.3756 | 21.2332 | 21.1025 | 20.9801 | 20.8895 | 20.8197 | 20.7808 | 20.771 | 20.7913 | 20.5924 | 19.5332 | 17.0388
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.974 | 19.7643 | 19.7404 | 19.6841 | 19.6311 | 19.5645 | 19.5337 | 19.4203 | 19.2494 | 19.0225 | 18.7021 | 17.3642 | 17.0782 | 16.732 | 15.747 | 14.514 | 13.058
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.974 | 19.7526 | 19.713 | 19.6192 | 19.5324 | 19.3003 | 19.0641 | 18.7441 | 17.3407 | 16.948 | 16.2263 | 15.3974 | 14.3923 | 13.683 | 10.6775 | 7.3438 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.974 | 19.9518 | 19.7425 | 19.7132 | 19.6877 | 19.6526 | 19.6055 | 19.519 | 19.3661 | 19.1232 | 18.827 | 18.6041 | 17.3085 | 17.112 | 16.715 | 16.1878 | 15.5032
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.974 | 19.752 | 19.7097 | 19.6126 | 19.5263 | 19.3597 | 19.1783 | 18.9809 | 18.709 | 18.5786 | 17.067 | 16.3326 | 15.3336 | 14.4647 | 11.3277 | 8.0844 | 0
Berkswell 132kV | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.974 | 19.7592 | 19.7301 | 19.6852 | 19.6379 | 19.5639 | 19.4569 | 19.2602 | 18.9538 | 18.6511 | 17.3169 | 16.9943 | 16.4293 | 16.0715 | 14.8979 | 13.393 | 11.5667
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.5194 | 25.2242 | 25.0417 | 24.4893 | 24.0056 | 23.4498 | 22.9251 | 22.3626 | 21.9196 | 21.4916 | 18.2521 | 17.7753 | 16.8686 | 16.014 | 12.3902 | 7.2021 | 0.69983
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.5194 | 25.2222 | 25.0337 | 24.4806 | 23.9961 | 23.2979 | 22.5858 | 21.8502 | 21.4112 | 17.8577 | 16.7767 | 15.254 | 13.4369 | 11.9073 | 5.4194 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.5194 | 25.4174 | 25.3073 | 25.278 | 25.2812 | 25.2442 | 25.1946 | 25.0948 | 24.9255 | 24.576 | 24.1413 | 23.6632 | 23.0522 | 22.675 | 22.2977 | 21.4605 | 18.225
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.5194 | 25.2112 | 24.9912 | 24.4131 | 23.9109 | 23.2834 | 22.6496 | 22.0813 | 21.5811 | 18.2545 | 17.7612 | 16.5619 | 14.8551 | 13.1746 | 5.7938 | 0 | 0
Berkswell 132kV | KENILWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.5194 | 25.2977 | 25.2154 | 25.049 | 24.8909 | 24.6014 | 24.2843 | 23.8536 | 23.2868 | 22.4899 | 21.7487 | 21.3556 | 17.8919 | 17.2811 | 14.8996 | 10.6876 | 5.2211
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.2967 | 18.2443 | 18.2578 | 18.147 | 17.3993 | 17.3846 | 17.35 | 17.2895 | 17.2158 | 17.1397 | 17.0544 | 16.9689 | 16.89 | 16.7934 | 16.1232 | 15.1881 | 13.1319
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.2967 | 18.244 | 18.2567 | 18.146 | 17.3993 | 17.3846 | 17.3491 | 17.291 | 17.2224 | 17.1484 | 17.0734 | 16.9843 | 16.8941 | 16.7825 | 15.6401 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.2967 | 18.3334 | 18.278 | 18.2545 | 18.2291 | 18.2044 | 18.1978 | 18.1858 | 18.1743 | 18.1653 | 18.1589 | 18.1575 | 18.1596 | 18.1533 | 18.1657 | 18.0898 | 17.4874
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.2967 | 18.248 | 18.2541 | 18.1411 | 17.3989 | 17.3788 | 17.3354 | 17.2689 | 17.1818 | 17.0854 | 16.9702 | 16.211 | 16.116 | 15.9968 | 15.1429 | 0 | 0
Berkswell 132kV | LOCKHEED 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.2967 | 18.2565 | 18.2903 | 18.237 | 18.1774 | 18.1196 | 18.0948 | 17.4133 | 17.413 | 17.4077 | 17.4002 | 17.3957 | 17.3854 | 17.3675 | 16.8455 | 16.35 | 15.7465
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.0782 | 13.0449 | 13.0045 | 12.9111 | 12.8245 | 12.7415 | 12.6673 | 12.59 | 12.5227 | 12.4677 | 12.4175 | 12.3715 | 12.3458 | 12.3332 | 11.455 | 10.8625 | 10.0487
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.0782 | 13.0446 | 13.0039 | 12.9095 | 12.8218 | 12.7372 | 12.658 | 12.5791 | 12.5102 | 12.4529 | 12.4046 | 12.36 | 12.3385 | 11.6622 | 11.2953 | 10.5191 | 9.7412
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.0782 | 13.0631 | 13.0485 | 13.0329 | 13.0142 | 12.996 | 12.9769 | 12.9596 | 12.939 | 12.9203 | 12.904 | 12.891 | 12.8817 | 12.8766 | 12.9193 | 12.9166 | 12.7878
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.0782 | 13.0425 | 12.9957 | 12.8979 | 12.8097 | 12.7227 | 12.6414 | 12.5675 | 12.4939 | 12.4337 | 12.3852 | 12.3516 | 12.3367 | 11.6553 | 11.2025 | 10.4159 | 9.4945
Berkswell 132kV | PRINCETHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.0782 | 13.0536 | 13.0275 | 12.9875 | 12.9437 | 12.8968 | 12.8527 | 12.8092 | 12.7673 | 12.7274 | 12.6918 | 12.6608 | 12.6373 | 12.6184 | 12.4751 | 12.2992 | 11.4906
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 23.3512 | 23.236 | 23.0905 | 22.7615 | 22.4374 | 22.0938 | 21.775 | 21.3781 | 20.9564 | 20.6304 | 20.3575 | 20.0447 | 19.8113 | 19.5928 | 16.1439 | 14.0533 | 10.5011
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 23.3512 | 23.2433 | 23.101 | 22.7784 | 22.4578 | 22.126 | 21.8099 | 21.447 | 21.0763 | 20.7779 | 20.5373 | 20.2325 | 19.9946 | 19.7656 | 16.1829 | 14.0797 | 10.8285
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 23.3512 | 23.2902 | 23.2267 | 23.1602 | 23.0877 | 23.0177 | 22.9443 | 22.8728 | 22.7927 | 22.7164 | 22.6423 | 22.5811 | 22.5314 | 22.5002 | 22.5827 | 22.6656 | 22.1211
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 23.3512 | 23.2353 | 23.0745 | 22.7325 | 22.3977 | 22.0464 | 21.7073 | 21.3289 | 20.905 | 20.5587 | 20.2853 | 20.031 | 19.7899 | 19.5445 | 15.8659 | 13.1643 | 9.1902
Berkswell 132kV | SANDY LANE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 23.3512 | 23.2759 | 23.1814 | 23.0445 | 22.8835 | 22.6944 | 22.5165 | 22.3194 | 22.0982 | 21.9118 | 21.764 | 21.6446 | 21.5463 | 21.4828 | 20.8885 | 19.5874 | 16.3115
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.9164 | 15.8232 | 15.7376 | 15.5065 | 15.3157 | 15.101 | 14.8865 | 14.658 | 14.3991 | 14.1083 | 13.7858 | 13.4555 | 13.0794 | 12.7535 | 11.1613 | 8.991 | 6.3124
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.9164 | 15.8271 | 15.7507 | 15.5156 | 15.3215 | 15.0251 | 14.6967 | 14.2977 | 13.8072 | 13.2399 | 12.612 | 11.9238 | 11.1733 | 10.5848 | 7.9891 | 4.5336 | 1.4405
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.9164 | 15.8746 | 15.8665 | 15.8518 | 15.8476 | 15.8208 | 15.7891 | 15.735 | 15.633 | 15.4891 | 15.3132 | 15.1338 | 14.917 | 14.7676 | 14.6619 | 14.3522 | 13.6841
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.9164 | 15.8261 | 15.7418 | 15.4967 | 15.3032 | 15.0361 | 14.7667 | 14.4819 | 14.1169 | 13.724 | 13.2045 | 12.5955 | 11.8546 | 11.1741 | 8.0968 | 4.5553 | 1.6465
Berkswell 132kV | SOUTHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.9164 | 15.855 | 15.8218 | 15.7439 | 15.6817 | 15.57 | 15.4447 | 15.2655 | 14.9929 | 14.6578 | 14.2888 | 13.9332 | 13.5278 | 13.2335 | 12.242 | 10.5578 | 8.4811
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 21.9006 | 21.8068 | 21.7074 | 21.4909 | 21.2651 | 21.0377 | 20.8626 | 20.6461 | 20.4685 | 20.2779 | 20.1059 | 19.9182 | 19.7671 | 19.6314 | 18.7958 | 17.2401 | 15.8434
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 21.9006 | 21.8158 | 21.718 | 21.5094 | 21.2913 | 21.0687 | 20.8807 | 20.6661 | 20.4952 | 20.3085 | 20.1411 | 19.9451 | 19.7707 | 19.5981 | 18.6824 | 17.0705 | 15.7208
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 21.9006 | 21.834 | 21.7772 | 21.7078 | 21.6531 | 21.5983 | 21.5453 | 21.4963 | 21.4373 | 21.3807 | 21.327 | 21.2779 | 21.2342 | 21.1999 | 21.1295 | 21.0821 | 20.8176
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 21.9006 | 21.8069 | 21.6985 | 21.4785 | 21.2533 | 21.0221 | 20.8383 | 20.629 | 20.4455 | 20.2408 | 20.0602 | 19.886 | 19.7323 | 19.5938 | 18.5459 | 16.9129 | 15.3235
Berkswell 132kV | SPON STREET 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 21.9006 | 21.8309 | 21.7581 | 21.6547 | 21.5357 | 21.4082 | 21.2976 | 21.1722 | 21.0595 | 20.9399 | 20.8312 | 20.742 | 20.6582 | 20.586 | 20.2151 | 19.5315 | 18.7268
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.7347 | 17.6277 | 17.4919 | 17.1694 | 16.844 | 16.5216 | 16.2301 | 15.9132 | 15.6193 | 15.3845 | 15.1779 | 14.0372 | 13.969 | 13.8441 | 12.3216 | 9.5972 | 5.9447
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.7347 | 17.6297 | 17.4953 | 17.178 | 16.8595 | 16.5504 | 16.2636 | 15.9696 | 15.7017 | 15.4836 | 15.2846 | 14.8373 | 14.0385 | 13.9671 | 12.5867 | 9.8527 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.7347 | 17.6872 | 17.6406 | 17.5916 | 17.5336 | 17.4739 | 17.4167 | 17.3608 | 17.2982 | 17.2457 | 17.2033 | 17.1737 | 17.158 | 17.1563 | 17.336 | 17.4653 | 16.9691
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.7347 | 17.6207 | 17.468 | 17.1316 | 16.8006 | 16.4705 | 16.1656 | 15.8735 | 15.5954 | 15.3494 | 15.1652 | 14.0428 | 13.9782 | 13.8422 | 11.8626 | 8.7643 | 0
Berkswell 132kV | TORRINGTON AVENUE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.7347 | 17.6627 | 17.5815 | 17.4566 | 17.307 | 17.1416 | 16.9904 | 16.8403 | 16.6913 | 16.5622 | 16.4517 | 16.3655 | 16.3028 | 16.2697 | 15.7883 | 14.0376 | 12.673
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 18.9406 | 18.7743 | 18.743 | 18.6614 | 18.5878 | 18.5174 | 18.457 | 18.3909 | 18.3385 | 18.2933 | 18.2465 | 18.193 | 18.1574 | 18.1234 | 17.4764 | 17.0735 | 13.1162
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.9406 | 18.7739 | 18.7417 | 18.6597 | 18.5856 | 18.5153 | 18.4543 | 18.3892 | 18.337 | 18.2891 | 18.2453 | 18.1951 | 18.1597 | 18.1242 | 17.4655 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.9406 | 18.9576 | 18.7779 | 18.768 | 18.7555 | 18.743 | 18.7312 | 18.7214 | 18.7146 | 18.7089 | 18.7063 | 18.7086 | 18.7166 | 18.7284 | 18.8486 | 18.9276 | 18.8491
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.9406 | 18.7752 | 18.739 | 18.6525 | 18.5756 | 18.5006 | 18.4321 | 18.3698 | 18.3151 | 18.2631 | 18.2143 | 18.1701 | 18.1294 | 18.0926 | 17.3932 | 0 | 0
Berkswell 132kV | Tournament Fields 33/11kv S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.9406 | 18.7835 | 18.7627 | 18.7304 | 18.6942 | 18.6559 | 18.6187 | 18.5904 | 18.5634 | 18.5384 | 18.5177 | 18.5062 | 18.4994 | 18.5005 | 18.4536 | 18.2279 | 17.1372
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 27.4035 | 27.2395 | 27.0866 | 26.7282 | 26.3994 | 25.9729 | 25.5729 | 25.0494 | 24.498 | 24.088 | 23.6287 | 23.6012 | 23.2273 | 22.8698 | 20.8394 | 18.4255 | 15.3165
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 27.4035 | 27.2421 | 27.0918 | 26.7387 | 26.4178 | 26.0008 | 25.6153 | 25.1183 | 24.6002 | 24.1868 | 23.7599 | 23.3575 | 22.997 | 22.6439 | 20.5942 | 26.7699 | 23.953
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 27.4035 | 27.3096 | 27.2551 | 27.2065 | 27.187 | 27.1356 | 27.1178 | 27.0625 | 26.998 | 26.9368 | 26.8709 | 26.8093 | 26.763 | 26.7311 | 26.8257 | 26.8426 | 26.3527
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 27.4035 | 27.2343 | 27.0655 | 26.6911 | 26.3498 | 25.9187 | 25.4804 | 24.9445 | 24.3486 | 23.8926 | 23.3971 | 23.0154 | 22.673 | 22.3423 | 28.8147 | 13.7349 | 10.3261
Berkswell 132kV | UNIVERSITY OF WARWICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 27.4035 | 27.2845 | 27.1976 | 27.0726 | 26.9488 | 26.73 | 26.5468 | 26.2938 | 26.0184 | 25.8067 | 25.5845 | 25.4223 | 25.2706 | 25.1483 | 24.4508 | 23.5971 | 22.1068
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 33.2333 | 33.1233 | 33.0805 | 32.7776 | 32.5081 | 32.2258 | 31.9551 | 31.663 | 31.4415 | 31.2264 | 30.9803 | 30.6065 | 30.2692 | 30.0351 | 28.5979 | 26.3951 | 23.3804
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 33.2333 | 33.1222 | 33.0757 | 32.7721 | 32.5015 | 32.2152 | 31.929 | 31.6169 | 31.3537 | 31.0721 | 30.7809 | 30.3595 | 29.8854 | 29.6027 | 27.8399 | 25.4015 | 22.5051
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 33.2333 | 33.1778 | 33.1993 | 33.1694 | 33.1429 | 33.1033 | 33.0566 | 33.0074 | 32.9553 | 32.8881 | 32.8068 | 32.7068 | 32.5821 | 32.5225 | 32.6916 | 32.6147 | 32.0405
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 33.2333 | 33.1156 | 33.0475 | 32.734 | 32.4599 | 32.1693 | 31.8863 | 31.6389 | 31.4138 | 31.1899 | 30.9046 | 30.5354 | 30.1175 | 29.6915 | 27.4758 | 24.7525 | 21.4764
Berkswell 132kV | WARWICK 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 33.2333 | 33.1587 | 33.1649 | 33.0553 | 32.9431 | 32.7905 | 32.6289 | 32.4562 | 32.3033 | 32.1198 | 31.9326 | 31.6911 | 31.4282 | 31.2729 | 30.6275 | 29.2765 | 27.6882
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 70.4116 | 60.3413 | 56.3168 | 43.9964 | 31.9179 | 19.671 | 7.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 70.4116 | 60.3489 | 56.3298 | 43.9452 | 31.8155 | 17.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 70.4116 | 67.8673 | 61.7415 | 61.2033 | 59.7624 | 57.8491 | 55.5744 | 52.3504 | 46.9057 | 38.7514 | 24.0392 | 7.6778 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 70.4116 | 60.1686 | 55.4479 | 42.6298 | 30.265 | 16.6891 | 0.86421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WARWICK 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 70.4116 | 61.3881 | 59.9923 | 55.9272 | 50.724 | 43.9336 | 36.4863 | 26.6083 | 10.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.6088 | 23.0611 | 22.8736 | 22.4561 | 22.0591 | 21.6844 | 21.3365 | 20.9703 | 20.6463 | 20.3682 | 20.0947 | 19.8072 | 19.6144 | 19.4585 | 15.7584 | 13.0531 | 9.1168
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.6088 | 23.0597 | 22.8682 | 22.45 | 22.0522 | 21.6785 | 21.3272 | 20.9726 | 20.6632 | 20.3869 | 20.1348 | 19.8489 | 19.6418 | 19.4695 | 15.6618 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.6088 | 23.4979 | 23.064 | 22.9977 | 22.9147 | 22.8302 | 22.7477 | 22.6724 | 22.588 | 22.5119 | 22.4495 | 22.4047 | 22.3757 | 22.3634 | 22.5275 | 22.547 | 21.9282
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.6088 | 23.0508 | 22.8387 | 22.4044 | 21.9983 | 21.6038 | 21.2342 | 20.8919 | 20.5744 | 20.275 | 19.9961 | 19.7625 | 19.5538 | 19.3977 | 15.0944 | 0 | 0
Berkswell 132kV | WISE STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.6088 | 23.1009 | 22.9728 | 22.8037 | 22.6103 | 22.3986 | 22.1995 | 22.0074 | 21.8212 | 21.6501 | 21.4966 | 21.3657 | 21.2628 | 21.1824 | 20.53 | 19.3481 | 15.9842
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.8081 | 8.5927 | 8.586 | 8.4726 | 8.401 | 7.4957 | 7.3403 | 7.0538 | 3.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.8081 | 8.5899 | 8.5823 | 8.471 | 8.3997 | 7.4686 | 7.2094 | 6.7737 | 5.7331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.8081 | 8.7842 | 8.6333 | 8.6167 | 8.5944 | 8.566 | 8.5357 | 8.4621 | 8.372 | 7.447 | 7.0903 | 6.6329 | 6.1044 | 4.7629 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.8081 | 8.5904 | 8.5774 | 8.4667 | 8.3984 | 7.4923 | 7.3288 | 7.0495 | 3.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | ALFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.8081 | 8.6066 | 8.6221 | 8.5719 | 8.5166 | 8.452 | 8.3987 | 7.5175 | 7.2705 | 6.7998 | 6.2216 | 2.1356 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.3561 | 3.2756 | 3.1609 | 2.8964 | 2.6367 | 2.0802 | 1.4231 | 0.53944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.3561 | 3.2707 | 3.1528 | 2.8666 | 2.587 | 1.8838 | 0.94108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.3561 | 3.3344 | 3.3055 | 3.2758 | 3.2313 | 3.1398 | 2.9801 | 2.6181 | 1.9053 | 0.69786 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.3561 | 3.2722 | 3.1462 | 2.8549 | 2.5753 | 2.0485 | 1.4748 | 0.81586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | BILLINGBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.3561 | 3.3101 | 3.2453 | 3.142 | 3.0199 | 2.7704 | 2.3474 | 1.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.0309 | 17.98 | 17.9138 | 17.7527 | 17.5951 | 17.1703 | 10.99 | 7.3642 | 3.3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.0309 | 17.9742 | 17.9002 | 17.7409 | 17.5828 | 17.0769 | 15.6228 | 10.9304 | 5.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.0309 | 18.0061 | 17.9836 | 17.9606 | 17.9316 | 17.8887 | 17.8233 | 17.6726 | 17.3649 | 16.8404 | 16.1612 | 15.1291 | 10.8035 | 7.5744 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.0309 | 17.9779 | 17.9052 | 17.7452 | 17.5884 | 17.1574 | 10.8782 | 7.3587 | 3.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CHAPEL ST LEONARDS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.0309 | 17.9969 | 17.9588 | 17.8977 | 17.8263 | 17.7114 | 17.543 | 17.1702 | 16.4863 | 12.9487 | 7.4651 | 2.1127 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | CRANWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.5814 | 7.5937 | 7.6146 | 7.662 | 7.7053 | 7.5238 | 6.6739 | 5.4514 | 3.2198 | 0.36894 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.5814 | 7.596 | 7.6185 | 7.6724 | 7.7217 | 7.3879 | 6.3358 | 4.7512 | 2.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.5814 | 7.5827 | 7.5868 | 7.5876 | 7.5938 | 7.6012 | 7.6173 | 7.6579 | 7.1756 | 5.8329 | 4.0365 | 2.1019 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.5814 | 7.597 | 7.6237 | 7.678 | 7.7255 | 7.6108 | 6.9754 | 6.2159 | 4.6614 | 2.8207 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | EASTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.5814 | 7.5895 | 7.6025 | 7.6194 | 7.6395 | 7.6664 | 7.7153 | 6.8251 | 4.7391 | 1.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 84.7939 | 83.8844 | 83.2638 | 81.7905 | 80.2806 | 77.5453 | 74.2774 | 69.8929 | 63.0474 | 54.7666 | 44.5553 | 33.3513 | 20.1069 | 3.2822 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 84.7939 | 83.8534 | 83.1883 | 81.6277 | 80.0334 | 77.0345 | 73.3363 | 68.2476 | 60.4762 | 50.8305 | 39.7219 | 28.107 | 5.0334 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 84.7939 | 84.5423 | 83.9642 | 83.7409 | 83.5273 | 83.1676 | 82.6326 | 81.5425 | 79.4777 | 76.0503 | 71.5275 | 66.6696 | 60.4363 | 56.045 | 49.2074 | 39.4706 | 28.114
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 84.7939 | 83.83 | 83.1161 | 81.4805 | 79.8384 | 77.2655 | 74.3958 | 71.1317 | 65.8317 | 59.9661 | 51.2558 | 40.4412 | 26.9237 | 6.3817 | 0 | 0 | 0
Bicker Fen 132kV | GRANTHAM 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 84.7939 | 84.0639 | 83.6983 | 83.121 | 82.4111 | 81.2275 | 79.5675 | 76.5407 | 70.8876 | 63.4242 | 54.662 | 45.9991 | 35.5048 | 28.2276 | 6.6177 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 3.4865 | 3.4525 | 3.3317 | 3.0529 | 2.7791 | 2.1926 | 1.5 | 0.56858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 3.4865 | 3.4474 | 3.3231 | 3.0214 | 2.7268 | 1.9855 | 0.99192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 3.4865 | 3.479 | 3.4759 | 3.4528 | 3.4058 | 3.3094 | 3.1411 | 2.7596 | 2.0082 | 0.73556 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 3.4865 | 3.4489 | 3.3162 | 3.0091 | 2.7144 | 2.1592 | 1.5545 | 0.85994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | GREAT HALE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 3.4865 | 3.4738 | 3.4206 | 3.3117 | 3.1831 | 2.9201 | 2.4742 | 1.5215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | HORNCASTLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.4466 | 20.3839 | 20.3117 | 20.1817 | 19.7471 | 19.3224 | 10.9338 | 7.3265 | 3.3385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.4466 | 20.3802 | 20.3036 | 20.175 | 19.7532 | 19.3319 | 15.5429 | 10.8745 | 5.6427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.4466 | 20.4029 | 20.3592 | 20.3155 | 20.2699 | 20.2183 | 20.157 | 20.0495 | 19.8645 | 19.5883 | 18.9336 | 15.0517 | 10.7482 | 7.5356 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.4466 | 20.3827 | 20.3059 | 20.1769 | 19.7434 | 19.32 | 10.8226 | 7.3211 | 3.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | INGOLDMELLS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.4466 | 20.3951 | 20.3399 | 20.2712 | 20.0835 | 19.8649 | 19.6532 | 19.4402 | 17.766 | 12.8825 | 7.4269 | 2.1019 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | LEADENHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.467 | 11.4639 | 11.4622 | 11.4577 | 11.4529 | 11.4463 | 11.4372 | 11.4197 | 11.0895 | 10.5995 | 9.7112 | 7.1618 | 4.3029 | 1.8946 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.467 | 11.4631 | 11.4603 | 11.4527 | 11.4443 | 11.4216 | 11.3898 | 11.2313 | 10.7734 | 10.1961 | 9.2576 | 6.6526 | 3.7064 | 1.1799 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.467 | 11.4645 | 11.4639 | 11.4633 | 11.4626 | 11.4607 | 11.4566 | 11.4453 | 11.4199 | 11.3742 | 11.3119 | 10.9686 | 10.5182 | 10.2209 | 9.7961 | 9.1756 | 8.4366
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.467 | 11.463 | 11.4598 | 11.452 | 11.4438 | 11.426 | 11.4058 | 11.3824 | 11.1713 | 10.847 | 10.3508 | 8.3636 | 5.3236 | 2.4279 | 0 | 0 | 0
Bicker Fen 132kV | MARKET OVERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.467 | 11.464 | 11.4628 | 11.4604 | 11.4574 | 11.4502 | 11.4364 | 11.4045 | 11.3372 | 10.9035 | 10.3362 | 9.7791 | 9.1045 | 7.8131 | 3.4877 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.0734 | 19.914 | 19.7208 | 19.2568 | 18.7732 | 18.1452 | 17.1557 | 15.9465 | 14.1885 | 12.141 | 9.7557 | 7.1946 | 4.3226 | 1.9033 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.0734 | 19.9128 | 19.7162 | 19.252 | 18.7685 | 18.1448 | 16.9879 | 15.7143 | 13.8859 | 11.7382 | 9.3001 | 6.6831 | 3.7234 | 1.1853 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.0734 | 20.0036 | 19.9413 | 19.874 | 19.8184 | 19.7398 | 19.643 | 19.4805 | 19.1934 | 18.7205 | 17.5014 | 16.6604 | 15.4299 | 14.5425 | 13.164 | 11.3551 | 8.7536
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.0734 | 19.9003 | 19.6836 | 19.187 | 18.6797 | 18.1188 | 17.0375 | 16.0518 | 14.6072 | 13.0692 | 10.955 | 8.4019 | 5.348 | 2.4391 | 0 | 0 | 0
Bicker Fen 132kV | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.0734 | 19.9711 | 19.8626 | 19.6922 | 19.4755 | 19.1572 | 18.7789 | 18.2469 | 16.8547 | 15.2906 | 13.4413 | 11.6014 | 9.4015 | 7.8489 | 3.5037 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.402 | 16.2806 | 16.2118 | 16.0514 | 15.8842 | 15.5958 | 15.272 | 14.8884 | 14.2676 | 13.5779 | 12.5378 | 11.2 | 9.5225 | 7.9956 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.402 | 16.279 | 16.2008 | 16.019 | 15.8293 | 15.4343 | 14.9239 | 14.2189 | 13.1753 | 11.8866 | 10.421 | 8.8975 | 7.057 | 0 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.402 | 16.3154 | 16.2944 | 16.2693 | 16.2393 | 16.1921 | 16.1187 | 15.9824 | 15.7262 | 15.3082 | 14.7474 | 14.1421 | 13.3601 | 12.817 | 11.9662 | 10.9865 | 9.4709
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.402 | 16.2777 | 16.196 | 16.0071 | 15.8154 | 15.4919 | 15.1223 | 14.7042 | 14.0372 | 13.3071 | 12.2364 | 10.8937 | 9.1836 | 7.6118 | 0 | 0 | 0
Bicker Fen 132kV | RUSKINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.402 | 16.3016 | 16.2572 | 16.1909 | 16.1084 | 15.9729 | 15.773 | 15.4045 | 14.7205 | 13.8156 | 12.7581 | 11.7131 | 10.4442 | 9.5862 | 7.4469 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 30.2011 | 28.6512 | 27.4562 | 24.2241 | 19.2293 | 9.9839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 30.2011 | 28.5843 | 27.3232 | 24.184 | 19.3057 | 9.535 | 0.88711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 30.2011 | 29.7326 | 28.8184 | 28.3956 | 27.8487 | 27.16 | 26.2804 | 24.4553 | 20.9537 | 15.0753 | 7.6762 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 30.2011 | 28.6013 | 27.2677 | 24.0578 | 19.0695 | 9.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKEGNESS 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 30.2011 | 28.9884 | 28.3341 | 27.0945 | 24.9803 | 21.2666 | 18.1812 | 13.2342 | 5.3388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.2646 | 12.2306 | 12.1989 | 12.1239 | 12.0513 | 11.9211 | 11.7998 | 11.4586 | 11.0817 | 10.5921 | 9.7054 | 7.1575 | 4.3003 | 1.8935 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.2646 | 12.2199 | 12.1729 | 12.0664 | 11.9645 | 11.8151 | 11.5213 | 11.2235 | 10.7658 | 10.189 | 9.2521 | 6.6486 | 3.7042 | 1.1792 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.2646 | 12.243 | 12.2271 | 12.2112 | 12.1939 | 12.1714 | 12.1356 | 12.0578 | 11.9142 | 11.6038 | 11.3077 | 10.9609 | 10.5109 | 10.2138 | 9.7893 | 9.1692 | 8.4307
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.2646 | 12.2173 | 12.1673 | 12.0571 | 11.9549 | 11.8289 | 11.5939 | 11.4443 | 11.1635 | 10.8394 | 10.3436 | 8.3586 | 5.3204 | 2.4265 | 0 | 0 | 0
Bicker Fen 132kV | SKILLINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.2646 | 12.2361 | 12.2104 | 12.1696 | 12.1232 | 12.0561 | 11.9604 | 11.8036 | 11.3749 | 10.8959 | 10.3289 | 9.7722 | 9.0982 | 7.8084 | 3.4857 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.5039 | 19.4042 | 19.2399 | 18.8374 | 18.4238 | 17.8453 | 17.2593 | 16.5603 | 15.5552 | 14.4371 | 12.835 | 10.8408 | 8.4586 | 6.2487 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.5039 | 19.4025 | 19.2341 | 18.7905 | 18.3384 | 17.6178 | 16.7735 | 15.6842 | 14.1614 | 12.3463 | 10.2794 | 8.0754 | 5.5814 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.5039 | 19.4796 | 19.4372 | 19.3789 | 19.3205 | 19.2671 | 19.1486 | 18.9489 | 18.5875 | 18.0661 | 17.2728 | 16.4867 | 15.4907 | 14.769 | 13.6595 | 12.2746 | 10.2459
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.5039 | 19.3967 | 19.2118 | 18.7451 | 18.2764 | 17.6377 | 16.919 | 16.1364 | 15.0097 | 13.7896 | 12.0884 | 10.0485 | 7.5609 | 5.2185 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.5039 | 19.4558 | 19.3651 | 19.2019 | 18.9975 | 18.7333 | 18.3595 | 17.7411 | 16.7507 | 15.4775 | 14.0011 | 12.5419 | 10.8104 | 9.5608 | 6.0526 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 68.7024 | 66.0952 | 64.7237 | 61.5802 | 57.1082 | 50.7227 | 43.8821 | 36.9494 | 27.4681 | 17.4629 | 3.7731 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 68.7024 | 66.0526 | 64.6026 | 61.2518 | 56.6275 | 49.18 | 40.5029 | 30.4161 | 17.3969 | 1.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 68.7024 | 67.8093 | 66.2528 | 65.7471 | 65.1736 | 64.4704 | 63.3899 | 61.4672 | 57.9936 | 52.3732 | 45.1569 | 37.5175 | 28.2314 | 21.5604 | 9.334 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 68.7024 | 66.0355 | 64.4986 | 61.0288 | 56.2695 | 49.5597 | 42.3268 | 35.3661 | 25.753 | 15.8808 | 2.2667 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SLEAFORD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 68.7024 | 66.488 | 65.6611 | 64.3303 | 62.2802 | 59.5317 | 56.0752 | 50.7794 | 41.9956 | 30.8098 | 18.0423 | 5.5603 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | SPILSBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.8843 | 18.3794 | 18.1286 | 17.5424 | 16.3393 | 14.7357 | 13.0889 | 11.6961 | 10.249 | 8.9372 | 7.4058 | 5.6731 | 3.782 | 2.2116 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.8843 | 18.3688 | 18.1008 | 17.5077 | 16.321 | 14.6675 | 12.8884 | 11.2538 | 9.6691 | 7.9487 | 6.1655 | 4.3141 | 2.3297 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.8843 | 18.6759 | 18.3979 | 18.3054 | 18.1976 | 18.082 | 17.93 | 17.6825 | 17.2579 | 16.5562 | 15.7048 | 14.8255 | 13.9318 | 13.2197 | 11.1034 | 9.1473 | 6.3526
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.8843 | 18.3676 | 18.088 | 17.4754 | 16.2429 | 14.5972 | 12.8874 | 11.4854 | 9.9999 | 8.6554 | 7.1238 | 5.4783 | 3.587 | 1.9872 | 0 | 0 | 0
Bicker Fen 132kV | TATTERSHALL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.8843 | 18.4503 | 18.2997 | 18.0498 | 17.5399 | 16.9164 | 16.2604 | 15.4893 | 14.463 | 13.2831 | 12.0296 | 10.8339 | 9.4956 | 8.5511 | 5.0594 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0981 | 15.0233 | 14.9411 | 14.5395 | 14.2633 | 12.8434 | 11.1767 | 7.4893 | 3.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0981 | 15.0202 | 14.9365 | 14.5424 | 14.2689 | 12.8165 | 12.3603 | 11.1161 | 5.7681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0981 | 15.0675 | 15.0383 | 15.0096 | 14.9742 | 14.9435 | 14.9215 | 14.672 | 14.6023 | 14.4361 | 14.2344 | 14.0328 | 10.987 | 7.703 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0981 | 15.0191 | 14.9326 | 14.5241 | 14.2438 | 12.822 | 11.0631 | 7.4837 | 3.4575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | TRUSTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0981 | 15.0491 | 14.9935 | 14.9279 | 14.6476 | 14.0427 | 13.9033 | 13.7048 | 13.4513 | 13.1687 | 7.5919 | 2.1486 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 30.2205 | 29.4451 | 28.8473 | 27.2306 | 24.7327 | 20.1101 | 10.9478 | 7.3359 | 3.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 30.2205 | 29.4116 | 28.7808 | 27.2106 | 24.7709 | 19.8856 | 15.5628 | 10.8884 | 5.6499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 30.2205 | 29.986 | 29.5287 | 29.3173 | 29.0438 | 28.6993 | 28.2595 | 27.3467 | 25.5957 | 22.6566 | 18.9578 | 15.071 | 10.762 | 7.5453 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 30.2205 | 29.4201 | 28.753 | 27.1474 | 24.6528 | 20.0333 | 10.8365 | 7.3304 | 3.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WARTH LANE SKEGNESS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 30.2205 | 29.6137 | 29.2865 | 28.6664 | 27.609 | 25.7517 | 24.209 | 21.7356 | 17.7887 | 12.899 | 7.4364 | 2.1046 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.1566 | 9.9703 | 9.8537 | 9.5422 | 9.0013 | 8.2569 | 7.5096 | 6.814 | 5.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.1566 | 9.9619 | 9.8345 | 9.5364 | 9.011 | 8.2443 | 7.4343 | 6.6674 | 1.2468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.1566 | 10.0793 | 9.9803 | 9.9368 | 9.8894 | 9.837 | 9.7787 | 9.665 | 9.4644 | 9.1062 | 8.6778 | 8.238 | 7.313 | 3.17 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.1566 | 9.9635 | 9.8306 | 9.5209 | 8.976 | 8.228 | 7.4701 | 6.7902 | 5.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WOODHALL SPA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.1566 | 10.0012 | 9.9311 | 9.7925 | 9.5444 | 9.2582 | 8.9782 | 8.6095 | 8.1693 | 7.6583 | 1.3852 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.9078 | 10.8864 | 10.8605 | 10.8029 | 10.7576 | 10.6622 | 10.5566 | 7.3942 | 3.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.9078 | 10.8845 | 10.8566 | 10.7984 | 10.7533 | 10.6398 | 10.5107 | 10.3682 | 5.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.9078 | 10.8972 | 10.8878 | 10.8783 | 10.8768 | 10.8758 | 10.8724 | 10.8576 | 10.8247 | 10.7632 | 10.6921 | 10.6199 | 10.5634 | 7.6053 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.9078 | 10.8856 | 10.8576 | 10.7991 | 10.7543 | 10.6656 | 10.563 | 7.3888 | 3.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicker Fen 132kV | WRANGLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.9078 | 10.8932 | 10.8773 | 10.8548 | 10.8413 | 10.8228 | 10.8051 | 10.7594 | 10.692 | 10.6283 | 7.4956 | 2.1213 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ACREAGE LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 41.2079 | 45.6567 | 45.4989 | 37.3923 | 36.9343 | 35.9996 | 32.006 | 30.7568 | 29.2709 | 27.2655 | 24.9657 | 22.4175 | 19.8391 | 17.7123 | 10.1877 | 0.62738 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 41.2079 | 45.3421 | 45.0608 | 36.6374 | 36.0133 | 34.541 | 32.901 | 30.5857 | 27.5182 | 23.6345 | 19.5143 | 15.1712 | 10.3397 | 6.5 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 41.2079 | 44.6947 | 44.8025 | 36.9436 | 37.1851 | 37.1087 | 33.8883 | 33.5068 | 32.7614 | 31.5808 | 30.0016 | 28.3231 | 26.0219 | 24.4201 | 22.0134 | 18.8591 | 13.7568
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 41.2079 | 45.5967 | 45.272 | 36.905 | 36.1818 | 34.7676 | 33.3478 | 31.7649 | 29.6166 | 26.922 | 23.6269 | 19.6984 | 14.9193 | 10.4287 | 0 | 0 | 0
Chesterfield 132kV | ALFRETON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 41.2079 | 45.4755 | 45.3949 | 37.6554 | 37.6252 | 37.002 | 36.2521 | 34.874 | 32.6926 | 29.8266 | 26.6656 | 23.5851 | 19.9573 | 17.5615 | 10.367 | 0.17957 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0007 | 19.9597 | 19.9865 | 19.9626 | 19.824 | 19.6882 | 19.5536 | 19.3977 | 19.2208 | 18.9647 | 18.7232 | 18.4776 | 18.2456 | 17.8192 | 10.2492 | 0.63117 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0007 | 19.7199 | 19.7235 | 19.6676 | 19.6145 | 19.5167 | 19.3972 | 19.1456 | 18.8189 | 18.4086 | 18.1271 | 15.2628 | 10.4022 | 6.5393 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0007 | 18.8243 | 18.9038 | 18.9824 | 19.0578 | 19.1275 | 19.1898 | 19.2337 | 19.2439 | 19.2132 | 19.1416 | 19.0604 | 18.8183 | 18.6406 | 18.2969 | 17.6736 | 13.8398
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0007 | 19.9577 | 19.9788 | 19.9418 | 19.7915 | 19.615 | 19.4381 | 19.2571 | 19.0174 | 18.6744 | 18.369 | 18.113 | 15.0094 | 10.4917 | 0 | 0 | 0
Chesterfield 132kV | AMBERGATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0007 | 19.7325 | 19.7523 | 19.7588 | 19.7584 | 19.7429 | 19.7109 | 19.5456 | 19.2988 | 18.972 | 18.6513 | 18.3669 | 17.7307 | 16.661 | 10.4296 | 0.18065 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 33.3074 | 33.2172 | 33.1885 | 33.0735 | 32.9483 | 32.8203 | 32.6952 | 32.5112 | 32.3104 | 32.1391 | 31.9083 | 31.5956 | 31.3329 | 31.149 | 29.8258 | 27.4597 | 23.9448
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 33.3074 | 33.1495 | 33.0133 | 32.6332 | 32.217 | 31.7566 | 31.2679 | 30.6956 | 30.0292 | 29.3306 | 28.5794 | 27.7009 | 26.824 | 26.0108 | 13.0113 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 33.3074 | 33.1999 | 33.1611 | 33.1157 | 33.0555 | 32.9851 | 32.9043 | 32.8014 | 32.6451 | 32.4391 | 32.1915 | 31.9365 | 31.6341 | 31.4252 | 31.2199 | 30.7915 | 29.5236
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 33.3074 | 33.1443 | 32.9932 | 32.5867 | 32.1517 | 31.6754 | 31.1925 | 30.6933 | 30.1167 | 29.5386 | 28.8423 | 28.0664 | 27.1643 | 26.2204 | 9.6555 | 0 | 0
Chesterfield 132kV | ANNESLEY (KIRKBY) 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 33.3074 | 33.1841 | 33.1082 | 32.9739 | 32.8044 | 32.5952 | 32.3669 | 32.0695 | 31.6491 | 31.1583 | 30.6211 | 30.1053 | 29.5366 | 29.1473 | 27.4591 | 23.661 | 19.7878
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 52.0395 | 51.8299 | 51.6792 | 51.128 | 49.6465 | 49.0451 | 48.4584 | 47.6709 | 46.7388 | 45.6467 | 44.2421 | 42.6082 | 40.8708 | 39.6367 | 34.1631 | 27.8453 | 17.6514
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 52.0395 | 51.6768 | 51.3004 | 50.2567 | 49.2556 | 47.7977 | 46.1867 | 44.189 | 41.7058 | 38.8707 | 35.6942 | 32.2682 | 28.5438 | 25.6364 | 8.752 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 52.0395 | 51.9314 | 51.7825 | 51.7081 | 50.6427 | 50.4664 | 50.2295 | 49.8617 | 49.2246 | 48.2761 | 47.076 | 45.8312 | 44.2638 | 43.2313 | 42.1586 | 41.4112 | 37.8617
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 52.0395 | 51.6646 | 51.2371 | 50.1598 | 49.141 | 47.8212 | 46.4868 | 45.0976 | 43.2312 | 41.3424 | 38.7886 | 35.7886 | 32.1343 | 27.8408 | 6.4947 | 0 | 0
Chesterfield 132kV | ANNESLEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 52.0395 | 51.8167 | 51.6395 | 51.298 | 50.9042 | 50.3027 | 49.5976 | 48.5637 | 46.9918 | 45.048 | 42.851 | 40.7427 | 38.2884 | 36.7386 | 31.3784 | 23.4222 | 14.0284
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BILSTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.8226 | 18.8173 | 18.8072 | 18.7191 | 18.6315 | 18.5384 | 18.4555 | 18.5268 | 18.4701 | 18.4241 | 18.3829 | 18.36 | 17.6366 | 17.6148 | 13.7633 | 6.9361 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.8226 | 18.8177 | 18.8069 | 18.7209 | 18.6352 | 18.5044 | 18.4025 | 18.4171 | 18.3715 | 17.6117 | 17.5306 | 17.3848 | 15.4055 | 13.0641 | 0.10194 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.8226 | 18.8297 | 18.8376 | 18.8257 | 18.809 | 18.7874 | 18.7661 | 18.8708 | 18.8899 | 18.9023 | 18.9134 | 18.9285 | 18.9469 | 18.9666 | 18.9482 | 18.9178 | 18.7339
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.8226 | 18.8187 | 18.8046 | 18.7151 | 18.6281 | 18.5102 | 18.4138 | 18.4413 | 18.3756 | 17.6254 | 17.5705 | 17.4718 | 16.9952 | 11.0515 | 0 | 0 | 0
Chesterfield 132kV | BIWATER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.8226 | 18.828 | 18.8336 | 18.7996 | 18.7568 | 18.702 | 18.6477 | 18.7997 | 18.759 | 18.7209 | 18.6802 | 18.6424 | 18.6106 | 18.5874 | 17.3928 | 12.8729 | 5.0186
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.4361 | 17.7738 | 18.1783 | 10.4455 | 10.7238 | 10.6172 | 7.4656 | 7.2636 | 7.0546 | 6.829 | 6.5222 | 6.1542 | 5.7774 | 5.5104 | 4.4177 | 0.62626 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.4361 | 17.7256 | 18.0496 | 10.1332 | 10.2433 | 9.9195 | 9.5503 | 9.0592 | 8.502 | 7.8812 | 7.1913 | 6.4418 | 5.6434 | 4.9916 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.4361 | 17.6964 | 17.9797 | 10.3203 | 10.5885 | 10.6033 | 7.5519 | 7.4965 | 7.3864 | 7.2115 | 6.9802 | 6.74 | 6.4188 | 6.1936 | 5.8785 | 5.4484 | 4.506
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.4361 | 17.7402 | 18.032 | 10.16 | 10.2746 | 9.9792 | 9.6497 | 9.2671 | 8.824 | 8.3709 | 7.7806 | 7.1079 | 6.3012 | 5.5311 | 0 | 0 | 0
Chesterfield 132kV | BLACKWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.4361 | 17.7613 | 18.1394 | 10.4116 | 10.6838 | 10.5593 | 10.3949 | 10.1351 | 9.7732 | 9.3385 | 8.8493 | 8.3807 | 7.836 | 7.4978 | 6.371 | 0.17924 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.1264 | 6.9643 | 6.8186 | 6.4864 | 6.1735 | 5.8405 | 5.5048 | 5.0685 | 4.4996 | 3.7344 | 2.7751 | 1.7133 | 0.47522 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.1264 | 6.96 | 6.8075 | 6.4283 | 6.0707 | 5.3686 | 4.5354 | 3.4571 | 1.9887 | 0.21472 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.1264 | 7.0452 | 7.006 | 6.9665 | 6.9169 | 6.8394 | 6.7377 | 6.5433 | 6.1828 | 5.6012 | 4.839 | 4.0322 | 2.998 | 2.3059 | 1.4321 | 0.10349 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.1264 | 6.9538 | 6.7866 | 6.3952 | 6.0383 | 5.4633 | 4.8594 | 4.2067 | 3.1863 | 2.136 | 0.62546 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BLIDWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.1264 | 7.0149 | 6.9324 | 6.7969 | 6.6444 | 6.411 | 6.1115 | 5.5875 | 4.6676 | 3.4646 | 2.0685 | 0.70409 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 8.8387 | 8.9068 | 9.0586 | 9.0123 | 8.8212 | 8.5812 | 8.3256 | 7.9714 | 7.5376 | 7.0266 | 6.3895 | 5.6887 | 4.8807 | 4.3149 | 2.7301 | 0.45469 | 0.50532
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.8387 | 8.8632 | 8.9452 | 8.7595 | 8.4344 | 8.0036 | 7.5214 | 6.8847 | 6.101 | 5.2089 | 4.2279 | 3.1958 | 2.0459 | 1.2228 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.8387 | 8.8969 | 9.0113 | 9.0843 | 9.0409 | 8.9718 | 8.8803 | 8.7277 | 8.4636 | 8.0583 | 7.5364 | 6.9865 | 6.2715 | 5.8092 | 5.2224 | 4.5979 | 6.4511
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.8387 | 8.8698 | 8.9348 | 8.7538 | 8.4178 | 8.0138 | 7.5949 | 7.1401 | 6.5259 | 5.9101 | 5.0949 | 4.1651 | 3.028 | 0.14511 | 0 | 0 | 0
Chesterfield 132kV | Bolsover 11kV S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.8387 | 8.9022 | 9.0427 | 9.0485 | 8.8963 | 8.6724 | 8.403 | 7.9864 | 7.3893 | 6.6486 | 5.8133 | 5.0163 | 4.0763 | 3.5551 | 1.0901 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.3825 | 2.6048 | 2.8581 | 2.8735 | 2.7141 | 2.5296 | 2.304 | 1.9617 | 1.4689 | 0.74603 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.3825 | 2.5819 | 2.8399 | 2.8067 | 2.6196 | 2.2785 | 1.8237 | 1.1256 | 0.13547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.3825 | 2.5603 | 2.7773 | 2.8921 | 2.879 | 2.8475 | 2.7767 | 2.6065 | 2.2575 | 1.6554 | 0.84507 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.3825 | 2.5985 | 2.8406 | 2.8278 | 2.6392 | 2.3755 | 2.0728 | 1.7347 | 1.1521 | 0.50949 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | BUDBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.3825 | 2.6045 | 2.8969 | 2.9736 | 2.8855 | 2.7339 | 2.4872 | 2.0007 | 1.178 | 0.062329 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.5656 | 9.5527 | 9.4183 | 9.1037 | 8.8044 | 8.4861 | 8.1703 | 7.7772 | 7.298 | 6.6934 | 5.9504 | 5.1267 | 4.199 | 3.5237 | 0.63377 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.5656 | 9.5497 | 9.406 | 9.0478 | 8.7046 | 8.0673 | 7.3263 | 6.3959 | 5.2333 | 3.8879 | 2.3764 | 0.77648 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.5656 | 9.5878 | 9.5949 | 9.5726 | 9.537 | 9.4758 | 9.3956 | 9.2502 | 8.9834 | 8.5628 | 8.0174 | 7.4452 | 6.7158 | 6.2437 | 5.7336 | 5.0234 | 3.7099
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.5656 | 9.5442 | 9.3875 | 9.019 | 8.6796 | 8.1505 | 7.5957 | 6.9996 | 6.1317 | 5.2954 | 4.1437 | 2.7689 | 1.0816 | 0 | 0 | 0 | 0
Chesterfield 132kV | CALVERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.5656 | 9.5905 | 9.5309 | 9.4109 | 9.2696 | 9.0605 | 8.8029 | 8.3823 | 7.716 | 6.8814 | 5.9259 | 4.9985 | 3.9035 | 3.2243 | 0.91723 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 67.6522 | 67.0606 | 66.8452 | 65.7557 | 64.5805 | 61.6898 | 60.232 | 58.7254 | 56.9171 | 54.9217 | 52.4704 | 49.7434 | 46.8176 | 44.4835 | 35.2806 | 23.4735 | 10.5922
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 67.6522 | 65.5363 | 65.1648 | 63.8074 | 62.365 | 60.3025 | 58.1059 | 55.7199 | 52.7717 | 49.5099 | 45.866 | 41.864 | 37.5261 | 33.9648 | 16.0066 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 67.6522 | 67.482 | 67.2135 | 67.121 | 66.9197 | 65.2104 | 64.8883 | 64.527 | 63.8176 | 62.7442 | 61.3148 | 59.8315 | 57.9396 | 56.7075 | 54.9045 | 53.9048 | 52.3699
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 67.6522 | 65.5449 | 65.1346 | 63.7375 | 62.2692 | 60.3293 | 58.3374 | 56.478 | 53.9731 | 51.4474 | 48.2104 | 44.6284 | 40.3738 | 32.4487 | 11.0997 | 0 | 0
Chesterfield 132kV | CHESTERFIELD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 67.6522 | 67.1282 | 67.0241 | 65.1588 | 64.5303 | 63.5858 | 62.5671 | 61.4001 | 59.5552 | 57.3146 | 54.71 | 52.2181 | 49.2829 | 47.4274 | 38.9186 | 28.8419 | 25.9855
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.2706 | 15.3271 | 15.4418 | 15.5003 | 15.5817 | 15.663 | 15.2566 | 13.851 | 12.0648 | 9.8551 | 7.0081 | 3.7813 | 0.092172 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.2706 | 15.3202 | 15.4382 | 15.4649 | 15.5311 | 15.3466 | 13.428 | 10.8797 | 7.4032 | 3.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.2706 | 15.3104 | 15.401 | 15.5067 | 15.6294 | 15.7548 | 15.7709 | 15.7869 | 15.7964 | 15.8042 | 13.9558 | 11.9371 | 9.1924 | 7.2599 | 4.4624 | 0.80722 | 1.1692
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.2706 | 15.3243 | 15.4333 | 15.4813 | 15.5524 | 15.581 | 14.1225 | 12.484 | 10.074 | 7.502 | 3.6374 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.2706 | 15.3303 | 15.4718 | 15.5629 | 15.6941 | 15.7641 | 15.725 | 15.675 | 13.4357 | 10.4629 | 6.7975 | 3.1817 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 18.2912 | 17.7416 | 18.2907 | 17.838 | 17.1491 | 16.3321 | 15.2581 | 13.8524 | 12.066 | 9.856 | 7.0081 | 3.7813 | 0.092172 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 18.2912 | 17.6968 | 18.2475 | 17.6513 | 16.8673 | 15.3481 | 13.4294 | 10.8808 | 7.4032 | 3.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 18.2912 | 18.5338 | 18.3708 | 18.6887 | 18.8002 | 18.8081 | 18.6028 | 18.152 | 17.2684 | 15.8381 | 13.9572 | 11.9383 | 9.1924 | 7.2599 | 4.4624 | 0.80722 | 1.1692
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 18.2912 | 17.7137 | 18.1882 | 17.6378 | 16.8465 | 15.6319 | 14.124 | 12.4853 | 10.075 | 7.502 | 3.6374 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLIPSTONE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 18.2912 | 17.8347 | 18.5898 | 18.6638 | 18.4885 | 17.9661 | 17.1432 | 15.7418 | 13.4371 | 10.464 | 6.7975 | 3.1817 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.5389 | 11.5147 | 11.4942 | 11.4724 | 10.2225 | 10.1782 | 10.1983 | 10.2018 | 10.2056 | 10.2008 | 10.1904 | 10.1552 | 10.0279 | 9.9553 | 8.6834 | 7.2391 | 5.1352
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.5389 | 11.5031 | 11.479 | 10.1776 | 10.0355 | 9.773 | 9.6152 | 9.3871 | 9.0938 | 8.7405 | 8.3788 | 7.9882 | 7.4439 | 7.0368 | 4.0216 | 0.77977 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.5389 | 11.5183 | 11.4991 | 11.4815 | 11.4689 | 10.2399 | 11.4602 | 11.459 | 11.4534 | 11.4411 | 11.4308 | 10.273 | 10.2632 | 10.278 | 11.4026 | 10.2865 | 9.711
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.5389 | 11.5013 | 11.4784 | 10.1595 | 9.9943 | 9.732 | 9.6224 | 9.4882 | 9.2675 | 9.0412 | 8.6905 | 8.3268 | 7.861 | 7.4506 | 4.1383 | 0.64692 | 0
Chesterfield 132kV | CLOWNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.5389 | 11.5121 | 11.4884 | 10.2277 | 10.2159 | 10.1592 | 10.1639 | 10.138 | 10.061 | 9.9258 | 9.779 | 9.6419 | 9.3379 | 9.2039 | 8.04 | 6.4281 | 4.2535
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.0296 | 6.931 | 6.8966 | 6.8322 | 6.7535 | 6.6624 | 6.5773 | 6.4745 | 6.3822 | 6.321 | 6.2543 | 6.1757 | 6.1361 | 6.0856 | 5.6378 | 4.7936 | 4.8799
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.0296 | 6.9072 | 6.8308 | 6.6675 | 6.4945 | 6.28 | 6.0587 | 5.8166 | 5.5811 | 5.361 | 5.1435 | 4.8975 | 4.6727 | 4.4476 | 2.184 | 0.42423 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.0296 | 6.9368 | 6.9095 | 6.8917 | 6.867 | 6.8415 | 6.8158 | 6.7828 | 6.7429 | 6.7072 | 6.675 | 6.6495 | 6.6285 | 6.6148 | 6.6385 | 6.6422 | 7.6698
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.0296 | 6.9028 | 6.8184 | 6.648 | 6.4713 | 6.264 | 6.0485 | 5.8156 | 5.5492 | 4.0888 | 3.8618 | 3.6518 | 3.434 | 0 | 0 | 0 | 0
Chesterfield 132kV | CRAGGS LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.0296 | 6.9278 | 6.8829 | 6.824 | 6.7482 | 6.6591 | 6.5702 | 6.4682 | 6.3617 | 6.2655 | 6.1748 | 6.104 | 6.0423 | 3.5263 | 2.3175 | 1.5687 | 3.0358
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.1668 | 16.5635 | 16.4463 | 16.1696 | 15.8544 | 15.5281 | 15.2258 | 13.8651 | 12.077 | 9.865 | 7.0117 | 3.7832 | 0.092219 | 0 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.1668 | 16.5626 | 16.4429 | 16.1655 | 15.8499 | 15.3621 | 13.4416 | 10.8907 | 7.4069 | 3.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.1668 | 17.154 | 16.581 | 16.5604 | 16.5121 | 16.4623 | 16.4237 | 16.3738 | 16.3161 | 15.8525 | 13.9699 | 11.9491 | 9.197 | 7.2636 | 4.4646 | 0.80763 | 1.1698
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.1668 | 16.5562 | 16.4229 | 16.1281 | 15.7994 | 15.456 | 14.1368 | 12.4967 | 10.0842 | 7.5058 | 3.6393 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | CROWN FM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.1668 | 16.5962 | 16.5288 | 16.4397 | 16.3003 | 16.1372 | 15.9965 | 15.7562 | 13.4493 | 10.4735 | 6.801 | 3.1833 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.5776 | 13.2511 | 13.1995 | 13.0324 | 12.9187 | 12.7132 | 12.5244 | 12.2654 | 11.9387 | 11.5055 | 10.9686 | 10.3872 | 9.647 | 9.0816 | 7.149 | 4.9082 | 2.3372
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.5776 | 13.2514 | 13.1993 | 13.0347 | 12.9226 | 12.623 | 12.2983 | 11.8578 | 11.2714 | 10.546 | 9.7253 | 8.85 | 7.7874 | 6.947 | 3.5789 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.5776 | 13.5575 | 13.2836 | 13.276 | 13.2978 | 13.2954 | 13.2817 | 13.2112 | 13.063 | 12.7966 | 12.4398 | 12.0652 | 11.5489 | 11.219 | 10.6812 | 9.9703 | 9.0273
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.5776 | 13.2539 | 13.205 | 13.0394 | 12.9308 | 12.692 | 12.4526 | 12.174 | 11.7641 | 11.3021 | 10.6254 | 9.8153 | 8.752 | 7.7742 | 0.54517 | 0 | 0
Chesterfield 132kV | DANESMOOR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.5776 | 13.2726 | 13.2555 | 13.206 | 13.196 | 13.0956 | 12.9801 | 12.7503 | 12.3537 | 11.8178 | 11.2012 | 10.5996 | 9.8064 | 9.3077 | 7.732 | 4.1849 | 1.746
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.9554 | 16.8818 | 16.7526 | 16.4381 | 16.1412 | 15.8317 | 15.5644 | 15.3259 | 15.1893 | 13.4629 | 13.1573 | 12.6728 | 12.0604 | 11.5604 | 9.3755 | 6.2351 | 2.2863
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.9554 | 16.8804 | 16.7501 | 16.4315 | 16.1283 | 15.8093 | 15.5209 | 15.2657 | 13.5152 | 13.2939 | 12.829 | 12.2107 | 11.5069 | 10.9861 | 8.575 | 5.1715 | 1.1131
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.9554 | 16.9372 | 16.8974 | 16.8566 | 16.8004 | 16.7302 | 16.6518 | 16.5518 | 16.3726 | 16.123 | 15.8148 | 15.519 | 15.2261 | 15.1441 | 13.6115 | 13.5522 | 12.9501
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.9554 | 16.8754 | 16.7291 | 16.3947 | 16.084 | 15.7677 | 15.5069 | 15.3184 | 15.1896 | 13.4875 | 13.2134 | 12.714 | 11.9993 | 11.3434 | 8.1293 | 4.3263 | 0.30767
Chesterfield 132kV | ECKINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.9554 | 16.9166 | 16.8387 | 16.7155 | 16.5726 | 16.3801 | 16.1797 | 15.9335 | 15.5898 | 15.2653 | 13.5342 | 13.3332 | 12.8917 | 12.613 | 11.6535 | 9.8123 | 7.3889
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Best View | Headroom (MW) | 32.7879 | 32.7661 | 31.4969 | 31.4706 | 31.4262 | 31.4264 | 31.3501 | 31.2794 | 31.1613 | 31.0773 | 30.9638 | 30.8166 | 30.6873 | 30.5472 | 29.6065 | 28.7804 | 27.6542
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.7879 | 32.7438 | 31.4845 | 31.4206 | 31.3149 | 31.2406 | 31.0811 | 30.9438 | 30.7508 | 30.599 | 30.4308 | 30.2218 | 30.02 | 29.8068 | 28.4601 | 27.2743 | 25.9593
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.7879 | 32.7712 | 32.7557 | 31.4925 | 31.4863 | 31.4949 | 31.4909 | 31.4896 | 31.4844 | 31.4791 | 31.4719 | 31.4636 | 31.4544 | 31.4441 | 31.3971 | 31.3698 | 31.2106
Chesterfield 132kV | Erin Road | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.7879 | 32.7427 | 31.4833 | 31.4121 | 31.2955 | 31.2441 | 31.0559 | 30.8975 | 30.6718 | 30.4915 | 30.2801 | 30.0519 | 29.8333 | 29.6191 | 28.2497 | 26.9882 | 25.1853
Chesterfield 132kV | Erin Road | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.7879 | 32.7606 | 31.4948 | 31.4775 | 31.4452 | 31.438 | 31.3859 | 31.3498 | 31.2744 | 31.216 | 31.1425 | 31.0693 | 30.9936 | 30.9182 | 30.3625 | 29.811 | 29.1558
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.6086 | 12.5761 | 12.5461 | 12.4694 | 12.3967 | 12.3262 | 12.2598 | 12.1903 | 12.1292 | 12.0808 | 11.9088 | 11.8772 | 11.8259 | 11.7687 | 11.3901 | 10.8664 | 10.2229
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.6086 | 12.5762 | 12.5457 | 12.469 | 12.3964 | 12.3266 | 12.2596 | 12.1929 | 12.1349 | 12.0872 | 12.0589 | 11.8891 | 11.8404 | 11.7818 | 11.3911 | 10.8299 | 10.2216
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.6086 | 12.5887 | 12.5806 | 12.5727 | 12.5609 | 12.5491 | 12.5369 | 12.5244 | 12.509 | 12.4955 | 12.4841 | 12.4748 | 12.4683 | 12.4642 | 12.4835 | 12.4713 | 12.3742
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.6086 | 12.5747 | 12.5404 | 12.4612 | 12.3875 | 12.3152 | 12.2461 | 12.1816 | 12.1225 | 12.0737 | 11.9071 | 11.8742 | 11.8204 | 11.7578 | 11.3011 | 10.7128 | 10.0069
Chesterfield 132kV | EYAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.6086 | 12.5832 | 12.5654 | 12.5368 | 12.5033 | 12.4663 | 12.4303 | 12.3947 | 12.3604 | 12.3261 | 12.2944 | 12.2668 | 12.2437 | 12.2239 | 12.0918 | 11.7948 | 11.4936
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.2371 | 7.1391 | 6.9897 | 6.6492 | 6.3285 | 5.9871 | 5.643 | 5.1957 | 4.6125 | 3.8281 | 2.8447 | 1.7563 | 0.48715 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.2371 | 7.1347 | 6.9784 | 6.5896 | 6.2231 | 5.5034 | 4.6492 | 3.5439 | 2.0386 | 0.22011 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.2371 | 7.222 | 7.1819 | 7.1414 | 7.0905 | 7.0111 | 6.9068 | 6.7076 | 6.338 | 5.7418 | 4.9605 | 4.1334 | 3.0733 | 2.3637 | 1.468 | 0.10608 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.2371 | 7.1284 | 6.957 | 6.5557 | 6.1898 | 5.6004 | 4.9813 | 4.3123 | 3.2663 | 2.1896 | 0.64115 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | FARNSFIELD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.2371 | 7.1909 | 7.1064 | 6.9675 | 6.8112 | 6.5719 | 6.2649 | 5.7278 | 4.7847 | 3.5515 | 2.1204 | 0.72176 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 100.6623 | 100.121 | 99.6568 | 98.2911 | 96.9149 | 96.6745 | 95.3186 | 93.7809 | 92.3627 | 91.354 | 91.4465 | 90.2485 | 82.2815 | 82.0378 | 77.2764 | 65.7472 | 50.68
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 100.6623 | 99.8528 | 99.0176 | 96.9835 | 94.9288 | 93.7304 | 91.8248 | 82.509 | 82.2196 | 81.6075 | 81.6674 | 80.5965 | 79.4561 | 78.1652 | 67.3341 | 51.0035 | 33.7969
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 100.6623 | 100.2744 | 100.0649 | 99.8827 | 99.6053 | 100.1608 | 99.9914 | 99.8177 | 99.5554 | 99.3266 | 99.8769 | 99.9284 | 100.0477 | 100.2329 | 101.4369 | 101.7858 | 101.148
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 100.6623 | 99.8337 | 98.9236 | 96.7901 | 94.6764 | 93.7827 | 91.6979 | 82.5044 | 82.1055 | 81.277 | 80.874 | 79.6395 | 78.2068 | 76.6292 | 63.7043 | 45.6013 | 24.5601
Chesterfield 132kV | GOITSIDE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 100.6623 | 100.0891 | 99.6136 | 98.912 | 98.0145 | 97.818 | 96.9182 | 96.0268 | 95.1014 | 94.2767 | 95.3375 | 94.6652 | 94.1145 | 93.7246 | 82.1673 | 78.7646 | 72.4584
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 21.8604 | 21.7601 | 21.657 | 21.3349 | 21.0205 | 20.6787 | 20.3576 | 19.9928 | 19.6755 | 19.4813 | 19.5694 | 19.2714 | 19.0997 | 18.8987 | 17.1134 | 13.8589 | 8.9594
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 21.8604 | 21.6693 | 21.4389 | 20.8586 | 20.2875 | 19.7275 | 19.183 | 18.6067 | 18.1063 | 17.5862 | 17.603 | 17.0965 | 16.6824 | 16.2464 | 12.9931 | 8.472 | 2.8065
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 21.8604 | 21.7924 | 21.726 | 21.6582 | 21.5724 | 21.4851 | 21.3961 | 21.3137 | 21.2233 | 21.1482 | 21.2694 | 21.2765 | 21.3078 | 21.362 | 21.7585 | 21.933 | 21.0709
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 21.8604 | 21.6563 | 21.3965 | 20.7778 | 20.1829 | 19.5851 | 18.9877 | 18.4051 | 17.7555 | 17.3035 | 17.1275 | 16.6537 | 16.1794 | 15.661 | 11.788 | 6.6305 | 0
Chesterfield 132kV | GOITSIDE 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 21.8604 | 21.7409 | 21.6076 | 21.3941 | 21.1382 | 20.85 | 20.5664 | 20.2857 | 20.0188 | 19.8085 | 20.0613 | 19.9004 | 19.7803 | 19.6978 | 18.8242 | 16.7399 | 13.9344
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.3136 | 20.1419 | 19.9541 | 19.481 | 19.0121 | 16.9744 | 16.4001 | 15.7375 | 15.1186 | 14.4585 | 13.5746 | 12.5603 | 11.5245 | 10.6718 | 6.9675 | 3.2796 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.3136 | 18.676 | 18.4432 | 17.8864 | 17.3369 | 16.5263 | 15.6938 | 14.7146 | 13.6579 | 12.5097 | 11.1564 | 9.6658 | 8.0912 | 6.7476 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.3136 | 20.2307 | 20.1605 | 20.0918 | 20.0107 | 18.4566 | 18.3486 | 18.1854 | 17.9775 | 17.6629 | 17.1937 | 16.704 | 16.0967 | 15.7051 | 15.1974 | 15.8362 | 14.1981
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.3136 | 18.6663 | 18.4098 | 17.8262 | 17.2651 | 16.4877 | 15.7116 | 14.9133 | 14.0025 | 13.1124 | 11.9222 | 10.5685 | 8.9915 | 5.4066 | 0 | 0 | 0
Chesterfield 132kV | GRASSMOOR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.3136 | 20.184 | 20.0507 | 18.4047 | 18.1629 | 17.7991 | 17.4312 | 16.9415 | 16.3533 | 15.6506 | 14.7421 | 13.8638 | 12.8556 | 12.1963 | 8.7445 | 6.3271 | 1.6009
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.2667 | 10.0554 | 9.9733 | 9.9314 | 9.7463 | 9.563 | 9.3879 | 9.2172 | 9.0466 | 8.8862 | 8.7319 | 8.5787 | 8.434 | 8.2929 | 7.2703 | 5.8658 | 4.0889
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.2667 | 10.0586 | 9.9844 | 9.7946 | 9.6081 | 9.4289 | 9.2579 | 9.0849 | 8.9255 | 8.7839 | 8.6449 | 8.4817 | 8.3474 | 8.2152 | 7.4577 | 6.2171 | 10.1557
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.2667 | 10.2416 | 10.0602 | 10.0298 | 9.9988 | 9.9659 | 9.9324 | 9.8967 | 9.8542 | 9.8165 | 9.7834 | 9.7551 | 9.7356 | 9.722 | 9.7579 | 9.738 | 9.4811
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.2667 | 10.0554 | 9.971 | 9.7713 | 9.5782 | 9.391 | 9.2126 | 9.042 | 8.8764 | 8.7186 | 8.5653 | 8.4158 | 8.274 | 8.2899 | 7.2255 | 11.3679 | 6.9196
Chesterfield 132kV | HALFWAY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.2667 | 10.0752 | 10.0298 | 9.956 | 9.8694 | 9.7737 | 9.6854 | 9.5963 | 9.5102 | 9.433 | 9.3675 | 9.3107 | 9.2618 | 9.2277 | 9.1335 | 8.577 | 13.2802
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.6828 | 15.5488 | 15.469 | 15.5223 | 15.6521 | 15.6801 | 15.7585 | 15.8238 | 15.9321 | 16.0685 | 16.2601 | 16.4089 | 16.4614 | 16.5078 | 16.6101 | 15.6618 | 13.9736
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.6828 | 15.5507 | 15.4727 | 15.5222 | 15.649 | 15.6777 | 15.7513 | 15.8206 | 15.9418 | 16.0816 | 16.2904 | 16.4363 | 16.4746 | 16.507 | 16.5124 | 14.8086 | 12.769
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.6828 | 15.6606 | 15.5598 | 15.7467 | 15.9427 | 16.1328 | 16.32 | 16.4702 | 16.6401 | 16.8395 | 17.0718 | 17.3348 | 17.6262 | 17.9332 | 19.4586 | 19.5539 | 19.2118
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.6828 | 15.5491 | 15.4651 | 15.5413 | 15.672 | 15.7982 | 15.8947 | 15.9681 | 16.0248 | 16.0936 | 16.1506 | 16.2192 | 16.2993 | 16.382 | 16.7035 | 15.2493 | 7.7941
Chesterfield 132kV | HOLME CARR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.6828 | 15.572 | 15.5302 | 15.6944 | 15.9206 | 16.0381 | 16.2004 | 16.3631 | 16.5622 | 16.777 | 17.0609 | 17.3282 | 17.476 | 17.6274 | 18.2433 | 17.8603 | 17.0643
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 30.6681 | 30.6711 | 30.6717 | 30.6485 | 30.5904 | 30.4497 | 30.3005 | 30.0363 | 29.7227 | 29.3494 | 28.8158 | 28.1226 | 27.4432 | 26.995 | 24.8794 | 21.2497 | 15.9413
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 30.6681 | 30.6573 | 30.6199 | 30.3272 | 29.8709 | 29.1459 | 28.3643 | 27.3505 | 26.1764 | 24.8544 | 23.385 | 21.7574 | 20.0731 | 18.8389 | 12.5541 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 30.6681 | 30.6727 | 30.6692 | 30.6707 | 30.6704 | 30.6651 | 30.6542 | 30.6244 | 30.5303 | 30.3065 | 29.9359 | 29.5006 | 28.8974 | 28.5151 | 28.4909 | 28.3435 | 26.784
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 30.6681 | 30.6562 | 30.605 | 30.2841 | 29.8024 | 29.0965 | 28.4109 | 27.6903 | 26.7768 | 25.8489 | 24.6225 | 23.2094 | 21.5209 | 19.2054 | 9.6337 | 0 | 0
Chesterfield 132kV | HUCKNALL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 30.6681 | 30.6686 | 30.6649 | 30.6421 | 30.582 | 30.405 | 30.1538 | 29.7363 | 29.1065 | 28.2794 | 27.3392 | 26.4451 | 25.4148 | 24.8395 | 22.7817 | 18.8434 | 14.7792
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.8137 | 2.7262 | 2.7395 | 2.6021 | 2.3854 | 2.3083 | 2.1965 | 2.0842 | 1.9755 | 1.9477 | 1.9244 | 1.8511 | 1.8783 | 1.9096 | 1.435 | 3.3428 | 1.0095
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.8137 | 2.6482 | 2.5485 | 2.1856 | 1.8904 | 1.5907 | 1.2513 | 0.91675 | 0.59334 | 0.31812 | 0.051593 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.8137 | 2.7702 | 2.7047 | 2.6655 | 2.5084 | 2.5097 | 2.4596 | 2.4244 | 2.3668 | 2.3239 | 2.2994 | 2.2884 | 2.2922 | 2.3047 | 2.4695 | 5.5475 | 5.0188
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.8137 | 2.6422 | 2.521 | 2.1409 | 1.8336 | 1.5376 | 1.1746 | 0.83339 | 0.49645 | 0.17488 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | HUTHWAITE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.8137 | 2.689 | 2.6545 | 2.5234 | 2.4318 | 2.3078 | 2.1393 | 1.9916 | 1.8263 | 1.6839 | 1.5733 | 1.4876 | 1.4305 | 1.4036 | 0.96082 | 1.3108 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.9804 | 21.6038 | 13.8666 | 12.4766 | 10.9301 | 9.4432 | 8.0826 | 6.6268 | 5.2978 | 4.1458 | 2.8806 | 1.3582 | 0.21516 | 0 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.9804 | 21.5236 | 13.6495 | 11.9948 | 10.3312 | 8.5343 | 6.8157 | 5.0145 | 3.2896 | 1.6348 | 0 | 0 | 0 | 0 | 1.8887 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.9804 | 21.8091 | 14.3971 | 14.2405 | 13.8974 | 13.6504 | 13.4496 | 13.2536 | 13.0073 | 12.7092 | 12.378 | 12.1065 | 11.8083 | 11.7289 | 12.4221 | 12.1945 | 13.5096
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.9804 | 21.4963 | 13.5335 | 11.7982 | 10.0813 | 8.2374 | 6.4723 | 4.7804 | 3.0536 | 1.3941 | 0 | 0 | 0 | 5.1084 | 0 | 0 | 0
Chesterfield 132kV | LIME TREE PLACE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.9804 | 21.7182 | 14.1537 | 13.5898 | 12.894 | 12.008 | 11.1891 | 10.3805 | 9.5476 | 8.6623 | 7.7998 | 7.0643 | 6.2099 | 5.7101 | 21.0312 | 18.4765 | 1.8336
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.2015 | 21.821 | 13.9735 | 12.5728 | 11.0144 | 9.516 | 8.1449 | 6.6779 | 5.3386 | 4.1778 | 2.9028 | 1.3687 | 0.21682 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.2015 | 21.74 | 13.7547 | 12.0873 | 10.4108 | 8.6001 | 6.8682 | 5.0532 | 3.3149 | 1.6474 | 0 | 0 | 0 | 0 | 1.9033 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.2015 | 22.0284 | 14.5081 | 14.3503 | 14.0045 | 13.7557 | 13.5533 | 13.3558 | 13.1076 | 12.8072 | 12.4735 | 12.1998 | 11.8993 | 11.8193 | 12.5179 | 12.2885 | 13.6137
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.2015 | 21.7125 | 13.6379 | 11.8892 | 10.159 | 8.3009 | 6.5222 | 4.8172 | 3.0771 | 1.4049 | 0 | 0 | 0 | 5.1478 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.2015 | 21.9366 | 14.2628 | 13.6946 | 12.9934 | 12.1005 | 11.2753 | 10.4605 | 9.6212 | 8.729 | 7.8599 | 7.1187 | 6.2578 | 5.7541 | 21.1933 | 18.6189 | 1.852
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 22.1408 | 21.7613 | 13.9395 | 12.5423 | 10.9877 | 9.4929 | 8.1251 | 6.6616 | 5.3257 | 4.1677 | 2.8958 | 1.3654 | 0.21629 | 0 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 22.1408 | 21.6806 | 13.7213 | 12.0579 | 10.3855 | 8.5793 | 6.8516 | 5.0409 | 3.3069 | 1.6434 | 0 | 0 | 0 | 0 | 1.8986 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 22.1408 | 21.9682 | 14.4728 | 14.3154 | 13.9705 | 13.7223 | 13.5203 | 13.3234 | 13.0757 | 12.776 | 12.4432 | 12.1702 | 11.8704 | 11.7906 | 12.4875 | 12.2586 | 13.5807
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 22.1408 | 21.6531 | 13.6047 | 11.8603 | 10.1344 | 8.2807 | 6.5064 | 4.8055 | 3.0696 | 1.4014 | 0 | 0 | 0 | 5.1353 | 0 | 0 | 0
Chesterfield 132kV | MANSFIELD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 22.1408 | 21.8766 | 14.2282 | 13.6613 | 12.9618 | 12.0712 | 11.2479 | 10.4351 | 9.5978 | 8.7078 | 7.8408 | 7.1014 | 6.2426 | 5.7402 | 21.1418 | 18.5737 | 1.847
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.7995 | 21.5797 | 21.5954 | 21.4937 | 21.3271 | 21.161 | 21.0014 | 20.7971 | 20.6011 | 20.3925 | 20.1965 | 19.9857 | 19.7973 | 17.6804 | 10.1694 | 0.62626 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.7995 | 21.5675 | 21.5774 | 21.4306 | 21.2297 | 21.0213 | 20.8227 | 20.5815 | 20.3566 | 20.1099 | 19.4792 | 15.144 | 10.3212 | 6.4884 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.7995 | 21.8052 | 21.6167 | 21.6445 | 21.6162 | 21.5854 | 21.5558 | 21.5074 | 21.4478 | 21.396 | 21.3425 | 21.2893 | 21.2409 | 21.1916 | 21.0683 | 18.8253 | 13.7321
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.7995 | 21.5667 | 21.5617 | 21.4222 | 21.2224 | 21.0158 | 20.8093 | 20.5626 | 20.3127 | 20.0156 | 19.7715 | 19.5612 | 14.8925 | 10.41 | 0 | 0 | 0
Chesterfield 132kV | MEADOW LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.7995 | 21.5898 | 21.639 | 21.6205 | 21.5343 | 21.4246 | 21.3183 | 21.1779 | 21.0396 | 20.886 | 20.7497 | 20.6255 | 19.9214 | 17.53 | 10.3484 | 0.17924 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.7689 | 8.7213 | 8.6909 | 8.5273 | 8.3596 | 8.1686 | 7.8953 | 7.4948 | 6.9139 | 6.0877 | 5.0266 | 3.845 | 0.093725 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.7689 | 8.7161 | 8.6831 | 8.4841 | 8.2842 | 7.8682 | 7.3037 | 6.4862 | 5.2387 | 3.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.7689 | 8.7554 | 8.7753 | 8.7882 | 8.7947 | 8.7725 | 8.675 | 8.4654 | 8.0568 | 7.3819 | 6.486 | 5.5207 | 4.2628 | 3.417 | 2.1631 | 0.43565 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.7689 | 8.7157 | 8.6729 | 8.4754 | 8.2731 | 7.9621 | 7.5766 | 7.1488 | 6.3817 | 5.5292 | 3.6987 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | OLLERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.7689 | 8.7469 | 8.7619 | 8.7189 | 8.6637 | 8.5091 | 8.2316 | 7.698 | 6.7149 | 5.3875 | 3.8244 | 2.2804 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.3796 | 24.3425 | 24.2819 | 23.8364 | 23.7362 | 23.6269 | 23.525 | 23.4115 | 23.3048 | 23.2238 | 23.1388 | 23.0372 | 22.9658 | 22.8919 | 22.3409 | 21.1232 | 19.9529
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.3796 | 24.3207 | 23.8579 | 23.6996 | 23.5224 | 23.3428 | 23.1666 | 22.9834 | 22.8082 | 22.6485 | 22.4914 | 22.3011 | 22.1325 | 21.9596 | 20.1236 | 18.3183 | 16.6079
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.3796 | 24.3396 | 24.2823 | 23.8694 | 23.8034 | 23.7333 | 23.6619 | 23.5876 | 23.5076 | 23.4325 | 23.3608 | 23.2952 | 23.2316 | 23.1723 | 22.953 | 22.7296 | 22.3198
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.3796 | 24.3208 | 23.855 | 23.6942 | 23.5146 | 23.3286 | 23.1462 | 22.9658 | 22.784 | 22.6074 | 22.4269 | 22.2469 | 22.0625 | 20.5649 | 19.3258 | 26.6805 | 25.1621
Chesterfield 132kV | PINXTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.3796 | 24.3363 | 23.8971 | 23.8185 | 23.7139 | 23.5981 | 23.4821 | 23.3644 | 23.248 | 23.1377 | 23.0302 | 22.9307 | 22.8401 | 22.7583 | 21.5749 | 20.6067 | 19.6295
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 39.5277 | 39.4425 | 39.3754 | 39.2259 | 39.0721 | 38.913 | 38.7623 | 38.6079 | 38.4778 | 38.437 | 38.3154 | 38.1769 | 38.0634 | 37.9511 | 37.2195 | 36.2391 | 33.4191
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 39.5277 | 39.4232 | 39.3269 | 39.1165 | 38.9044 | 38.6954 | 38.4967 | 38.3001 | 38.1271 | 37.9678 | 37.8138 | 37.632 | 37.4804 | 37.3212 | 36.397 | 33.5821 | 32.1696
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 39.5277 | 39.4488 | 39.4032 | 39.3596 | 39.3032 | 39.2497 | 39.1964 | 39.1452 | 39.0868 | 39.0309 | 38.9822 | 38.9396 | 38.9049 | 38.878 | 38.8252 | 38.7484 | 38.4033
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 39.5277 | 39.4205 | 39.3166 | 39.1034 | 38.8871 | 38.6708 | 38.4591 | 38.267 | 38.0872 | 37.9138 | 37.7467 | 37.5916 | 37.4334 | 37.2722 | 36.2982 | 33.3501 | 31.5679
Chesterfield 132kV | QUEENS PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 39.5277 | 39.4383 | 39.3726 | 39.2829 | 39.1714 | 39.0503 | 38.9329 | 38.8215 | 38.7137 | 38.6114 | 38.5182 | 38.4349 | 38.3639 | 38.2998 | 37.9331 | 37.2872 | 36.4616
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.3579 | 7.3269 | 7.2915 | 7.218 | 7.1455 | 7.0314 | 6.9101 | 6.6986 | 6.3515 | 5.796 | 5.069 | 4.2834 | 3.2876 | 2.5772 | 1.0698 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.3579 | 7.3255 | 7.2863 | 7.2064 | 7.125 | 6.8057 | 6.3962 | 5.784 | 4.7737 | 3.4443 | 1.89 | 0.30514 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.3579 | 7.3414 | 7.3271 | 7.3108 | 7.2983 | 7.2635 | 7.2014 | 7.0567 | 6.767 | 6.2665 | 5.5976 | 4.874 | 3.9387 | 3.2896 | 2.2553 | 0.77496 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.3579 | 7.3283 | 7.2912 | 7.2117 | 7.1326 | 6.8993 | 6.6634 | 6.3761 | 5.7965 | 5.1214 | 4.0228 | 2.6171 | 0.7873 | 0 | 0 | 0 | 0
Chesterfield 132kV | RAVENSDALE PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.3579 | 7.3402 | 7.3197 | 7.2871 | 7.2484 | 7.1469 | 6.9884 | 6.6271 | 5.8814 | 4.8468 | 3.6198 | 2.4057 | 0.91464 | 0 | 0 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1711 | 20.1441 | 20.1168 | 20.0884 | 20.0615 | 20.0333 | 20.0058 | 19.9792 | 19.9527 | 19.9269 | 19.9015 | 19.8758 | 19.8514 | 19.8273 | 19.7044 | 19.5779 | 10.5763
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1711 | 20.1433 | 20.1152 | 20.0863 | 20.0578 | 20.0298 | 20.0025 | 19.9744 | 19.9472 | 19.9206 | 19.8938 | 19.8667 | 19.8408 | 19.8151 | 15.9826 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1711 | 20.1441 | 20.1173 | 20.0907 | 20.0644 | 20.0385 | 20.0129 | 19.9877 | 19.9618 | 19.9362 | 19.9112 | 19.8866 | 19.8625 | 19.8388 | 19.7272 | 19.6205 | 19.5126
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1711 | 20.1434 | 20.1151 | 20.0853 | 20.057 | 20.0281 | 19.9998 | 19.9721 | 19.945 | 19.9177 | 19.891 | 19.865 | 19.8392 | 19.8138 | 11.083 | 0 | 0
Chesterfield 132kV | ROBERT HYDE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1711 | 20.144 | 20.1163 | 20.089 | 20.0619 | 20.0345 | 20.0074 | 19.9815 | 19.9551 | 19.9292 | 19.9038 | 19.8787 | 19.8545 | 19.8306 | 19.7118 | 19.5913 | 19.4725
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.9606 | 5.9357 | 5.9031 | 5.8237 | 5.7467 | 5.6723 | 5.6012 | 5.5262 | 5.457 | 5.3999 | 5.3405 | 5.2724 | 5.2092 | 5.146 | 4.7617 | 4.2516 | 6.0328
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.9606 | 5.9355 | 5.9023 | 5.8228 | 5.7467 | 5.6738 | 5.604 | 5.532 | 5.4671 | 5.4105 | 5.3572 | 5.2907 | 5.2293 | 5.1666 | 4.7883 | 4.2959 | 6.0761
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.9606 | 5.9514 | 5.9426 | 5.9345 | 5.9223 | 5.9087 | 5.8953 | 5.8824 | 5.8682 | 5.8543 | 5.8427 | 5.8361 | 5.8314 | 5.8298 | 5.864 | 5.8866 | 8.3291
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.9606 | 5.9344 | 5.8985 | 5.8162 | 5.7392 | 5.6639 | 5.5906 | 5.5217 | 5.4526 | 5.3924 | 5.3318 | 5.27 | 5.2106 | 5.1445 | 4.711 | 4.1646 | 5.8421
Chesterfield 132kV | ROBIN HOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.9606 | 5.9446 | 5.9266 | 5.8979 | 5.8636 | 5.8255 | 5.7881 | 5.7526 | 5.7175 | 5.6869 | 5.659 | 5.6359 | 5.6192 | 5.6069 | 5.5114 | 5.2933 | 7.3718
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.5445 | 9.5711 | 9.5574 | 9.556 | 9.476 | 9.3762 | 9.2649 | 9.0855 | 8.8202 | 8.4506 | 7.0833 | 3.8218 | 0.093161 | 0 | 0 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.5445 | 9.566 | 9.5506 | 9.5318 | 9.4385 | 9.1906 | 8.884 | 8.4488 | 7.4825 | 3.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.5445 | 9.5751 | 9.5885 | 9.6757 | 9.6861 | 9.6792 | 9.6559 | 9.575 | 9.3992 | 9.1048 | 8.7141 | 8.2944 | 7.7487 | 7.3378 | 4.5102 | 0.81588 | 1.1817
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.5445 | 9.5696 | 9.5511 | 9.547 | 9.4543 | 9.2732 | 9.0738 | 8.8382 | 8.4352 | 7.5825 | 3.6764 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | RUFFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.5445 | 9.5815 | 9.592 | 9.656 | 9.6331 | 9.5578 | 9.4494 | 9.2139 | 8.7696 | 8.1735 | 6.8704 | 3.2158 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 15.8521 | 15.7231 | 15.6383 | 15.3611 | 15.0867 | 14.8055 | 14.5131 | 14.1855 | 13.8548 | 13.554 | 13.2619 | 12.948 | 12.6951 | 12.4382 | 10.9085 | 8.271 | 5.4835
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 15.8521 | 15.6914 | 15.5657 | 15.2377 | 14.9064 | 14.5757 | 14.2242 | 13.8626 | 13.5062 | 13.1697 | 12.8539 | 12.4538 | 12.0955 | 11.7284 | 9.8141 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 15.8521 | 15.7506 | 15.7313 | 15.687 | 15.637 | 15.5887 | 15.531 | 15.4644 | 15.3764 | 15.2926 | 15.2111 | 15.1371 | 15.0706 | 15.0152 | 14.9728 | 14.8108 | 14.3181
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 15.8521 | 15.6995 | 15.576 | 15.236 | 14.8997 | 14.5553 | 14.1856 | 13.811 | 13.4253 | 13.0173 | 12.6218 | 12.2939 | 11.9781 | 11.6549 | 9.5283 | 0 | 0
Chesterfield 132kV | SHEEPBRIDGE 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 15.8521 | 15.7206 | 15.653 | 15.5282 | 15.3791 | 15.2095 | 15.0302 | 14.839 | 14.634 | 14.4239 | 14.2312 | 14.066 | 13.9109 | 13.7732 | 13.0539 | 11.6563 | 16.237
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 24.0531 | 24.0462 | 24.0329 | 23.9633 | 23.8941 | 24.0384 | 23.9872 | 23.9239 | 23.8559 | 23.8073 | 23.9173 | 23.8438 | 23.7936 | 23.7532 | 23.3452 | 22.6545 | 21.1343
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 24.0531 | 24.0232 | 23.9798 | 23.8646 | 23.7501 | 23.7799 | 23.6969 | 23.6423 | 23.4458 | 23.3683 | 23.4831 | 23.3982 | 23.2995 | 23.2056 | 22.4975 | 20.7826 | 18.7887
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 24.0531 | 24.0491 | 24.0445 | 24.0325 | 24.021 | 24.1557 | 24.1636 | 24.1689 | 24.163 | 24.1595 | 24.2573 | 24.2824 | 24.3097 | 24.34 | 24.4493 | 24.4698 | 24.2997
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 24.0531 | 24.0254 | 23.9812 | 23.8597 | 23.742 | 23.8338 | 23.7375 | 23.6567 | 23.4623 | 23.3654 | 23.4103 | 23.2982 | 23.1807 | 23.0727 | 22.1622 | 20.2529 | 17.8773
Chesterfield 132kV | SHEFFIELD ROAD 33 11 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 24.0531 | 24.0366 | 24.0142 | 23.9739 | 23.9241 | 24.0133 | 23.9805 | 23.9474 | 23.9023 | 23.8611 | 24.0654 | 24.0296 | 23.9992 | 23.9833 | 23.7586 | 23.228 | 22.6405
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.6532 | 20.6269 | 20.5996 | 20.5702 | 20.5412 | 20.5123 | 20.484 | 20.4542 | 20.4237 | 20.3905 | 20.3567 | 20.3222 | 20.2891 | 20.2547 | 20.0935 | 19.9203 | 19.7501
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.6532 | 20.6269 | 20.5996 | 20.5703 | 20.5412 | 20.5013 | 20.4585 | 20.4151 | 20.3624 | 20.3089 | 20.2522 | 20.1891 | 20.1224 | 20.0426 | 12.7895 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.6532 | 20.6269 | 20.6007 | 20.5748 | 20.5492 | 20.523 | 20.497 | 20.4695 | 20.4414 | 20.4113 | 20.3815 | 20.351 | 20.3214 | 20.2921 | 20.1552 | 20.0129 | 19.875
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.6532 | 20.6269 | 20.5992 | 20.5706 | 20.5422 | 20.5047 | 20.465 | 20.4219 | 20.3576 | 20.3054 | 20.2492 | 20.1915 | 20.1314 | 20.0654 | 9.4908 | 0 | 0
Chesterfield 132kV | SHERWOOD PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.6532 | 20.6269 | 20.5999 | 20.5725 | 20.5453 | 20.5183 | 20.4916 | 20.4628 | 20.429 | 20.3948 | 20.3599 | 20.3246 | 20.2895 | 20.2529 | 20.0622 | 19.8377 | 19.6137
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.394 | 15.3638 | 15.3381 | 9.0031 | 8.9157 | 8.8161 | 8.7095 | 8.5647 | 8.3786 | 8.159 | 7.8868 | 7.5867 | 7.249 | 7.0075 | 6.2961 | 5.2461 | 3.8948
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.394 | 15.3446 | 15.2863 | 8.8622 | 8.6957 | 8.4685 | 8.2057 | 7.882 | 7.4758 | 7.0111 | 6.5038 | 5.97 | 5.3804 | 4.9195 | 3.1047 | 0.7545 | 4.7472
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.394 | 15.3727 | 15.3538 | 9.075 | 9.0482 | 9.0143 | 8.9709 | 8.9004 | 8.7826 | 8.6055 | 8.379 | 8.143 | 7.8428 | 7.6472 | 7.3816 | 7.0603 | 6.533
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.394 | 15.3419 | 15.2789 | 15.1359 | 15.0043 | 14.8946 | 14.1182 | 14.0039 | 13.7557 | 13.454 | 13.0486 | 12.5846 | 12.021 | 11.5072 | 9.3538 | 6.9297 | 5.0196
Chesterfield 132kV | SHIREBROOK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.394 | 15.3613 | 15.3292 | 9.0094 | 8.9325 | 8.8341 | 8.7148 | 8.5336 | 8.262 | 7.9249 | 7.5474 | 7.1867 | 6.7641 | 6.5092 | 5.7604 | 4.6046 | 9.2953
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SKEGBY LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.3887 | 9.3029 | 8.7654 | 8.5468 | 8.3305 | 8.1236 | 7.9516 | 7.7439 | 7.547 | 7.3156 | 7.1609 | 6.9866 | 6.846 | 6.7124 | 5.3868 | 0.63123 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.3887 | 9.3006 | 8.758 | 8.5149 | 8.2769 | 8.0442 | 7.837 | 7.603 | 7.3818 | 7.0928 | 6.942 | 6.736 | 6.5382 | 6.3388 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.3887 | 9.3387 | 9.2883 | 8.8068 | 8.7473 | 8.6878 | 8.6446 | 8.5844 | 8.5145 | 8.4759 | 8.4332 | 8.4022 | 8.3806 | 8.3679 | 8.4399 | 8.3288 | 7.8779
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.3887 | 9.2971 | 8.7463 | 8.4899 | 8.2457 | 8.003 | 7.7907 | 7.5593 | 7.3289 | 6.9553 | 6.7655 | 6.5849 | 6.4007 | 6.203 | 0 | 0 | 0
Chesterfield 132kV | SOMERCOTES 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.3887 | 9.3246 | 8.8219 | 8.7172 | 8.5973 | 8.4654 | 8.3593 | 8.2306 | 8.1019 | 7.9642 | 7.8968 | 7.8365 | 7.7683 | 7.7174 | 7.0908 | 0.18067 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.9666 | 5.8709 | 5.8159 | 5.5811 | 5.3509 | 5.0883 | 4.8263 | 4.4949 | 4.1448 | 3.7843 | 3.5318 | 2.9821 | 2.4113 | 2.0157 | 0.44723 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.9666 | 5.8009 | 5.6461 | 5.2367 | 4.8279 | 4.406 | 3.9659 | 3.4402 | 2.8793 | 2.2823 | 1.9244 | 1.1631 | 0.3811 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.9666 | 5.9364 | 5.8544 | 5.8096 | 5.7614 | 5.7002 | 5.6238 | 5.5127 | 5.3299 | 5.0735 | 4.8825 | 4.5856 | 4.2011 | 3.9802 | 3.9211 | 3.72 | 6.6044
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.9666 | 5.7965 | 5.6271 | 5.1865 | 4.7575 | 4.3249 | 3.8961 | 3.4667 | 2.9919 | 2.5265 | 2.1169 | 1.4119 | 0.58871 | 0 | 0 | 0 | 0
Chesterfield 132kV | STAVELEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.9666 | 5.8515 | 5.7709 | 5.6257 | 5.4474 | 5.2253 | 4.9811 | 4.663 | 4.2565 | 3.775 | 3.5486 | 3.0289 | 2.4359 | 2.1293 | 1.0723 | 0 | 0.23634
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 68.1543 | 67.8104 | 66.7299 | 65.9464 | 65.1072 | 64.2993 | 63.3665 | 62.4027 | 61.267 | 60.1691 | 59.0457 | 57.517 | 55.9397 | 54.6744 | 48.7306 | 40.4873 | 33.4607
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 68.1543 | 67.7175 | 66.5061 | 65.4016 | 64.3067 | 63.228 | 62.0277 | 60.7579 | 59.2728 | 57.7863 | 56.4561 | 54.577 | 52.6663 | 51.1488 | 43.5672 | 33.5544 | 28.639
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 68.1543 | 68.0617 | 67.8098 | 66.8839 | 66.7326 | 66.6238 | 66.4112 | 66.1848 | 65.7581 | 65.1906 | 64.6138 | 63.9237 | 63.0529 | 62.5232 | 62.1764 | 61.5844 | 63.0722
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 68.1543 | 67.703 | 66.4476 | 65.2718 | 64.1299 | 63.0631 | 61.8525 | 60.7806 | 59.4567 | 58.2183 | 56.8534 | 55.0775 | 53.0499 | 51.344 | 41.9323 | 33.9938 | 25.1908
Chesterfield 132kV | STAVELEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 68.1543 | 67.8429 | 66.8214 | 66.4074 | 65.9181 | 65.3793 | 64.7159 | 64.0064 | 62.9892 | 61.8635 | 60.9192 | 59.7189 | 58.3659 | 57.5917 | 54.5931 | 49.4149 | 49.7285
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | SUTTON JUNCTION 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.8498 | 14.7849 | 14.0633 | 12.6537 | 11.0853 | 9.5772 | 8.1972 | 6.7208 | 5.373 | 4.2047 | 2.9215 | 1.3775 | 0.21821 | 0 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.8498 | 14.742 | 13.8432 | 12.165 | 10.4778 | 8.6555 | 6.9124 | 5.0857 | 3.3362 | 1.658 | 0 | 0 | 0 | 0 | 1.9155 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.8498 | 14.7775 | 14.5774 | 14.4426 | 14.0946 | 13.8441 | 13.6404 | 13.4417 | 13.1919 | 12.8895 | 12.5537 | 12.2783 | 11.9758 | 11.8954 | 12.5984 | 12.3675 | 12.6508
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.8498 | 14.737 | 13.7256 | 11.9656 | 10.2244 | 8.3543 | 6.5642 | 4.8482 | 3.0969 | 1.4139 | 0 | 0 | 0 | 5.1809 | 0 | 0 | 0
Chesterfield 132kV | TEVERSAL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.8498 | 14.7634 | 14.3546 | 13.7826 | 13.077 | 12.1784 | 11.3478 | 10.5278 | 9.6831 | 8.7852 | 7.9104 | 7.1645 | 6.298 | 5.7911 | 12.0727 | 10.8845 | 1.867
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.2914 | 2.5051 | 2.7488 | 2.7636 | 2.6103 | 2.4328 | 2.2159 | 1.8866 | 1.4127 | 0.7175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.2914 | 2.4832 | 2.7313 | 2.6993 | 2.5194 | 2.1914 | 1.754 | 1.0826 | 0.13029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.2914 | 2.4624 | 2.6711 | 2.7815 | 2.7689 | 2.7386 | 2.6705 | 2.5068 | 2.1711 | 1.5921 | 0.81275 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.2914 | 2.4991 | 2.7319 | 2.7196 | 2.5383 | 2.2846 | 1.9935 | 1.6684 | 1.108 | 0.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | THORESBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.2914 | 2.5049 | 2.7861 | 2.8599 | 2.7751 | 2.6294 | 2.3921 | 1.9242 | 1.133 | 0.059945 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.964 | 12.9477 | 12.9334 | 12.8924 | 12.8628 | 12.8429 | 12.7987 | 11.132 | 11.119 | 11.1046 | 11.0851 | 11.055 | 11.0307 | 11.0027 | 10.6648 | 9.8757 | 8.5637
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.964 | 12.9372 | 12.9102 | 12.8548 | 12.8281 | 11.1416 | 11.1156 | 11.0661 | 11.0045 | 10.9412 | 10.8733 | 10.7857 | 10.7135 | 10.6333 | 9.914 | 8.7792 | 7.2903
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.964 | 12.9542 | 12.9474 | 12.9411 | 12.9322 | 12.9244 | 12.917 | 12.9113 | 12.9061 | 12.9036 | 12.9028 | 12.9045 | 12.9087 | 12.9148 | 12.978 | 13.0344 | 12.8976
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.964 | 12.9347 | 12.9038 | 12.8477 | 12.8071 | 11.1382 | 11.1029 | 11.0459 | 10.9746 | 10.9023 | 10.8216 | 10.7368 | 10.6454 | 10.5419 | 9.632 | 8.3175 | 6.4983
Chesterfield 132kV | WALTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.964 | 12.9471 | 12.9312 | 12.9068 | 12.8826 | 12.8624 | 12.85 | 12.8213 | 12.7672 | 11.1223 | 11.1148 | 11.1064 | 11.0984 | 11.092 | 11.0212 | 10.7099 | 10.0892
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.3132 | 18.289 | 18.5508 | 18.4365 | 17.7245 | 16.8801 | 15.7701 | 14.3172 | 12.4708 | 10.1687 | 7.166 | 3.8664 | 0.094248 | 0 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.3132 | 18.2893 | 18.5505 | 18.2435 | 17.4332 | 15.8631 | 13.8799 | 11.2459 | 7.5699 | 3.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.3132 | 18.3012 | 18.4937 | 18.4883 | 18.4815 | 18.4735 | 18.465 | 18.4572 | 17.8478 | 16.3695 | 14.4255 | 12.3 | 9.3994 | 7.4234 | 4.5629 | 0.8254 | 1.1955
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.3132 | 18.2878 | 18.527 | 18.2296 | 17.4118 | 16.1564 | 14.5979 | 12.9042 | 10.413 | 7.671 | 3.7193 | 0 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WARSOP 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.3132 | 18.2976 | 18.5816 | 18.5433 | 18.4979 | 18.4489 | 17.7184 | 16.27 | 13.888 | 10.7442 | 6.9506 | 3.2533 | 0 | 0 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.2708 | 17.9304 | 17.8463 | 17.7187 | 17.6771 | 17.5823 | 17.4825 | 17.3508 | 17.1475 | 16.8593 | 16.4323 | 15.962 | 15.416 | 14.5108 | 10.1755 | 0.62663 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.2708 | 18.0998 | 18.0286 | 17.9117 | 17.797 | 17.5973 | 17.3702 | 17.1148 | 16.7017 | 16.139 | 14.4515 | 12.3159 | 9.8124 | 6.4923 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.2708 | 18.8028 | 18.7194 | 18.6416 | 18.5613 | 18.4594 | 18.3475 | 18.1894 | 17.9493 | 17.5816 | 17.1175 | 16.626 | 16.0927 | 15.7624 | 15.0123 | 13.0673 | 10.7975
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.2708 | 17.9263 | 17.8359 | 17.6994 | 17.653 | 17.5428 | 17.4399 | 17.3582 | 17.1905 | 17.0156 | 16.4832 | 15.2516 | 12.786 | 10.4162 | 0 | 0 | 0
Chesterfield 132kV | WESSINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.2708 | 18.1127 | 18.0601 | 17.9988 | 17.9329 | 17.807 | 17.6513 | 17.4607 | 17.0961 | 16.5959 | 15.9744 | 15.1009 | 13.0507 | 11.7213 | 8.4285 | 0.17935 | 0
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.3179 | 20.2514 | 20.1688 | 19.9812 | 19.8201 | 19.6381 | 19.436 | 19.2909 | 19.1069 | 18.975 | 18.8545 | 18.7641 | 17.2465 | 17.212 | 16.3248 | 14.8137 | 7.5492
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.3179 | 20.2517 | 20.1676 | 19.9807 | 19.8205 | 19.6434 | 19.4499 | 19.3201 | 19.1511 | 19.0238 | 18.9105 | 18.8007 | 18.7439 | 17.2474 | 16.4055 | 14.8279 | 10.6053
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.3179 | 20.2862 | 20.255 | 20.224 | 20.2009 | 20.1658 | 20.1207 | 20.1188 | 20.0849 | 20.0563 | 20.0282 | 20.0053 | 19.9803 | 19.9591 | 19.9115 | 19.8686 | 19.5503
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.3179 | 20.2482 | 20.157 | 19.9608 | 19.7977 | 19.6136 | 19.4023 | 19.2674 | 19.089 | 18.9539 | 18.8367 | 18.7599 | 17.2451 | 17.1891 | 16.0491 | 14.3155 | 6.9167
Chesterfield 132kV | WESTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.3179 | 20.2708 | 20.2189 | 20.1427 | 20.0752 | 19.9794 | 19.8662 | 19.8245 | 19.7202 | 19.6354 | 19.5512 | 19.4766 | 19.4028 | 19.337 | 18.9395 | 17.311 | 16.7045
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 47.5527 | 47.1922 | 46.9756 | 43.9706 | 43.7682 | 43.4117 | 43.2995 | 43.1135 | 42.9472 | 42.8175 | 42.5305 | 41.9401 | 41.135 | 40.5281 | 36.6031 | 30.311 | 22.8725
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 47.5527 | 47.1199 | 46.7794 | 43.4463 | 42.9704 | 42.2473 | 41.7055 | 41.0589 | 40.2373 | 39.0867 | 37.9537 | 36.6301 | 35.0264 | 33.7077 | 25.2342 | 14.8263 | 12.7843
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 47.5527 | 47.3792 | 47.1507 | 44.466 | 44.567 | 44.6443 | 44.8545 | 44.962 | 45.0231 | 45.0515 | 45.0661 | 45.1359 | 45.1664 | 45.4077 | 47.0555 | 46.6419 | 45.7352
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 47.5527 | 47.103 | 46.7262 | 46.1687 | 45.6735 | 45.0749 | 44.6322 | 44.1401 | 43.4598 | 41.632 | 40.8218 | 40.0062 | 39.0498 | 33.9966 | 26.6532 | 19.4504 | 7.8034
Chesterfield 132kV | WHITWELL 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 47.5527 | 47.212 | 47.0173 | 44.163 | 44.1062 | 43.8752 | 43.847 | 43.7378 | 43.5295 | 43.2663 | 43.069 | 42.8096 | 41.9917 | 39.1499 | 36.1738 | 31.3085 | 35.5495
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.396 | 13.2374 | 13.1656 | 13.0433 | 12.9038 | 12.7716 | 12.6149 | 11.4485 | 11.3724 | 11.2232 | 11.0645 | 10.829 | 10.623 | 10.4082 | 8.9799 | 7.1676 | 4.769
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.396 | 13.2279 | 13.1417 | 12.9951 | 12.8361 | 12.7013 | 12.5771 | 11.4341 | 11.3278 | 11.1619 | 11.0051 | 10.752 | 10.5164 | 10.2592 | 8.493 | 6.4183 | 4.0156
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.396 | 13.273 | 13.2492 | 13.2843 | 13.2778 | 13.3023 | 13.2994 | 13.2957 | 13.2885 | 13.2753 | 13.2719 | 13.2584 | 13.25 | 13.2445 | 13.2798 | 13.3113 | 12.9638
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.396 | 13.2233 | 13.1271 | 12.979 | 12.8198 | 12.698 | 12.5668 | 11.4115 | 11.2466 | 11.0053 | 10.7663 | 10.4937 | 10.2139 | 9.9178 | 7.9752 | 5.6962 | 2.8181
Chesterfield 132kV | WINGERWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.396 | 13.2546 | 13.2055 | 13.1896 | 13.1307 | 13.0714 | 12.9721 | 12.8724 | 12.7847 | 12.7075 | 12.6582 | 12.5988 | 12.5558 | 12.5285 | 11.2355 | 10.3804 | 9.2105
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.4086 | 18.3681 | 18.3163 | 16.9826 | 16.8723 | 16.6207 | 16.2626 | 15.7162 | 14.763 | 13.5511 | 12.1922 | 10.7993 | 9.153 | 7.7547 | 3.2182 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.4086 | 18.3641 | 18.3052 | 16.9695 | 16.8557 | 16.5938 | 16.2423 | 15.7071 | 14.7694 | 13.5614 | 12.1988 | 10.8016 | 9.1348 | 7.7136 | 3.0612 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.4086 | 18.3857 | 18.3608 | 18.329 | 18.3087 | 18.2722 | 18.2152 | 18.135 | 17.36 | 17.0756 | 16.5346 | 15.8989 | 15.063 | 14.469 | 13.4897 | 11.9695 | 10.3475
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.4086 | 18.3647 | 18.3056 | 16.965 | 16.8465 | 16.6273 | 16.3642 | 16.0404 | 15.4301 | 14.7368 | 13.7338 | 12.4683 | 10.8518 | 9.2238 | 3.965 | 0 | 0
Coventry 132kV | ANSTY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.4086 | 18.381 | 18.3459 | 18.2927 | 18.2336 | 18.1542 | 17.3821 | 17.2138 | 16.5824 | 15.5935 | 14.4082 | 13.2255 | 11.7736 | 10.7719 | 8.3136 | 4.7765 | 0.35555
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.3364 | 15.3246 | 15.3159 | 15.2835 | 15.2507 | 15.157 | 15.038 | 14.8899 | 14.0629 | 13.6266 | 13.016 | 12.3622 | 11.5893 | 10.9355 | 8.7986 | 5.6267 | 3.2045
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.3364 | 15.3014 | 15.2601 | 15.1623 | 15.0714 | 14.9445 | 14.86 | 14.058 | 13.666 | 13.0822 | 12.3829 | 11.6515 | 10.7975 | 10.0623 | 7.4831 | 3.8742 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.3364 | 15.3214 | 15.3094 | 15.2968 | 15.2803 | 15.2538 | 15.2132 | 15.1348 | 15.0032 | 14.858 | 14.0611 | 13.7593 | 13.2995 | 12.9798 | 12.5182 | 11.7782 | 10.87
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.3364 | 15.2995 | 15.2558 | 15.1554 | 15.0656 | 14.952 | 14.8733 | 14.1392 | 13.9814 | 13.69 | 13.1871 | 12.5329 | 11.6832 | 10.8177 | 7.7864 | 4.2909 | 0
Coventry 132kV | ARLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.3364 | 15.3128 | 15.2893 | 15.2527 | 15.2093 | 15.1388 | 15.0443 | 14.9039 | 14.0853 | 13.6446 | 13.0198 | 12.3864 | 11.6107 | 11.1138 | 9.8678 | 7.9182 | 5.4456
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.1332 | 14.09 | 14.0374 | 13.8939 | 13.7448 | 13.5397 | 13.3212 | 13.062 | 12.8159 | 11.2269 | 10.9502 | 10.4616 | 9.878 | 9.3741 | 7.2262 | 3.919 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.1332 | 14.0466 | 13.9336 | 13.6618 | 13.4045 | 13.1308 | 12.8923 | 11.2335 | 11.0536 | 10.5967 | 9.9905 | 9.3 | 8.5468 | 7.8937 | 4.9267 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.1332 | 14.1018 | 14.0717 | 14.0423 | 14.0027 | 13.9543 | 13.8895 | 13.7945 | 13.6382 | 13.4127 | 13.1478 | 12.9125 | 12.7391 | 11.261 | 11.1877 | 10.9145 | 10.0862
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.1332 | 14.0413 | 13.916 | 13.6339 | 13.3756 | 13.1137 | 12.8986 | 12.7749 | 11.1774 | 10.9345 | 10.4808 | 9.882 | 9.1148 | 8.3348 | 3.4557 | 0 | 0
Coventry 132kV | BARWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.1332 | 14.0801 | 14.0167 | 13.9166 | 13.7976 | 13.6499 | 13.4769 | 13.2484 | 12.9546 | 12.7558 | 11.1105 | 10.7369 | 10.1924 | 9.8584 | 8.7672 | 6.7594 | 4.1201
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.3344 | 19.2145 | 19.2156 | 18.9715 | 18.7385 | 18.5542 | 16.8342 | 16.6777 | 16.3039 | 15.8478 | 15.3402 | 14.7228 | 13.893 | 13.1985 | 1.7731 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.3344 | 19.2138 | 19.2131 | 18.9689 | 18.736 | 18.5531 | 16.8337 | 16.6771 | 16.3034 | 15.841 | 15.3456 | 14.7391 | 13.9127 | 13.2161 | 1.5844 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.3344 | 19.2229 | 19.2586 | 19.219 | 19.1711 | 19.1716 | 19.1544 | 19.0868 | 18.9943 | 18.8876 | 18.7641 | 18.6506 | 18.4954 | 18.4285 | 16.974 | 16.7904 | 16.4135
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.3344 | 19.2182 | 19.2035 | 18.9489 | 18.7129 | 18.5556 | 16.8386 | 16.7349 | 16.4665 | 16.1499 | 15.7164 | 15.1945 | 14.4479 | 13.7114 | 4.442 | 0 | 0
Coventry 132kV | BRAUNSTON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.3344 | 19.2436 | 19.2954 | 19.1996 | 19.067 | 18.9567 | 18.8312 | 18.6361 | 18.4864 | 16.8512 | 16.7431 | 16.5694 | 16.1866 | 15.853 | 14.5713 | 12.7547 | 0
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 36.1774 | 35.7339 | 35.5892 | 35.2427 | 34.9123 | 34.5977 | 34.2778 | 33.9673 | 33.6961 | 33.4883 | 33.2756 | 33.0098 | 32.8311 | 32.6662 | 28.9056 | 26.2458 | 22.3242
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 36.1774 | 35.734 | 35.587 | 35.2438 | 34.9178 | 34.6148 | 34.313 | 34.0216 | 33.7677 | 33.5701 | 33.3897 | 33.155 | 32.995 | 32.8343 | 29.1299 | 26.8 | 23.3277
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 36.1774 | 36.1152 | 35.7345 | 35.6744 | 35.6023 | 35.5305 | 35.4637 | 35.3993 | 35.3265 | 35.2658 | 35.2178 | 35.1859 | 35.1725 | 35.1783 | 35.4015 | 35.5747 | 35.0374
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 36.1774 | 35.7245 | 35.5576 | 35.1985 | 34.8648 | 34.5447 | 34.2137 | 33.9311 | 33.6723 | 33.4436 | 33.2322 | 33.0392 | 32.8596 | 32.6857 | 28.6334 | 25.6879 | 21.3881
Coventry 132kV | COPSEWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 36.1774 | 35.7682 | 35.671 | 35.5306 | 35.372 | 35.2027 | 35.0331 | 34.8785 | 34.7272 | 34.6054 | 34.5017 | 34.4248 | 34.3746 | 34.3526 | 33.9337 | 32.7691 | 29.2728
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.1374 | 22.0792 | 22.255 | 22.2807 | 22.4295 | 22.9475 | 23.0278 | 23.0652 | 23.1076 | 23.1852 | 23.0787 | 22.9123 | 22.7977 | 22.6743 | 21.6088 | 19.7497 | 16.7361
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.1374 | 22.0545 | 22.21 | 22.138 | 22.2089 | 22.435 | 22.4426 | 22.4378 | 22.4734 | 22.5546 | 22.446 | 22.267 | 22.1432 | 21.9967 | 20.5797 | 18.4383 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.1374 | 22.0844 | 22.2214 | 22.3454 | 22.5268 | 22.9542 | 23.1108 | 23.2277 | 23.3499 | 23.5042 | 23.5886 | 23.6826 | 23.7845 | 23.8786 | 23.9322 | 23.8734 | 23.3826
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.1374 | 22.0493 | 22.1768 | 22.1293 | 22.2052 | 22.6552 | 22.6642 | 22.6514 | 22.6174 | 22.6126 | 22.4352 | 22.2385 | 22.0418 | 21.8279 | 20.1017 | 8.461 | 0
Coventry 132kV | COTON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.1374 | 22.0727 | 22.2648 | 22.339 | 22.5372 | 22.8739 | 22.9805 | 23.0792 | 23.1948 | 23.3355 | 23.2956 | 23.2733 | 23.2677 | 23.2702 | 22.7945 | 21.6389 | 20.2215
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.734 | 21.0192 | 21.2938 | 21.1784 | 21.0107 | 20.8027 | 20.5584 | 20.2571 | 19.9275 | 19.6585 | 19.5025 | 19.3305 | 19.2089 | 19.1048 | 18.7708 | 16.6892 | 15.5794
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.734 | 20.9791 | 21.2404 | 21.0645 | 20.8548 | 20.6139 | 20.3493 | 20.0278 | 19.6936 | 19.4111 | 19.2278 | 19.0394 | 18.8998 | 18.8187 | 16.6123 | 15.3256 | 13.9805
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.734 | 20.9521 | 21.1737 | 21.1636 | 21.1485 | 21.1325 | 21.1121 | 21.0858 | 21.0526 | 21.0146 | 20.9663 | 20.9207 | 20.8692 | 20.8168 | 20.7283 | 20.6818 | 20.344
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.734 | 21.0037 | 21.2507 | 21.0698 | 20.8456 | 20.5883 | 20.2865 | 19.9305 | 19.5355 | 19.2243 | 19.045 | 18.9075 | 18.8308 | 17.1895 | 16.5247 | 15.3563 | 0.20925
Coventry 132kV | COVENTRY ARENA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.734 | 21.0041 | 21.3019 | 21.2421 | 21.1399 | 21.0113 | 20.8688 | 20.6889 | 20.4925 | 20.324 | 20.1933 | 20.0759 | 19.964 | 19.8704 | 19.3954 | 18.8664 | 17.2883
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 35.8873 | 35.8186 | 35.2889 | 35.06 | 34.833 | 34.6049 | 34.4102 | 34.2244 | 34.035 | 33.8776 | 33.711 | 33.5192 | 33.3881 | 33.2716 | 30.3734 | 28.2542 | 25.4041
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 35.8873 | 35.7916 | 35.227 | 34.9408 | 34.658 | 34.3875 | 34.1573 | 33.9469 | 33.7392 | 33.5723 | 33.4274 | 33.2749 | 33.1936 | 30.7114 | 29.7584 | 27.1883 | 14.0398
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 35.8873 | 35.837 | 35.7847 | 35.2936 | 35.2353 | 35.1756 | 35.1376 | 35.0946 | 35.0227 | 34.9582 | 34.901 | 34.8541 | 34.8169 | 34.7905 | 34.7819 | 34.6982 | 34.2215
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 35.8873 | 35.7879 | 35.2106 | 34.9154 | 34.6286 | 34.3465 | 34.112 | 33.9068 | 33.6942 | 33.5096 | 33.3502 | 33.2368 | 33.1767 | 30.6677 | 29.2062 | 26.3878 | 0.20963
Coventry 132kV | COVENTRY NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 35.8873 | 35.8208 | 35.3038 | 35.1858 | 35.045 | 34.8924 | 34.7725 | 34.659 | 34.5145 | 34.3783 | 34.2526 | 34.1435 | 34.0498 | 33.9749 | 33.4597 | 30.7406 | 29.7142
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 97.6553 | 97.9023 | 96.078 | 92.2763 | 89.002 | 84.0652 | 76.7259 | 67.5937 | 55.8644 | 25.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 97.6553 | 97.5722 | 95.4195 | 90.7322 | 86.7743 | 78.9065 | 70.6049 | 60.7097 | 29.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 97.6553 | 97.9214 | 98.2709 | 98.4375 | 98.1076 | 97.5942 | 97.2017 | 96.0728 | 94.7955 | 92.8823 | 89.9568 | 85.6567 | 80.2575 | 76.3617 | 70.8946 | 79.333 | 55.8661
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 97.6553 | 97.6193 | 95.2771 | 90.7473 | 86.6881 | 78.7441 | 70.5832 | 60.7362 | 31.4681 | 2.4342 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY NORTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 97.6553 | 97.9738 | 97.0803 | 97.7031 | 95.9948 | 93.6757 | 91.3614 | 88.3391 | 81.8284 | 72.7837 | 59.8219 | 32.8487 | 8.313 | 0 | 0 | 0 | 0
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 55.7666 | 55.6588 | 55.5694 | 55.3712 | 55.1874 | 55.0151 | 54.8577 | 54.6646 | 54.5144 | 54.3927 | 54.291 | 54.1636 | 54.077 | 53.9988 | 53.584 | 46.4898 | 45.1868
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 55.7666 | 55.6592 | 55.57 | 55.3753 | 55.1945 | 55.0274 | 54.8753 | 54.6994 | 54.5625 | 54.4487 | 54.36 | 54.2464 | 54.1674 | 54.0907 | 53.6241 | 46.5557 | 45.539
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 55.7666 | 55.6899 | 55.6468 | 55.6054 | 55.5625 | 55.5213 | 55.481 | 55.4451 | 55.4089 | 55.3772 | 55.3526 | 55.3372 | 55.3328 | 55.3386 | 55.5143 | 55.6447 | 55.3927
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 55.7666 | 55.6527 | 55.5492 | 55.3472 | 55.1641 | 54.9831 | 54.8184 | 54.6432 | 54.4936 | 54.36 | 54.2591 | 54.1696 | 54.088 | 54.004 | 53.5338 | 46.3808 | 44.8085
Coventry 132kV | COVENTRY SOUTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 55.7666 | 55.6771 | 55.6137 | 55.5287 | 55.4343 | 55.3323 | 55.2373 | 55.1367 | 55.0479 | 54.9698 | 54.9109 | 54.8664 | 54.8397 | 54.8272 | 54.6513 | 54.1682 | 53.7135
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.4401 | 11.1897 | 11.0104 | 10.6689 | 10.3159 | 9.6245 | 8.7245 | 7.4934 | 5.5171 | 2.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.4401 | 11.1984 | 11.0277 | 10.6926 | 10.351 | 9.6683 | 8.794 | 7.588 | 5.6548 | 2.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.4401 | 11.3545 | 11.1822 | 11.0999 | 11.0378 | 10.9495 | 10.8184 | 10.5685 | 10.1197 | 9.3753 | 8.3865 | 7.3228 | 5.9702 | 4.9393 | 2.9034 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.4401 | 11.1991 | 11.022 | 10.6742 | 10.3246 | 9.7413 | 9.0591 | 8.2946 | 7.0483 | 5.6271 | 2.9612 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | CRICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.4401 | 11.2415 | 11.1332 | 10.9886 | 10.8169 | 10.5463 | 10.1585 | 9.4594 | 8.1009 | 6.3383 | 4.2493 | 1.1642 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.7571 | 21.6084 | 21.4945 | 21.2838 | 21.1108 | 20.9187 | 20.8634 | 19.0888 | 18.7934 | 18.2329 | 17.4888 | 16.585 | 15.5764 | 14.6846 | 1.7737 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.7571 | 21.6075 | 21.4904 | 21.2781 | 21.1026 | 20.9124 | 20.8596 | 19.0835 | 18.7618 | 18.1739 | 17.4333 | 16.5309 | 15.5149 | 14.6091 | 1.585 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.7571 | 21.6553 | 21.6137 | 21.614 | 21.626 | 21.6348 | 21.7886 | 21.8834 | 21.8645 | 21.7946 | 21.6875 | 21.5829 | 21.438 | 21.3708 | 21.3409 | 21.6266 | 20.8412
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.7571 | 21.6006 | 21.4681 | 21.2494 | 21.0711 | 20.9092 | 20.866 | 19.0977 | 18.9312 | 18.5284 | 17.8534 | 16.9628 | 15.9234 | 14.912 | 4.4435 | 0 | 0
Coventry 132kV | DAVENTRY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.7571 | 21.6417 | 21.5721 | 21.5183 | 21.4624 | 21.3524 | 21.3974 | 21.3813 | 21.1303 | 20.8984 | 19.1245 | 18.9853 | 18.5871 | 18.2258 | 16.7954 | 14.365 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 64.9693 | 60.6846 | 58.5654 | 52.093 | 45.6608 | 35.5735 | 24.8976 | 9.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 64.9693 | 60.6837 | 58.5237 | 52.0424 | 45.5959 | 35.5062 | 24.8461 | 9.9311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 64.9693 | 61.9113 | 61.3387 | 60.7374 | 60.0765 | 59.4847 | 59.4292 | 57.6885 | 53.9604 | 46.9788 | 37.6786 | 27.8431 | 14.8592 | 5.5938 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 64.9693 | 60.6278 | 58.162 | 51.4148 | 44.7833 | 36.0513 | 27.7217 | 17.8428 | 2.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | DAVENTRY 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 64.9693 | 61.5025 | 60.617 | 58.4654 | 55.8079 | 52.1314 | 48.6334 | 41.5555 | 27.9478 | 9.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.4549 | 21.7458 | 22.031 | 21.9703 | 21.8991 | 21.6767 | 21.4365 | 21.1751 | 20.9046 | 20.6902 | 20.3981 | 20.0236 | 19.6879 | 19.3594 | 16.7748 | 14.3988 | 11.0713
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.4549 | 21.6396 | 21.8193 | 21.5376 | 21.2766 | 20.8854 | 20.4762 | 20.0377 | 19.5982 | 19.1972 | 18.846 | 16.8834 | 16.771 | 16.5177 | 14.282 | 10.7478 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.4549 | 21.6579 | 21.8643 | 21.9423 | 22.0072 | 21.9868 | 21.9412 | 21.8899 | 21.8102 | 21.7179 | 21.6189 | 21.5266 | 21.417 | 21.3314 | 21.3177 | 21.1521 | 20.347
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.4549 | 21.6571 | 21.8112 | 21.5365 | 21.2703 | 20.8671 | 20.4424 | 20.0483 | 19.63 | 19.262 | 18.8954 | 18.677 | 16.8106 | 16.519 | 13.6219 | 8.461 | 0
Coventry 132kV | GIPSY LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.4549 | 21.6937 | 21.9515 | 21.9317 | 21.8926 | 21.6975 | 21.4755 | 21.2302 | 20.9471 | 20.6516 | 20.3428 | 20.0673 | 19.7828 | 19.5871 | 18.7689 | 16.2829 | 14.0371
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 21.5923 | 21.4208 | 21.3261 | 21.1386 | 20.9524 | 20.7819 | 20.6225 | 20.4537 | 20.3027 | 20.1746 | 20.0426 | 19.8905 | 19.9315 | 19.7965 | 19.0139 | 16.8317 | 15.3502
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 21.5923 | 21.4234 | 21.3309 | 21.1469 | 20.9627 | 20.7957 | 20.6373 | 20.4729 | 20.3281 | 20.2004 | 20.0797 | 19.9411 | 19.9896 | 19.8619 | 19.078 | 16.9196 | 15.6359
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 21.5923 | 21.4413 | 21.3908 | 21.337 | 21.2849 | 21.2341 | 21.1837 | 21.133 | 21.0778 | 21.0266 | 20.9808 | 20.9418 | 20.91 | 20.8849 | 20.8843 | 20.955 | 20.7018
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 21.5923 | 21.4182 | 21.3149 | 21.1214 | 20.9328 | 20.7591 | 20.5929 | 20.4343 | 20.2814 | 20.1481 | 20.0229 | 19.9121 | 19.9532 | 19.8218 | 18.8875 | 16.7046 | 15.071
Coventry 132kV | GULSON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 21.5923 | 21.4359 | 21.3681 | 21.2762 | 21.1761 | 21.0749 | 20.9749 | 20.877 | 20.7872 | 20.7067 | 20.6402 | 20.5874 | 20.6925 | 20.6581 | 20.3859 | 19.7107 | 18.9355
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.1756 | 18.811 | 18.6026 | 18.1084 | 17.6066 | 16.9865 | 16.2915 | 15.4076 | 14.434 | 13.4511 | 12.3357 | 11.0607 | 9.6944 | 8.6483 | 4.2267 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.1756 | 18.8165 | 18.6085 | 18.1098 | 17.6118 | 16.9987 | 16.3175 | 15.4598 | 14.4989 | 13.4983 | 12.4083 | 11.1662 | 9.8008 | 8.7437 | 4.2647 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.1756 | 18.9147 | 18.8446 | 18.7634 | 18.6885 | 18.5967 | 18.4801 | 18.2987 | 17.9856 | 17.5572 | 17.0114 | 16.4199 | 15.6585 | 15.2027 | 14.7845 | 14.0385 | 12.572
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.1756 | 18.8041 | 18.5747 | 18.048 | 17.5329 | 16.9555 | 16.341 | 15.69 | 14.9544 | 14.2995 | 13.3945 | 12.2797 | 10.9432 | 9.7161 | 4.3084 | 0 | 0
Coventry 132kV | HILLMORTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.1756 | 18.8806 | 18.7616 | 18.5677 | 18.337 | 18.041 | 17.6842 | 17.1704 | 16.4518 | 15.6463 | 14.7503 | 13.8169 | 12.699 | 12.0859 | 10.2 | 7.2126 | 3.3746
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 45.6601 | 44.2949 | 43.9707 | 41.5624 | 38.8086 | 34.1471 | 28.9351 | 21.3749 | 10.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 45.6601 | 43.8409 | 42.2001 | 36.8143 | 31.4821 | 24.5322 | 15.9042 | 4.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 45.6601 | 45.7056 | 44.1605 | 43.9625 | 43.5976 | 42.7392 | 41.5089 | 39.5888 | 36.3419 | 31.4945 | 24.1582 | 16.0517 | 5.784 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 45.6601 | 43.7809 | 41.867 | 36.2323 | 30.7018 | 23.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | HINCKLEY 132KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 45.6601 | 44.2479 | 43.694 | 42.0875 | 40.0072 | 36.6797 | 32.7133 | 27.1606 | 17.3609 | 4.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.9797 | 21.6299 | 21.5375 | 21.2201 | 20.9903 | 20.7014 | 20.432 | 20.0898 | 19.7468 | 19.4639 | 19.1845 | 18.9572 | 18.8201 | 17.0988 | 16.0676 | 14.3515 | 11.7217
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.9797 | 21.5533 | 21.3452 | 20.816 | 20.4004 | 19.9464 | 19.5232 | 19.0951 | 18.8366 | 16.5053 | 16.331 | 16.0393 | 15.6873 | 15.3106 | 13.1907 | 10.4984 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.9797 | 21.9076 | 21.5372 | 21.3805 | 21.3333 | 21.2719 | 21.2233 | 21.1597 | 21.0834 | 21.0004 | 20.915 | 20.84 | 20.7618 | 20.6927 | 20.6425 | 20.5606 | 20.0206
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.9797 | 21.5435 | 21.3184 | 20.7338 | 20.3139 | 19.8498 | 19.4134 | 19.0053 | 17.0348 | 16.4165 | 16.1132 | 15.7823 | 15.4627 | 15.135 | 12.9502 | 8.4396 | 0
Coventry 132kV | LANGDALE DRIVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.9797 | 21.61 | 21.4881 | 21.2446 | 21.0505 | 20.8038 | 20.5731 | 20.2977 | 20.0116 | 19.7583 | 19.5222 | 19.3485 | 19.1703 | 19.0366 | 16.638 | 16.0694 | 14.7167
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.0508 | 8.8492 | 8.1367 | 7.7237 | 7.3354 | 6.8137 | 6.2827 | 5.5871 | 4.7015 | 3.7043 | 2.4337 | 1.0627 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.0508 | 8.8641 | 8.1643 | 7.7632 | 7.392 | 6.8893 | 6.3777 | 5.7124 | 4.8676 | 3.8788 | 2.6617 | 1.3529 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.0508 | 8.9657 | 8.9926 | 8.3761 | 8.4088 | 8.4264 | 8.4391 | 8.3828 | 8.2427 | 7.986 | 7.5852 | 7.1613 | 6.6018 | 6.2331 | 5.7135 | 4.9078 | 4.2196
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.0508 | 8.8507 | 8.1219 | 7.711 | 7.3285 | 6.879 | 6.4163 | 5.9035 | 5.2207 | 4.5192 | 3.4537 | 2.1999 | 0.69341 | 0 | 0 | 0 | 0
Coventry 132kV | LAWFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.0508 | 8.9317 | 8.3263 | 8.2343 | 8.1355 | 7.935 | 7.7291 | 7.3948 | 6.8406 | 6.1157 | 5.1663 | 4.2534 | 3.1376 | 2.3705 | 0 | 0 | 0
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 19.2743 | 19.2041 | 19.1532 | 19.0787 | 19.0107 | 18.9088 | 18.8027 | 18.6777 | 18.5465 | 18.4875 | 18.4242 | 18.3559 | 18.3077 | 18.2658 | 18.0346 | 17.4308 | 17.1075
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 19.2743 | 19.2095 | 19.1621 | 19.09 | 19.0228 | 18.9253 | 18.8282 | 18.7146 | 18.6002 | 18.5302 | 18.4617 | 18.3904 | 18.3276 | 18.2701 | 17.5283 | 17.4126 | 17.1224
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 19.2743 | 19.2178 | 19.1871 | 19.1569 | 19.1357 | 19.1177 | 19.101 | 19.0836 | 19.0692 | 19.0482 | 19.0281 | 19.0083 | 18.9887 | 18.9766 | 18.971 | 18.9695 | 18.8979
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 19.2743 | 19.2053 | 19.1525 | 19.0755 | 19.0063 | 18.9052 | 18.7973 | 18.6724 | 18.5332 | 18.4713 | 18.4052 | 18.343 | 18.2935 | 18.2516 | 17.9951 | 17.4004 | 17.041
Coventry 132kV | LONDON ROAD 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 19.2743 | 19.2177 | 19.1824 | 19.142 | 19.1014 | 19.0445 | 18.9889 | 18.9238 | 18.857 | 18.8128 | 18.7691 | 18.7325 | 18.6992 | 18.6707 | 18.5532 | 18.3811 | 18.155
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1836 | 19.9606 | 20.1094 | 20.0674 | 20.0608 | 19.8151 | 19.5213 | 19.0245 | 18.5596 | 16.6303 | 15.4901 | 14.1459 | 12.5601 | 11.2162 | 5.7437 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1836 | 19.9197 | 20.0058 | 19.8274 | 19.6928 | 19.3363 | 18.9438 | 18.5663 | 16.7252 | 15.6298 | 14.2041 | 12.646 | 10.8465 | 9.2986 | 2.8542 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1836 | 20.1451 | 20.0923 | 20.1933 | 20.3029 | 20.3924 | 20.4597 | 20.3976 | 20.2442 | 19.8754 | 19.3812 | 18.8807 | 17.1257 | 16.9655 | 16.2798 | 15.271 | 13.7777
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1836 | 19.9171 | 19.9838 | 19.8205 | 19.686 | 19.4454 | 19.1312 | 18.7464 | 17.0369 | 16.5628 | 15.4578 | 13.9552 | 12.1034 | 10.3198 | 3.3016 | 0 | 0
Coventry 132kV | LUTTERWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1836 | 19.9557 | 20.1048 | 20.1362 | 20.1892 | 20.1136 | 20.0012 | 19.6684 | 19.1144 | 18.5473 | 16.6213 | 15.682 | 14.4263 | 13.5108 | 10.4104 | 7.0358 | 2.8623
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.2513 | 12.849 | 12.2487 | 12.1992 | 12.15 | 12.0418 | 11.8972 | 11.6791 | 11.3225 | 10.8276 | 10.2462 | 9.6559 | 8.9438 | 8.3414 | 6.4058 | 3.7609 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.2513 | 12.8489 | 12.2485 | 12.199 | 12.1498 | 12.0418 | 11.8974 | 11.679 | 11.3224 | 10.8275 | 10.2464 | 9.6572 | 8.9463 | 8.3457 | 6.4102 | 3.4407 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.2513 | 13.2281 | 12.6344 | 12.0434 | 12.0182 | 11.9843 | 11.9366 | 11.8497 | 11.7029 | 11.4486 | 11.1134 | 10.7538 | 10.2901 | 9.9766 | 9.4267 | 8.6588 | 7.8738
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.2513 | 12.8486 | 12.2475 | 12.1982 | 12.1506 | 12.0655 | 11.9728 | 11.8669 | 11.6634 | 11.4044 | 10.9865 | 10.4518 | 9.7536 | 9.0479 | 6.8142 | 0 | 0
Coventry 132kV | MAGNA PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.2513 | 12.8528 | 12.2586 | 12.2278 | 12.195 | 12.1392 | 12.0508 | 11.872 | 11.538 | 11.0529 | 10.4768 | 9.9048 | 9.2052 | 8.7605 | 7.6861 | 6.1761 | 4.2961
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.2531 | 12.1935 | 12.117 | 11.8569 | 11.5701 | 11.1576 | 10.7024 | 10.1077 | 9.3331 | 8.4729 | 7.4654 | 6.3347 | 5.1402 | 4.076 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.2531 | 12.1265 | 11.9462 | 11.4444 | 10.9259 | 10.2971 | 9.6145 | 8.7863 | 7.7524 | 6.6046 | 5.3406 | 3.9452 | 2.4545 | 1.1025 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.2531 | 12.2176 | 12.1799 | 12.1327 | 12.0648 | 11.9764 | 11.8674 | 11.7106 | 11.4576 | 11.0927 | 10.6293 | 10.1391 | 9.5297 | 9.1003 | 8.4279 | 7.8038 | 6.3505
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.2531 | 12.1161 | 11.913 | 11.3796 | 10.8319 | 10.2004 | 9.5213 | 8.8047 | 7.9127 | 6.9855 | 5.8203 | 4.4822 | 2.0393 | 0.46591 | 0 | 0 | 0
Coventry 132kV | MIDDLEFIELD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.2531 | 12.1778 | 12.0834 | 11.9094 | 11.6843 | 11.3846 | 11.0347 | 10.563 | 9.8675 | 9.0309 | 8.0849 | 7.1527 | 6.072 | 5.3198 | 1.9532 | 0 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.6549 | 15.8092 | 15.9613 | 15.935 | 15.9273 | 15.7841 | 15.7155 | 15.5994 | 15.4615 | 15.3999 | 15.3054 | 15.1745 | 15.1375 | 15.0921 | 13.6662 | 11.5438 | 6.4709
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.6549 | 15.7265 | 15.7836 | 15.5586 | 15.3698 | 15.0725 | 14.0684 | 13.9886 | 13.841 | 13.6923 | 13.5395 | 13.3428 | 13.1648 | 12.9729 | 10.9309 | 5.0982 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.6549 | 15.7684 | 15.8832 | 15.9798 | 16.0807 | 16.1104 | 16.1841 | 16.2409 | 16.2793 | 16.3348 | 16.4077 | 16.4981 | 16.6054 | 16.7206 | 17.1012 | 17.3262 | 16.8075
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.6549 | 15.7333 | 15.7695 | 15.5439 | 15.344 | 15.0599 | 14.0587 | 13.9678 | 13.7762 | 13.5786 | 13.3471 | 13.1499 | 12.9576 | 12.7391 | 10.3768 | 2.2808 | 0
Coventry 132kV | NEWDIGATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.6549 | 15.7742 | 15.9006 | 15.9128 | 15.9323 | 15.8049 | 15.7534 | 15.6973 | 15.6149 | 15.5687 | 15.5541 | 15.5744 | 15.5801 | 15.62 | 15.1982 | 13.6519 | 11.9389
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.681 | 20.501 | 20.7028 | 20.6766 | 20.5418 | 20.3795 | 20.2146 | 20.0247 | 19.9165 | 19.8609 | 19.7757 | 19.7149 | 19.7094 | 19.6973 | 19.275 | 18.9954 | 15.9689
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.681 | 20.4459 | 20.5961 | 20.4536 | 20.218 | 19.9754 | 19.7357 | 19.4897 | 19.3407 | 19.2413 | 19.1667 | 19.1034 | 19.0558 | 19.0297 | 16.4057 | 14.7944 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.681 | 20.7959 | 20.5841 | 20.6287 | 20.5968 | 20.5639 | 20.5283 | 20.4926 | 20.5005 | 20.5299 | 20.5622 | 20.6074 | 20.6662 | 20.7321 | 21.1144 | 21.1565 | 20.7007
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.681 | 20.4554 | 20.5876 | 20.4507 | 20.2078 | 19.9534 | 19.6893 | 19.4382 | 19.2627 | 19.1482 | 19.073 | 19.0504 | 16.9479 | 16.9464 | 16.2568 | 8.4878 | 0
Coventry 132kV | NUNEATON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.681 | 20.4725 | 20.6628 | 20.6559 | 20.5377 | 20.3995 | 20.2556 | 20.1039 | 20.036 | 20.0048 | 19.9937 | 20.0126 | 19.9958 | 19.9978 | 19.7562 | 19.1219 | 18.9612
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 101.2681 | 90.8426 | 90.7967 | 89.0465 | 86.4673 | 85.5296 | 80.9707 | 75.0603 | 65.981 | 15.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 101.2681 | 90.4148 | 89.9588 | 85.0995 | 73.7573 | 56.9196 | 40.1139 | 20.6832 | 0.20907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 101.2681 | 100.8818 | 90.5982 | 89.7694 | 88.9553 | 89.2255 | 88.0043 | 86.2801 | 84.1608 | 81.1609 | 76.7558 | 72.0835 | 66.3135 | 61.8401 | 55.1881 | 45.2179 | 28.1464
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 101.2681 | 90.3603 | 89.6809 | 84.3914 | 71.9507 | 56.208 | 38.8136 | 20.4759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | NUNEATON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 101.2681 | 90.7043 | 90.6459 | 89.1383 | 86.8887 | 85.5373 | 81.4634 | 75.9468 | 69.4073 | 61.7595 | 51.854 | 34.421 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 78.8167 | 74.6878 | 71.6838 | 70.3931 | 69.2921 | 65.7971 | 61.4843 | 54.4996 | 10.6648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 78.8167 | 74.2002 | 70.4765 | 67.599 | 65.0442 | 60.2219 | 54.4798 | 46.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 78.8167 | 78.1812 | 74.0968 | 70.9825 | 71.2817 | 71.3178 | 71.0192 | 69.3834 | 66.2319 | 60.3239 | 52.4587 | 44.0154 | 33.0695 | 25.6114 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 78.8167 | 74.163 | 70.2438 | 67.3906 | 64.8188 | 61.0976 | 56.7823 | 51.5376 | 19.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | PAILTON 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 78.8167 | 74.6377 | 71.6084 | 71.0863 | 70.5866 | 68.9061 | 66.5366 | 61.5052 | 52.7633 | 40.1123 | 1.8457 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 50.2904 | 49.8847 | 49.7975 | 49.5248 | 49.2763 | 48.9791 | 48.6896 | 48.3624 | 48.0808 | 47.8107 | 47.4582 | 47.0371 | 46.6681 | 46.3017 | 44.165 | 10.5834 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 50.2904 | 49.8908 | 49.8064 | 49.5356 | 49.2909 | 49.0034 | 48.7239 | 48.4135 | 48.15 | 47.8738 | 47.5391 | 47.1435 | 46.785 | 46.4264 | 44.2958 | 2.5632 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 50.2904 | 50.0626 | 49.8961 | 49.8594 | 49.8314 | 49.8466 | 49.8593 | 49.8555 | 49.8597 | 49.848 | 49.8225 | 49.8057 | 49.798 | 49.797 | 49.7183 | 49.5496 | 54.125
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 50.2904 | 49.886 | 49.783 | 49.5107 | 49.2623 | 49.0342 | 48.7772 | 48.4912 | 48.1677 | 47.8856 | 47.5425 | 47.1939 | 46.8475 | 46.4835 | 44.1972 | 0 | 0
Coventry 132kV | RUGBY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 50.2904 | 49.9239 | 49.8906 | 49.7919 | 49.6969 | 49.6054 | 49.5337 | 49.4571 | 49.3956 | 49.2968 | 49.1504 | 49.0248 | 48.913 | 48.8204 | 48.1876 | 46.8012 | 50.4287
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 77.4297 | 70.3598 | 63.4326 | 54.9643 | 46.5875 | 36.3102 | 25.3104 | 11.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 77.4297 | 70.5306 | 63.7293 | 55.3666 | 47.1984 | 37.1805 | 26.5255 | 13.4062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 77.4297 | 74.9596 | 71.401 | 54.2598 | 53.4719 | 52.4746 | 51.2458 | 49.1664 | 45.6002 | 40.4413 | 33.5712 | 26.2922 | 17.0688 | 11.0109 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 77.4297 | 70.3339 | 63.1018 | 54.3657 | 45.9366 | 36.3877 | 26.3554 | 15.7344 | 3.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | RUGBY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 77.4297 | 71.6532 | 66.4486 | 63.487 | 60.0635 | 55.4081 | 50.2442 | 43.1195 | 32.9069 | 20.9418 | 1.3967 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Best View | Headroom (MW) | 13.3595 | 13.2064 | 12.979 | 12.9599 | 12.9409 | 12.8997 | 12.8448 | 12.7624 | 12.628 | 12.4421 | 12.2243 | 12.0036 | 11.7379 | 11.5135 | 10.7942 | 9.8153 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.3595 | 13.2063 | 12.979 | 12.9598 | 12.9408 | 12.8997 | 12.8449 | 12.7623 | 12.628 | 12.4421 | 12.2243 | 12.0041 | 11.7388 | 11.5151 | 10.7958 | 2.9702 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.3595 | 13.3501 | 13.1247 | 12.9012 | 12.8913 | 12.878 | 12.8597 | 12.8265 | 12.7709 | 12.675 | 12.5488 | 12.4138 | 12.24 | 12.1226 | 11.9161 | 11.6289 | 11.3363
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.3595 | 13.2062 | 12.9786 | 12.9595 | 12.9411 | 12.9086 | 12.8733 | 12.833 | 12.7561 | 12.6584 | 12.5013 | 12.3008 | 12.0397 | 11.7764 | 10.9455 | 0 | 0
Coventry 132kV | Rugby Gateway | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.3595 | 13.2078 | 12.9828 | 12.9707 | 12.9579 | 12.9364 | 12.9026 | 12.8349 | 12.7089 | 12.5266 | 12.3105 | 12.0964 | 11.8353 | 11.6694 | 11.2688 | 10.7081 | 10.0121
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.5905 | 16.5388 | 16.4849 | 16.3722 | 16.2996 | 16.1862 | 16.0665 | 15.8994 | 15.6391 | 15.3201 | 14.9522 | 14.5641 | 14.1191 | 13.746 | 12.3731 | 11.0173 | 7.813
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.5905 | 16.54 | 16.4852 | 16.3718 | 16.2985 | 16.1877 | 16.0704 | 15.907 | 15.6487 | 15.3301 | 14.9696 | 14.591 | 14.155 | 13.7899 | 12.4331 | 11.1132 | 7.9976
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.5905 | 16.5576 | 16.5313 | 16.5045 | 16.4997 | 16.4876 | 16.4665 | 16.415 | 16.3065 | 16.1292 | 15.8998 | 15.6539 | 15.3372 | 15.1458 | 16.154 | 16.0911 | 13.0713
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.5905 | 16.5366 | 16.4781 | 16.3637 | 16.2902 | 16.1986 | 16.1051 | 16.0075 | 15.8245 | 15.6297 | 15.3494 | 15.0106 | 14.5858 | 14.1569 | 12.8228 | 11.2042 | 8.421
Coventry 132kV | RYTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.5905 | 16.5504 | 16.5123 | 16.4605 | 16.4395 | 16.389 | 16.3246 | 16.205 | 15.9626 | 15.6394 | 15.2636 | 14.8963 | 14.4604 | 14.2279 | 13.5961 | 13.1636 | 10.4388
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.5482 | 24.4498 | 24.3717 | 24.14 | 23.8993 | 23.4696 | 22.9491 | 22.1665 | 21.0148 | 19.5672 | 17.8566 | 16.0615 | 14.0067 | 12.5222 | 7.3011 | 0.3072 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.5482 | 24.3732 | 24.1854 | 23.7103 | 23.2528 | 22.6343 | 21.9195 | 20.9467 | 19.5911 | 17.9185 | 16.0125 | 14.0231 | 11.7496 | 10.051 | 3.5904 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.5482 | 24.4717 | 24.4283 | 24.3901 | 24.3298 | 24.2419 | 24.116 | 23.8827 | 23.451 | 22.7577 | 21.8539 | 20.8973 | 19.6562 | 18.8489 | 17.9527 | 16.5144 | 14.3926
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.5482 | 24.3667 | 24.1556 | 23.658 | 23.1917 | 22.6447 | 22.0924 | 21.5264 | 20.6322 | 19.6659 | 18.2184 | 16.4273 | 14.1422 | 12.0586 | 4.0656 | 0 | 0
Coventry 132kV | SAPCOTE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.5482 | 24.4356 | 24.337 | 24.1737 | 23.9792 | 23.6981 | 23.3291 | 22.7115 | 21.6785 | 20.3089 | 18.7175 | 17.1686 | 15.3073 | 14.1684 | 11.1383 | 6.5793 | 0.74957
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.9977 | 22.4864 | 22.3023 | 21.8978 | 21.5113 | 21.14 | 20.7986 | 20.4536 | 20.163 | 19.9464 | 19.7702 | 19.6649 | 16.3238 | 16.217 | 14.2363 | 10.7468 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.9977 | 22.4895 | 22.3072 | 21.9074 | 21.5268 | 21.1654 | 20.8309 | 20.4973 | 20.2147 | 19.995 | 19.8201 | 19.6862 | 16.3516 | 16.3104 | 14.574 | 2.6028 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.9977 | 22.9235 | 22.492 | 20.681 | 20.6149 | 20.5497 | 20.4836 | 20.423 | 20.354 | 20.2923 | 20.2401 | 20.1964 | 20.1656 | 20.1461 | 20.1759 | 20.2051 | 19.7271
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.9977 | 22.4804 | 22.2766 | 21.858 | 21.4666 | 21.0869 | 20.7324 | 20.4083 | 20.1147 | 19.8949 | 19.7378 | 19.6637 | 16.3181 | 16.2009 | 13.9314 | 0 | 0
Coventry 132kV | UNION STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.9977 | 22.533 | 22.4139 | 22.248 | 22.0593 | 21.8566 | 21.6581 | 21.4654 | 21.2773 | 21.1122 | 20.9654 | 20.8405 | 20.7347 | 20.6529 | 20.0237 | 16.501 | 15.3093
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 33.8314 | 33.7891 | 33.7457 | 33.7539 | 33.6951 | 28.8091 | 28.7756 | 28.6975 | 28.5954 | 28.4952 | 28.3678 | 28.1782 | 28.0315 | 27.8332 | 26.1192 | 23.0698 | 18.9475
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 33.8314 | 33.7891 | 33.7457 | 33.7561 | 33.6956 | 28.8127 | 28.7854 | 28.7197 | 28.6323 | 28.5461 | 28.4513 | 28.3062 | 28.1981 | 28.0415 | 26.4911 | 23.6605 | 14.0453
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 33.8314 | 33.7985 | 33.765 | 33.8707 | 33.8327 | 33.7959 | 33.7595 | 33.7253 | 33.6897 | 33.6595 | 33.6349 | 33.6136 | 33.596 | 33.576 | 33.5235 | 38.6704 | 37.9996
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 33.8314 | 33.7881 | 33.7434 | 33.7631 | 33.6969 | 28.8152 | 28.7886 | 28.7297 | 28.6293 | 28.5134 | 28.3808 | 28.2379 | 28.0766 | 27.8848 | 33.6257 | 19.4826 | 0.20971
Coventry 132kV | WALSGRAVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 33.8314 | 33.7958 | 33.7566 | 33.8388 | 33.7696 | 33.7104 | 33.6658 | 33.6355 | 28.8828 | 28.8949 | 28.9038 | 28.9128 | 28.9246 | 28.9411 | 37.0473 | 28.0753 | 26.4578
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.6882 | 18.5847 | 18.5412 | 18.4623 | 18.422 | 17.4955 | 17.2565 | 16.82 | 16.2502 | 15.2399 | 14.0488 | 12.8064 | 11.3395 | 10.1148 | 1.7729 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.6882 | 18.5844 | 18.5403 | 18.4617 | 18.4219 | 17.4951 | 17.2559 | 16.8212 | 16.2528 | 15.2401 | 14.0542 | 12.8174 | 11.3527 | 10.1275 | 1.5842 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.6882 | 18.6026 | 18.5864 | 18.5697 | 18.5486 | 18.5212 | 18.4855 | 18.4324 | 18.4046 | 17.5009 | 17.1975 | 16.7949 | 16.2496 | 15.8459 | 15.1773 | 13.9748 | 12.6272
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.6882 | 18.5835 | 18.5379 | 18.4589 | 18.4212 | 17.5129 | 17.3667 | 17.1438 | 16.8672 | 16.3201 | 15.4463 | 14.3369 | 12.9065 | 11.4885 | 4.4415 | 0 | 0
Coventry 132kV | WEEDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.6882 | 18.5943 | 18.5669 | 18.5283 | 18.4881 | 18.4404 | 18.4108 | 17.4815 | 17.214 | 16.4961 | 15.6032 | 14.7092 | 13.6203 | 12.796 | 10.5036 | 7.306 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.81737 | 0.6999 | 0.63759 | 0.48273 | 0.33515 | 0.082456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.81737 | 0.69939 | 0.63563 | 0.4804 | 0.33241 | 0.080239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.81737 | 0.73197 | 0.71301 | 0.69338 | 0.66797 | 0.63293 | 0.58705 | 0.50427 | 0.35295 | 0.11316 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.81737 | 0.69657 | 0.62634 | 0.46668 | 0.31677 | 0.10112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WELTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.81737 | 0.71912 | 0.68108 | 0.62154 | 0.55329 | 0.45743 | 0.33 | 0.11084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WEST HADDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 35.3566 | 35.3206 | 35.1891 | 34.9839 | 34.911 | 34.8712 | 35.1534 | 34.9856 | 34.8136 | 34.6986 | 34.5887 | 34.4862 | 34.4265 | 34.386 | 28.8632 | 34.234 | 27.7859
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 35.3566 | 35.3236 | 35.1978 | 34.9952 | 34.9229 | 34.8882 | 35.1821 | 35.0213 | 34.8576 | 34.739 | 34.6329 | 34.5256 | 34.4575 | 34.403 | 29.0751 | 34.4286 | 28.5496
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 35.3566 | 35.335 | 35.2566 | 35.1793 | 35.1986 | 35.3107 | 35.7326 | 35.7236 | 35.699 | 35.6758 | 35.6602 | 35.6551 | 35.6555 | 35.6669 | 35.5967 | 35.486 | 34.8558
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 35.3566 | 35.3232 | 35.1878 | 34.9779 | 34.9004 | 34.9256 | 35.2863 | 35.121 | 34.9326 | 34.7975 | 34.6753 | 34.555 | 34.4584 | 34.3917 | 28.6425 | 34.1629 | 27.0127
Coventry 132kV | WHITLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 35.3566 | 35.342 | 35.2456 | 35.1302 | 35.1354 | 35.1765 | 35.6351 | 35.5441 | 35.4229 | 35.331 | 35.2466 | 35.1829 | 35.1347 | 35.1107 | 34.7105 | 38.0937 | 36.1639
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 86.3557 | 82.5858 | 79.4301 | 72.3459 | 67.048 | 61.8602 | 60.4478 | 53.4546 | 45.9573 | 39.7033 | 32.7995 | 24.5917 | 18.601 | 11.6786 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 86.3557 | 82.6679 | 79.5885 | 72.6141 | 67.3827 | 62.429 | 61.2889 | 54.6942 | 47.6868 | 41.5113 | 35.2337 | 27.7964 | 22.3627 | 16.0831 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 86.3557 | 85.3498 | 82.1352 | 80.6332 | 80.1786 | 80.5724 | 83.485 | 82.4528 | 80.8254 | 78.8553 | 76.7645 | 74.8349 | 72.7129 | 71.6677 | 79.6733 | 80.472 | 52.2794
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 86.3557 | 82.5204 | 79.0459 | 71.7208 | 66.2885 | 62.0291 | 61.2263 | 55.092 | 48.1045 | 42.2672 | 35.9851 | 29.2591 | 22.9862 | 15.2161 | 0 | 0 | 0
Coventry 132kV | WHITLEY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 86.3557 | 83.2817 | 81.2701 | 78.2314 | 76.3988 | 74.5062 | 76.2714 | 72.7531 | 68.2338 | 63.903 | 59.5462 | 55.7808 | 52.9849 | 51.0308 | 38.4839 | 45.4964 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.5488 | 16.5076 | 16.4921 | 16.3987 | 16.2824 | 16.1298 | 15.9711 | 15.7684 | 15.5271 | 15.3545 | 15.0925 | 14.7065 | 16.6751 | 16.4816 | 14.7017 | 11.4105 | 7.584
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.5488 | 16.4741 | 16.3994 | 16.1452 | 15.8193 | 15.4523 | 15.0527 | 14.5773 | 14.043 | 13.504 | 12.9243 | 12.2138 | 14.4193 | 13.7958 | 10.422 | 5.7764 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.5488 | 16.542 | 16.4944 | 16.4764 | 16.454 | 16.427 | 16.393 | 16.3524 | 16.2888 | 16.2062 | 16.1074 | 16.0065 | 15.8871 | 15.7976 | 15.7988 | 15.7909 | 14.9781
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.5488 | 16.4695 | 16.3817 | 16.1022 | 15.7572 | 15.3694 | 14.9548 | 14.5102 | 13.9801 | 13.4842 | 12.9037 | 12.1927 | 14.3181 | 13.5691 | 5.1463 | 0.098015 | 0
Coventry 132kV | WHITTLEFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.5488 | 16.4969 | 16.4619 | 16.3881 | 16.2757 | 16.1307 | 15.9627 | 15.7574 | 15.4839 | 15.1856 | 14.8625 | 14.5398 | 16.6119 | 16.4764 | 15.6027 | 10.576 | 7.6128
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.4586 | 12.5254 | 12.6002 | 12.647 | 12.7117 | 12.7033 | 12.6939 | 12.6839 | 12.674 | 12.6633 | 12.6526 | 12.6375 | 12.6214 | 12.6054 | 12.5235 | 5.7169 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.4586 | 12.5254 | 12.6002 | 12.647 | 12.7117 | 12.7033 | 12.6939 | 12.6839 | 12.674 | 12.6633 | 12.6526 | 12.6374 | 12.6214 | 12.6054 | 10.4189 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.4586 | 12.5106 | 12.5641 | 12.6119 | 12.662 | 12.6622 | 12.6623 | 12.6613 | 12.6593 | 12.6573 | 12.6551 | 12.6529 | 12.6473 | 12.6363 | 12.577 | 12.5121 | 12.4567
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.4586 | 12.5318 | 12.6048 | 12.6623 | 12.7289 | 12.7204 | 8.4462 | 8.4376 | 8.4252 | 8.4103 | 8.3938 | 8.3776 | 8.3616 | 8.3454 | 3.4568 | 0 | 0
Coventry 132kV | WOOD LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.4586 | 12.5254 | 12.6009 | 12.6493 | 12.7156 | 12.708 | 12.7004 | 12.6902 | 12.68 | 12.6688 | 12.6551 | 12.6415 | 12.6279 | 12.615 | 12.5358 | 12.4534 | 7.0921
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.6849 | 11.6725 | 11.66 | 11.6066 | 11.5385 | 11.4446 | 11.3413 | 11.2258 | 11.1145 | 11.0133 | 10.9036 | 10.0421 | 8.024 | 6.3109 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.6849 | 11.6724 | 11.6595 | 11.6058 | 11.5377 | 11.4446 | 11.3422 | 11.2295 | 11.1202 | 11.0168 | 10.9119 | 10.0823 | 8.0703 | 6.3584 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.6849 | 11.6784 | 11.6782 | 11.6778 | 11.6751 | 11.6714 | 11.6667 | 11.6615 | 11.6538 | 11.6458 | 11.6394 | 11.6352 | 11.6336 | 11.6349 | 11.6725 | 11.6861 | 11.2621
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.6849 | 11.6719 | 11.6571 | 11.5989 | 11.5282 | 11.4368 | 11.3381 | 11.2342 | 11.1137 | 11.0106 | 10.9046 | 10.8006 | 8.8061 | 6.8211 | 0 | 0 | 0
Coventry 132kV | WOODFORD HALSE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.6849 | 11.6759 | 11.6713 | 11.6588 | 11.6392 | 11.6122 | 11.5821 | 11.5484 | 11.5109 | 11.4736 | 11.4383 | 11.4071 | 11.381 | 11.0036 | 7.2669 | 2.6709 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.3872 | 16.3493 | 16.2895 | 16.423 | 16.4836 | 16.3253 | 16.1303 | 15.8924 | 15.8353 | 15.5605 | 15.2402 | 14.8727 | 14.5239 | 14.2864 | 13.3449 | 10.0612 | 2.6565
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.3872 | 16.3398 | 16.2685 | 16.372 | 16.4272 | 16.1292 | 15.7707 | 15.3532 | 15.1905 | 14.7554 | 14.2771 | 13.7315 | 13.1483 | 12.6428 | 9.6789 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.3872 | 16.3726 | 16.354 | 16.5523 | 16.6807 | 16.6783 | 16.672 | 16.6647 | 16.7695 | 16.7778 | 16.7793 | 16.7761 | 16.7701 | 16.7474 | 16.6111 | 16.4913 | 16.1954
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.3872 | 16.3476 | 16.2833 | 16.4175 | 16.478 | 16.241 | 15.9435 | 15.5799 | 15.2901 | 14.8604 | 14.381 | 13.8564 | 13.3168 | 11.9198 | 5.1194 | 0 | 0
Drakelow 132kV | ASHBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.3872 | 16.3597 | 16.3226 | 16.5169 | 16.6513 | 16.5781 | 16.4938 | 16.3845 | 16.4978 | 16.3765 | 16.2351 | 16.0865 | 15.9227 | 15.7806 | 14.5616 | 13.3164 | 12.5173
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.6314 | 14.6487 | 14.6064 | 14.5298 | 14.452 | 14.3664 | 14.2806 | 14.1561 | 13.9897 | 13.7535 | 13.4514 | 13.115 | 12.724 | 12.4222 | 11.6575 | 10.3877 | 8.9645
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.6314 | 14.6303 | 14.5612 | 14.4113 | 14.2667 | 14.0337 | 13.7581 | 13.3917 | 12.8365 | 12.1514 | 11.3674 | 10.5532 | 9.6122 | 8.8406 | 5.6404 | 1.8008 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.6314 | 14.648 | 14.6225 | 14.5957 | 14.5633 | 14.5238 | 14.4749 | 14.3939 | 14.2555 | 14.042 | 13.7659 | 13.4764 | 13.1111 | 12.841 | 12.4202 | 11.7129 | 10.8136
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.6314 | 14.6314 | 14.5585 | 14.4046 | 14.257 | 14.0531 | 13.8408 | 13.6127 | 13.2526 | 12.8506 | 12.2568 | 11.5261 | 10.5993 | 9.086 | 5.7896 | 0 | 0
Drakelow 132kV | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.6314 | 14.6482 | 14.6048 | 14.5428 | 14.473 | 14.3776 | 14.2569 | 14.0554 | 13.6797 | 13.1902 | 12.6222 | 12.0649 | 11.397 | 10.8993 | 9.2542 | 7.2027 | 4.6316
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.7512 | 18.6341 | 18.5116 | 18.253 | 18.0073 | 17.7802 | 17.5853 | 17.3885 | 17.2391 | 14.6546 | 14.5799 | 14.3202 | 13.9386 | 13.5928 | 11.9818 | 9.3864 | 6.2402
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.7512 | 18.6268 | 18.488 | 18.1792 | 17.8921 | 17.5615 | 17.3005 | 14.6298 | 14.3982 | 13.8756 | 13.1652 | 12.3245 | 11.4037 | 10.7146 | 7.3286 | 2.9637 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.7512 | 18.6946 | 18.6513 | 18.6093 | 18.5544 | 18.4921 | 18.419 | 18.3223 | 18.1755 | 17.981 | 17.7587 | 17.5526 | 17.3398 | 17.2328 | 17.1354 | 17.0504 | 14.5808
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.7512 | 18.621 | 18.4699 | 18.1475 | 17.8569 | 17.5564 | 17.327 | 17.2031 | 14.5705 | 14.3131 | 13.8151 | 13.1288 | 12.2342 | 11.4274 | 7.426 | 0 | 0
Drakelow 132kV | BRETBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.7512 | 18.6667 | 18.5835 | 18.4623 | 18.3216 | 18.1562 | 17.9795 | 17.752 | 17.4866 | 17.2657 | 14.67 | 14.5935 | 14.3385 | 14.1265 | 13.2123 | 11.2999 | 8.7267
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Best View | Headroom (MW) | 102.8776 | 102.1873 | 101.9679 | 101.511 | 101.3213 | 101.1152 | 96.3742 | 96.0581 | 95.615 | 95.1837 | 94.6442 | 93.8501 | 93.2679 | 92.7777 | 89.3627 | 82.2141 | 72.8332
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 102.8776 | 102.0271 | 101.5496 | 96.2961 | 95.8348 | 94.5961 | 93.0807 | 91.2417 | 89.217 | 87.2648 | 85.3627 | 83.1035 | 80.9736 | 79.0956 | 68.1792 | 53.2341 | 35.5297
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Falling Short | Headroom (MW) | 102.8776 | 102.5731 | 102.0615 | 101.8522 | 101.8141 | 101.6028 | 101.4125 | 101.2298 | 101.0546 | 100.9526 | 96.565 | 96.4362 | 96.1871 | 95.9828 | 96.2012 | 96.0377 | 93.1863
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | Leading the Way | Headroom (MW) | 102.8776 | 102.0008 | 101.4919 | 96.2459 | 95.66 | 94.2953 | 92.6671 | 90.9056 | 88.9329 | 87.0687 | 85.1489 | 83.0946 | 80.8395 | 78.641 | 65.2703 | 48.559 | 29.0695
Drakelow 132kV | Burton 11kV | Primary Substation | 11 | System Transformation | Headroom (MW) | 102.8776 | 102.149 | 101.7908 | 101.4191 | 101.251 | 96.4034 | 96.165 | 95.5626 | 94.604 | 93.5322 | 92.396 | 91.3326 | 90.2231 | 89.4169 | 85.3609 | 77.6312 | 67.7305
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Best View | Headroom (MW) | 74.7171 | 70.1797 | 67.601 | 65.3554 | 63.1557 | 60.9452 | 58.8002 | 56.1128 | 53.0063 | 49.3545 | 44.9906 | 40.0933 | 34.6598 | 30.4915 | 16.5828 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 74.7171 | 70.097 | 67.3539 | 64.6148 | 61.938 | 58.6488 | 54.9847 | 50.2206 | 44.1243 | 37.0398 | 29.1982 | 20.9167 | 11.6815 | 5.197 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 74.7171 | 72.1896 | 70.2018 | 68.2407 | 67.7716 | 67.2277 | 66.5403 | 65.5199 | 63.8447 | 61.3904 | 58.2999 | 55.0953 | 51.0262 | 48.2948 | 45.2978 | 40.7045 | 32.2029
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 74.7171 | 70.0508 | 49.8675 | 46.9773 | 44.222 | 41.1983 | 38.1534 | 34.9517 | 30.4873 | 25.9846 | 19.7734 | 12.3027 | 2.9878 | 0 | 0 | 0 | 0
Drakelow 132kV | Burton 33kV | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 74.7171 | 70.423 | 68.1559 | 67.0836 | 65.8446 | 64.2663 | 62.41 | 59.7048 | 55.6736 | 50.727 | 45.1708 | 39.8133 | 33.4939 | 29.3447 | 19.2423 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 52.915 | 34.0127 | 33.6722 | 32.9493 | 32.3716 | 31.8193 | 31.1999 | 30.2614 | 28.8967 | 27.1049 | 25.2338 | 23.0274 | 20.4194 | 18.2909 | 12.2988 | 2.2795 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 52.915 | 33.8149 | 33.1812 | 31.7429 | 30.4625 | 28.5281 | 26.1256 | 22.9908 | 18.434 | 13.1644 | 8.1654 | 2.7274 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 52.915 | 34.5041 | 33.7349 | 33.4759 | 33.341 | 33.5021 | 33.4661 | 33.1881 | 32.512 | 31.352 | 29.7732 | 28.1079 | 25.9699 | 24.3951 | 21.6307 | 17.1351 | 10.8779
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 52.915 | 33.8153 | 33.1328 | 31.6393 | 30.308 | 28.7647 | 26.5034 | 23.8565 | 19.906 | 15.7712 | 11.6081 | 6.6402 | 0.63979 | 0 | 0 | 0 | 0
Drakelow 132kV | BURTON SOUTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 52.915 | 33.9821 | 33.6182 | 33.0545 | 32.5355 | 31.8754 | 30.9406 | 29.4536 | 26.6923 | 23.333 | 19.8925 | 16.4725 | 12.223 | 8.9612 | 16.3257 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.2871 | 15.8305 | 15.7162 | 15.7223 | 8.6653 | 8.3679 | 8.0609 | 7.5743 | 7.0112 | 6.3699 | 5.6084 | 4.786 | 3.8947 | 3.2051 | 0.6357 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.2871 | 9.0941 | 8.9302 | 8.8264 | 8.4594 | 7.9412 | 7.3415 | 6.4913 | 5.4267 | 4.2106 | 2.8568 | 1.4374 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.2871 | 15.9916 | 15.8452 | 16.0056 | 9.2598 | 9.1968 | 9.1142 | 8.9764 | 8.7476 | 8.3966 | 7.9564 | 7.4936 | 6.9113 | 6.4903 | 5.8848 | 6.6307 | 5.2838
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.2871 | 15.8176 | 15.6758 | 15.6137 | 15.3001 | 14.8878 | 14.4323 | 13.8034 | 12.9727 | 12.1166 | 10.9838 | 9.6875 | 8.107 | 5.4299 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.2871 | 9.1425 | 9.0482 | 9.177 | 9.0136 | 8.8054 | 8.5475 | 8.1092 | 7.4582 | 6.6693 | 5.7853 | 4.941 | 3.9493 | 3.2616 | 0.31551 | 0 | 1.4905
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 61.5802 | 59.2104 | 58.368 | 57.8076 | 40.7055 | 38.5627 | 36.3426 | 33.4559 | 30.7066 | 27.3316 | 24.4152 | 20.0419 | 15.6397 | 12.148 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 61.5802 | 43.7486 | 42.7967 | 41.9045 | 40.1096 | 36.8579 | 33.2236 | 28.6569 | 23.9763 | 18.3114 | 12.1074 | 5.3882 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 61.5802 | 60.4329 | 59.3601 | 60.2987 | 44.919 | 44.5708 | 44.1466 | 43.5373 | 42.8736 | 41.5824 | 39.9788 | 38.3164 | 36.262 | 34.7784 | 32.7042 | 33.3591 | 27.3756
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 61.5802 | 59.1515 | 58.1778 | 57.4376 | 55.6846 | 52.8193 | 49.7406 | 46.0689 | 41.8088 | 37.3434 | 35.8818 | 29.7082 | 22.6165 | 11.6496 | 0 | 0 | 0
Drakelow 132kV | GRESLEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 61.5802 | 44.0394 | 43.5145 | 44.0558 | 43.5102 | 42.2757 | 40.8761 | 38.8456 | 36.6497 | 33.5265 | 30.0711 | 26.7517 | 22.9868 | 20.3568 | 11.8445 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.6855 | 24.6327 | 23.6708 | 23.291 | 22.9236 | 22.5493 | 22.1879 | 21.7324 | 21.2039 | 20.5277 | 19.6987 | 18.7767 | 17.7209 | 16.9201 | 14.5876 | 10.9878 | 6.9127
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.6855 | 24.6093 | 23.6093 | 23.1129 | 22.6356 | 22.1256 | 21.5582 | 20.789 | 19.7186 | 18.3904 | 16.8797 | 15.3232 | 13.5411 | 12.3098 | 8.0571 | 2.4278 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.6855 | 25.4716 | 24.6101 | 23.7432 | 23.6403 | 23.5163 | 23.367 | 23.1516 | 22.804 | 22.2898 | 21.6406 | 20.9651 | 20.0999 | 19.502 | 18.8241 | 17.6084 | 15.7851
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.6855 | 24.6 | 14.8116 | 14.2846 | 13.792 | 13.3033 | 12.8387 | 12.3887 | 11.68 | 10.9245 | 9.7621 | 8.3267 | 6.4839 | 4.8675 | 0 | 0 | 0
Drakelow 132kV | HATTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.6855 | 24.6677 | 23.75 | 23.5428 | 23.3086 | 23.0068 | 22.6449 | 22.1185 | 21.2855 | 20.2072 | 18.9687 | 17.7722 | 16.3448 | 15.3739 | 12.9015 | 9.0152 | 4.0443
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.1306 | 0.76088 | 0.67833 | 0.48525 | 0.29831 | 0.099662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.1306 | 0.75932 | 0.6747 | 0.47702 | 0.28126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.1306 | 1.0702 | 0.76876 | 0.73694 | 0.702 | 0.659 | 0.60561 | 0.51809 | 0.37673 | 0.1639 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.1306 | 0.75738 | 0.66603 | 0.46389 | 0.26928 | 0.0021928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | MOIRA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.1306 | 0.78485 | 0.73288 | 0.65449 | 0.56356 | 0.44199 | 0.2964 | 0.061019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | STATION STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0796 | 15.0269 | 14.9911 | 14.9168 | 14.852 | 14.8004 | 14.7753 | 14.172 | 14.031 | 13.7997 | 13.4778 | 13.1111 | 12.6601 | 12.3368 | 11.6016 | 10.5954 | 9.4814
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0796 | 15.0273 | 14.9917 | 14.9099 | 14.8409 | 14.7863 | 14.1939 | 14.0448 | 13.6962 | 13.2247 | 12.662 | 12.0863 | 11.3989 | 10.9962 | 9.8098 | 8.371 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0796 | 15.0455 | 15.034 | 15.0224 | 15.0082 | 14.9874 | 14.956 | 14.8977 | 14.812 | 14.2078 | 14.0554 | 13.7952 | 13.4194 | 13.1656 | 12.8854 | 12.5129 | 11.998
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0796 | 15.0252 | 14.9854 | 14.9008 | 14.8325 | 14.7871 | 14.2038 | 14.1714 | 14.0096 | 13.802 | 13.4112 | 12.8852 | 12.18 | 11.6453 | 9.9706 | 0 | 0
Drakelow 132kV | TRENT ALLOYS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0796 | 15.0385 | 15.0162 | 14.9835 | 14.9456 | 14.8899 | 14.8256 | 14.2073 | 14.0668 | 13.724 | 13.2796 | 12.8341 | 12.288 | 11.9489 | 11.2071 | 10.1567 | 8.7864
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.6836 | 6.4494 | 6.3462 | 6.1149 | 5.9526 | 5.8178 | 5.6449 | 5.3557 | 4.8924 | 4.2833 | 3.6936 | 2.9762 | 2.1008 | 1.3772 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.6836 | 6.3731 | 6.1567 | 5.6564 | 5.2254 | 4.5683 | 3.7223 | 2.6064 | 0.97382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.6836 | 6.6947 | 6.3504 | 6.26 | 6.238 | 6.3758 | 6.4217 | 6.3779 | 6.1958 | 5.8479 | 5.3549 | 4.8298 | 4.1423 | 3.6368 | 2.6823 | 1.1543 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.6836 | 6.3743 | 6.1418 | 5.6192 | 5.168 | 4.682 | 3.8528 | 2.8489 | 1.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drakelow 132kV | WELLINGTON ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.6836 | 6.4358 | 6.3197 | 6.129 | 5.9725 | 5.783 | 5.4814 | 4.9847 | 4.0326 | 2.8923 | 1.7801 | 0.66039 | 0 | 0 | 3.6481 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.5034 | 13.3813 | 13.2537 | 12.9968 | 12.6283 | 12.2604 | 11.9114 | 11.536 | 11.1733 | 10.8479 | 10.5003 | 10.0969 | 9.7541 | 9.3946 | 6.9378 | 3.4186 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.5034 | 13.3804 | 13.2519 | 13.0008 | 12.6401 | 12.2314 | 11.8256 | 11.3974 | 10.9882 | 10.6103 | 10.2362 | 9.7896 | 9.3916 | 8.9839 | 6.1031 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.5034 | 13.4593 | 13.4346 | 13.5088 | 13.4564 | 13.4026 | 13.3472 | 13.2951 | 13.233 | 13.1809 | 13.138 | 13.1102 | 13.0991 | 13.0957 | 13.2249 | 13.2309 | 12.6525
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.5034 | 13.374 | 13.228 | 12.9771 | 12.6126 | 12.2114 | 11.8151 | 11.4201 | 10.9708 | 10.5823 | 10.189 | 9.7928 | 9.3813 | 8.9285 | 3.5482 | 0 | 0
Drakelow 132kV | WILLESLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.5034 | 13.4252 | 13.3639 | 13.3517 | 13.1936 | 13.0173 | 12.8471 | 12.6751 | 12.5024 | 12.3484 | 12.2061 | 12.084 | 11.9835 | 11.904 | 11.0976 | 8.4796 | 6.6494
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Best View | Headroom (MW) | 25.463 | 22.5895 | 22.5938 | 22.5407 | 22.4283 | 22.271 | 22.0823 | 21.8323 | 21.527 | 21.1709 | 20.7393 | 20.2447 | 19.7099 | 19.2831 | 17.536 | 15.0852 | 12.207
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.463 | 22.5895 | 22.5924 | 22.5278 | 22.3949 | 22.1349 | 21.7765 | 21.2887 | 20.6869 | 19.9948 | 19.2147 | 18.358 | 17.4229 | 16.7384 | 13.6313 | 8.7644 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.463 | 25.4436 | 25.4307 | 22.612 | 22.6204 | 22.6249 | 22.6237 | 22.611 | 22.569 | 22.4785 | 22.3288 | 22.1443 | 21.8816 | 21.6962 | 21.4775 | 21.2017 | 20.4669
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.463 | 22.5895 | 22.5906 | 22.5171 | 22.374 | 22.1364 | 21.8414 | 21.4952 | 21.0325 | 20.5572 | 19.9267 | 19.1868 | 18.291 | 17.5222 | 11.6804 | 0 | 0
Drakelow 132kV | WOODVILLE 33/11kV | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.463 | 25.4429 | 22.6001 | 22.6002 | 22.5822 | 22.5363 | 22.4589 | 22.3152 | 22.0702 | 21.7407 | 21.3439 | 20.9422 | 20.4652 | 20.1545 | 19.0885 | 16.3189 | 14.0506
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 29.814 | 29.7779 | 29.7191 | 29.4876 | 29.2135 | 28.9017 | 28.5745 | 28.2132 | 27.8673 | 27.5468 | 27.1902 | 26.7589 | 26.3865 | 25.9908 | 24.1569 | 16.5519 | 11.4015
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 29.814 | 29.7702 | 29.701 | 29.484 | 29.2236 | 28.9369 | 28.6341 | 28.3143 | 28.007 | 27.7285 | 27.4495 | 27.1111 | 26.8362 | 26.5392 | 25.0495 | 21.7441 | 22.824
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 29.814 | 29.8088 | 29.802 | 29.7839 | 29.756 | 29.7246 | 29.6889 | 29.6484 | 29.5962 | 29.5494 | 29.5087 | 29.4748 | 29.4618 | 29.4588 | 29.5298 | 30.0109 | 29.5011
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 29.814 | 29.7743 | 29.705 | 29.474 | 29.2009 | 28.8919 | 28.5624 | 28.2339 | 27.9072 | 27.5918 | 27.2689 | 26.9399 | 26.5936 | 26.2151 | 24.1771 | 16.5498 | 11.3726
East Claydon 132kV | BLETCHLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 29.814 | 29.7878 | 29.7514 | 29.681 | 29.5823 | 29.4593 | 29.3256 | 29.1889 | 29.0505 | 28.9278 | 28.8143 | 28.7139 | 28.6321 | 28.5683 | 28.6612 | 26.6006 | 24.4221
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 63.2899 | 19.9951 | 17.3513 | 13.8541 | 10.365 | 6.7407 | 2.9856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 63.2899 | 19.9218 | 17.2115 | 13.7961 | 10.3649 | 6.7917 | 3.2158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 63.2899 | 63.3373 | 63.3795 | 63.4214 | 63.4283 | 63.4525 | 8.8925 | 6.5949 | 4.2922 | 2.0695 | 0 | 0 | 0 | 0 | 0 | 46.6771 | 40.4074
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 63.2899 | 19.9739 | 17.2753 | 13.7912 | 10.3077 | 6.6893 | 2.9206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BLETCHLEY 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 63.2899 | 63.3465 | 63.4392 | 63.7441 | 12.2112 | 9.3659 | 6.5287 | 3.8373 | 1.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Best View | Headroom (MW) | 11.2921 | 11.2793 | 11.2273 | 11.063 | 10.9099 | 10.6782 | 10.423 | 10.0748 | 9.6104 | 9.0543 | 8.4417 | 7.7914 | 7.0747 | 6.5032 | 3.0279 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.2921 | 11.2787 | 11.225 | 11.0606 | 10.9077 | 10.678 | 10.4242 | 10.0805 | 9.6216 | 9.0625 | 8.4613 | 7.824 | 7.1105 | 6.539 | 3.0198 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.2921 | 11.3078 | 11.3057 | 11.3018 | 11.2932 | 11.2795 | 11.257 | 11.21 | 11.1193 | 10.9693 | 10.7865 | 10.5964 | 10.3571 | 10.1874 | 10.0046 | 9.6204 | 8.9495
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.2921 | 11.2788 | 11.2161 | 11.0438 | 10.8854 | 10.6827 | 10.4803 | 10.239 | 9.9044 | 9.5302 | 9.0567 | 8.4851 | 7.7714 | 5.0528 | 0 | 0 | 0
East Claydon 132kV | Brackley 11kv | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.2921 | 11.3043 | 11.281 | 11.2324 | 11.1776 | 11.0914 | 10.9911 | 10.8218 | 10.5458 | 10.1822 | 9.7843 | 9.3996 | 8.944 | 8.6121 | 6.5765 | 3.9341 | 1.8977
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 77.4403 | 31.5775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 77.4403 | 30.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 77.4403 | 59.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 77.4403 | 23.9561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 77.4403 | 29.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.8072 | 20.5946 | 20.545 | 20.3176 | 20.0919 | 19.8101 | 19.5137 | 19.1786 | 18.7685 | 16.9038 | 16.5989 | 15.8915 | 14.9043 | 14.0655 | 11.0448 | 5.5842 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.8072 | 20.5866 | 20.5316 | 20.3049 | 20.0809 | 19.7868 | 19.459 | 19.0491 | 18.6295 | 16.7695 | 16.1827 | 15.3648 | 14.3544 | 13.5993 | 10.8971 | 4.8446 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.8072 | 20.8297 | 20.6092 | 20.5694 | 20.5256 | 20.4708 | 20.4054 | 20.3004 | 20.126 | 19.8756 | 19.5671 | 19.2517 | 18.8808 | 18.6562 | 16.998 | 16.8651 | 16.1702
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.8072 | 20.5924 | 20.5326 | 20.2982 | 20.069 | 19.7997 | 19.5362 | 19.2692 | 18.9118 | 18.6177 | 16.8173 | 16.2893 | 15.3767 | 14.4994 | 11.0994 | 4.2655 | 0
East Claydon 132kV | BRACKLEY TOWN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.8072 | 20.6105 | 20.5941 | 20.5014 | 20.3934 | 20.2462 | 20.0735 | 19.8125 | 19.4036 | 18.9122 | 18.5706 | 16.7882 | 16.3102 | 15.8616 | 14.4962 | 12.4757 | 9.7937
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 86.7811 | 118.473 | 119.0493 | 104.3033 | 87.5186 | 69.0903 | 49.6246 | 28.5985 | 4.8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 86.7811 | 82.556 | 78.2796 | 63.957 | 48.2668 | 30.0783 | 10.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 86.7811 | 84.992 | 84.3773 | 83.0806 | 80.7464 | 78.1098 | 74.8977 | 70.3828 | 63.3306 | 53.4229 | 41.2053 | 28.3879 | 12.4842 | 1.9128 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 86.7811 | 118.2458 | 117.9218 | 103.7436 | 87.1409 | 69.1484 | 49.7884 | 30.864 | 8.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BRADWELL ABBEY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 86.7811 | 118.2719 | 121.5104 | 117.1614 | 110.3528 | 102.0759 | 90.522 | 76.9172 | 59.1311 | 39.1401 | 17.76 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.7297 | 16.7112 | 16.6704 | 16.4987 | 16.2784 | 15.9341 | 15.5406 | 15.0977 | 14.3731 | 13.5391 | 12.2944 | 10.7432 | 8.7824 | 0.12227 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.7297 | 16.7103 | 16.6716 | 16.4943 | 16.2697 | 15.8625 | 15.3364 | 14.6004 | 13.4496 | 11.99 | 10.3105 | 8.5348 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.7297 | 16.7322 | 16.738 | 16.7398 | 16.7317 | 16.7146 | 16.6816 | 16.605 | 16.4255 | 16.0841 | 15.5837 | 15.0209 | 14.2886 | 13.746 | 12.9962 | 11.5188 | 9.5522
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.7297 | 16.7107 | 16.6687 | 16.4825 | 16.2506 | 15.8871 | 15.4751 | 15.0109 | 14.2635 | 13.4014 | 12.1204 | 10.5289 | 8.5147 | 0 | 0 | 0 | 0
East Claydon 132kV | BUCKINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.7297 | 16.7243 | 16.7131 | 16.6748 | 16.6111 | 16.4961 | 16.3242 | 15.9886 | 15.2692 | 14.2492 | 13.0346 | 11.826 | 10.3655 | 9.1084 | 0 | 0 | 0
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.4715 | 19.4334 | 19.3835 | 19.2456 | 19.0899 | 18.9023 | 18.6437 | 18.361 | 17.6379 | 17.5522 | 17.4243 | 17.2552 | 17.1218 | 17.0093 | 16.4513 | 15.569 | 11.9447
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.4715 | 19.4331 | 19.3808 | 19.2574 | 19.1155 | 18.9375 | 18.7266 | 18.4929 | 18.2451 | 17.6306 | 17.5895 | 17.4849 | 17.36 | 17.2259 | 16.5046 | 15.7461 | 14.7674
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.4715 | 19.4524 | 19.4296 | 19.3973 | 19.387 | 19.3745 | 19.3614 | 19.3463 | 19.3291 | 19.3032 | 19.2686 | 19.2356 | 19.2064 | 19.1844 | 19.1734 | 19.1978 | 19.0219
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.4715 | 19.4309 | 19.3749 | 19.2385 | 19.0838 | 18.8973 | 18.6374 | 18.3655 | 18.1039 | 17.5586 | 17.4401 | 17.2992 | 17.1749 | 17.0679 | 16.458 | 15.5741 | 12.1868
East Claydon 132kV | Campbell Park 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.4715 | 19.4489 | 19.4188 | 19.3663 | 19.2981 | 19.2057 | 19.0944 | 18.9728 | 18.8351 | 18.7247 | 18.6373 | 18.5575 | 18.4751 | 18.4063 | 18.1238 | 17.5074 | 17.0744
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 32.1198 | 32.0761 | 32.0119 | 31.8172 | 31.6002 | 31.3571 | 31.1395 | 30.8944 | 30.6545 | 30.4252 | 30.173 | 29.8927 | 29.652 | 29.4179 | 32.5745 | 31.0981 | 19.4845
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.1198 | 32.0765 | 32.0118 | 31.8353 | 31.6355 | 31.4075 | 31.1881 | 30.9469 | 30.732 | 30.5146 | 30.2981 | 30.0546 | 29.8399 | 29.629 | 28.2011 | 31.5469 | 29.4152
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.1198 | 32.1035 | 32.0868 | 32.0638 | 32.0423 | 32.0197 | 31.993 | 31.9656 | 31.9297 | 31.8954 | 31.8679 | 31.8464 | 31.8324 | 31.8243 | 31.886 | 31.8518 | 31.5357
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.1198 | 32.0731 | 32.0006 | 31.8069 | 31.5907 | 31.3494 | 31.1281 | 30.9044 | 30.676 | 30.4482 | 30.2121 | 29.9822 | 29.76 | 29.5287 | 32.577 | 31.0979 | 19.4748
East Claydon 132kV | CHILDS WAY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.1198 | 32.0934 | 32.0601 | 31.9977 | 31.9159 | 31.8103 | 31.7078 | 31.6012 | 31.4974 | 31.3925 | 31.3002 | 31.2177 | 31.1406 | 31.0805 | 30.6639 | 34.697 | 32.8899
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 26.6089 | 26.5815 | 26.5437 | 26.4881 | 26.4308 | 26.3701 | 26.3177 | 26.2813 | 26.2232 | 26.1846 | 26.1421 | 26.0988 | 26.059 | 19.7256 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 26.6089 | 26.5809 | 26.5438 | 26.4913 | 26.4367 | 26.377 | 26.3142 | 26.2658 | 26.214 | 26.1598 | 26.1047 | 26.0621 | 21.3323 | 13.4736 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 26.6089 | 26.5889 | 26.5634 | 26.5399 | 26.521 | 26.5007 | 26.4808 | 26.4699 | 26.449 | 26.427 | 26.4054 | 26.3845 | 26.3631 | 26.3506 | 26.292 | 26.2217 | 26.1285
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 26.6089 | 26.5812 | 26.5426 | 26.4871 | 26.4296 | 26.3693 | 26.3166 | 26.2821 | 26.2249 | 26.1864 | 26.1456 | 26.1063 | 26.0677 | 21.2582 | 0 | 0 | 0
East Claydon 132kV | ELDERGATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 26.6089 | 26.594 | 26.5669 | 26.5371 | 26.5046 | 26.4649 | 26.4245 | 26.3998 | 26.3668 | 26.3299 | 26.2914 | 26.2672 | 26.2446 | 26.2247 | 21.0756 | 1.4791 | 0
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.8584 | 17.1219 | 17.0714 | 17.0158 | 16.9585 | 16.8993 | 16.8413 | 16.7835 | 16.7247 | 16.6703 | 16.6167 | 16.564 | 16.5119 | 16.4547 | 18.4981 | 18.215 | 17.7126
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.8584 | 17.1219 | 17.0714 | 17.0158 | 16.9585 | 16.8993 | 16.8413 | 16.7835 | 16.7287 | 16.6736 | 16.6192 | 16.5652 | 16.5078 | 16.4505 | 18.5098 | 18.2123 | 17.7125
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.8584 | 19.802 | 19.6254 | 19.5698 | 19.5136 | 19.4579 | 16.8749 | 16.8217 | 16.7687 | 16.7175 | 16.6666 | 16.616 | 16.5657 | 16.5158 | 16.281 | 18.399 | 18.1938
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.8584 | 17.1219 | 17.0714 | 17.0158 | 16.9585 | 16.8993 | 16.8413 | 16.7835 | 16.7247 | 16.6703 | 16.6173 | 16.5651 | 16.513 | 16.4558 | 18.5 | 18.2162 | 17.7134
East Claydon 132kV | FEN FARM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.8584 | 19.6815 | 19.6242 | 19.5649 | 16.9716 | 16.9172 | 16.8629 | 16.8088 | 16.7549 | 16.7013 | 16.6479 | 16.5941 | 16.5436 | 16.4937 | 18.5648 | 18.2958 | 17.8513
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.5419 | 18.6487 | 18.6193 | 18.2121 | 17.8233 | 17.4549 | 16.662 | 16.6381 | 16.3241 | 16.0357 | 15.5649 | 14.5417 | 13.4401 | 12.5197 | 10.9166 | 2.0853 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.5419 | 17.3664 | 17.1658 | 16.744 | 16.3439 | 15.946 | 15.5232 | 15.0365 | 14.5206 | 14.0454 | 13.5199 | 12.9381 | 12.2893 | 11.7514 | 8.5181 | 5.7117 | 0.57528
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.5419 | 17.4495 | 17.3657 | 17.2695 | 17.2018 | 17.1292 | 17.0374 | 16.9155 | 16.7215 | 16.4319 | 16.0624 | 15.6656 | 15.1589 | 14.8139 | 14.3261 | 13.9633 | 13.2232
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.5419 | 18.6394 | 18.5871 | 18.1863 | 17.8006 | 17.4358 | 16.6597 | 16.6393 | 16.3535 | 16.0632 | 15.6157 | 14.6844 | 13.616 | 12.7149 | 10.9709 | 2.1419 | 0
East Claydon 132kV | FOX MILNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.5419 | 18.6365 | 18.6812 | 18.5325 | 18.3596 | 18.1489 | 17.8992 | 17.5572 | 16.6875 | 16.6438 | 16.21 | 15.7585 | 15.2161 | 14.8393 | 13.0061 | 10.9091 | 9.0578
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.4799 | 7.4429 | 7.3967 | 7.2905 | 7.1898 | 7.0195 | 6.8405 | 6.6295 | 6.2916 | 5.9105 | 5.3245 | 4.5815 | 3.6497 | 2.8266 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.4799 | 7.4407 | 7.3918 | 7.2881 | 7.1869 | 6.964 | 6.6815 | 6.2932 | 5.7478 | 4.7076 | 3.2593 | 1.7098 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.4799 | 7.4615 | 7.4421 | 7.4229 | 7.4033 | 7.3722 | 7.3257 | 7.2361 | 7.0687 | 6.7951 | 6.4373 | 6.0543 | 5.5617 | 5.2339 | 4.7489 | 4.0986 | 3.1567
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.4799 | 7.4413 | 7.3909 | 7.2861 | 7.1863 | 7.0172 | 6.8379 | 6.6355 | 6.3031 | 5.923 | 5.3431 | 4.6188 | 3.6926 | 2.8727 | 0 | 0 | 0
East Claydon 132kV | HANSLOPE PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.4799 | 7.4553 | 7.4261 | 7.3848 | 7.3366 | 7.259 | 7.1456 | 6.9297 | 6.5512 | 6.0395 | 5.4419 | 4.8534 | 4.141 | 3.6917 | 2.5584 | 0.076464 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.0082 | 21.8946 | 21.7305 | 21.3063 | 20.889 | 20.4652 | 19.9871 | 19.5456 | 19.2099 | 16.4609 | 16.2162 | 15.8651 | 15.5272 | 15.1836 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.0082 | 21.8941 | 21.7267 | 21.3367 | 20.9412 | 20.5375 | 20.0992 | 19.6875 | 19.3362 | 19.141 | 16.4373 | 16.2314 | 15.9285 | 13.4107 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.0082 | 21.9534 | 21.8886 | 21.7995 | 21.7491 | 21.6902 | 21.6272 | 21.558 | 21.4741 | 21.3888 | 21.2946 | 21.1973 | 21.1073 | 21.0246 | 20.9209 | 20.7805 | 20.2305
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.0082 | 21.8888 | 21.7107 | 21.2914 | 20.8774 | 20.4569 | 19.9802 | 19.5603 | 19.2229 | 16.4668 | 16.2517 | 15.9666 | 15.6619 | 15.3378 | 0 | 0 | 0
East Claydon 132kV | KILN FARM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.0082 | 21.9388 | 21.8466 | 21.6874 | 21.4961 | 21.2707 | 21.0287 | 20.7824 | 20.5157 | 20.2543 | 19.9881 | 19.7902 | 19.6007 | 19.4519 | 16.583 | 1.4722 | 0
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.5736 | 22.4953 | 22.4068 | 22.2481 | 22.1023 | 21.9584 | 21.8198 | 21.6737 | 21.5403 | 21.4109 | 21.2748 | 21.1262 | 20.9957 | 20.8592 | 20.0372 | 18.9959 | 16.7991
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.5736 | 22.4957 | 22.4077 | 22.2574 | 22.1162 | 21.979 | 21.8467 | 21.7119 | 21.5874 | 21.4666 | 21.3512 | 21.2198 | 21.1054 | 20.9848 | 20.2337 | 19.2768 | 18.2495
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.5736 | 22.5169 | 22.462 | 22.4096 | 22.3552 | 22.3014 | 22.2473 | 22.1941 | 22.1401 | 22.0882 | 22.0395 | 21.9956 | 21.957 | 21.9231 | 21.8177 | 21.6559 | 21.355
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.5736 | 22.4928 | 22.3984 | 22.2414 | 22.0966 | 21.954 | 21.8144 | 21.6795 | 21.5528 | 21.4243 | 21.2953 | 21.1694 | 21.0454 | 20.912 | 20.0486 | 19.0065 | 16.8008
East Claydon 132kV | KINGSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.5736 | 22.5077 | 22.4396 | 22.3591 | 22.272 | 22.1808 | 22.0926 | 22.0058 | 21.9217 | 21.8421 | 21.7656 | 21.6956 | 21.6322 | 21.5744 | 21.2126 | 20.6765 | 20.047
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.4806 | 23.3988 | 23.2305 | 22.8217 | 22.4294 | 22.0424 | 21.6672 | 21.2929 | 20.9475 | 20.6362 | 20.3045 | 19.9381 | 19.6563 | 19.4094 | 15.5954 | 12.3282 | 7.7892
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.4806 | 23.3926 | 23.2213 | 22.8429 | 22.4718 | 22.1132 | 21.7656 | 21.4244 | 21.1112 | 20.837 | 20.5758 | 20.2571 | 20.0032 | 19.7513 | 16.1885 | 13.5544 | 9.8247
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.4806 | 23.4534 | 23.387 | 23.3119 | 23.2293 | 23.1452 | 23.0605 | 22.9812 | 22.8939 | 22.8187 | 22.7548 | 22.705 | 22.6681 | 22.6447 | 22.696 | 22.6334 | 21.9568
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.4806 | 23.3914 | 23.2047 | 22.8016 | 22.413 | 22.0313 | 21.6542 | 21.3161 | 20.9892 | 20.6813 | 20.3758 | 20.0825 | 19.8031 | 19.537 | 15.6163 | 12.3375 | 7.7734
East Claydon 132kV | MARLBOROUGH STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.4806 | 23.4328 | 23.3179 | 23.1569 | 22.9717 | 22.7689 | 22.5719 | 22.3871 | 22.2029 | 22.0379 | 21.8904 | 21.7604 | 21.6484 | 21.5602 | 20.829 | 19.4574 | 16.2908
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.4293 | 13.8593 | 14.1394 | 13.7362 | 13.2517 | 12.6746 | 12.0823 | 11.411 | 10.5414 | 9.6443 | 8.4421 | 6.9419 | 5.2013 | 3.7008 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.4293 | 10.2659 | 10.0698 | 9.603 | 9.1418 | 8.5399 | 7.8577 | 6.9812 | 5.8806 | 4.5866 | 3.1755 | 1.6659 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.4293 | 10.3539 | 10.2869 | 10.2157 | 10.1411 | 10.0472 | 9.9263 | 9.7337 | 9.4047 | 8.9043 | 8.266 | 7.5933 | 6.7429 | 6.1933 | 5.5612 | 4.6257 | 3.0755
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.4293 | 13.85 | 14.109 | 13.7118 | 13.2314 | 12.6599 | 12.0649 | 11.4381 | 10.5912 | 9.6992 | 8.5321 | 7.1391 | 5.4293 | 3.9464 | 0 | 0 | 0
East Claydon 132kV | NEWPORT PAGNELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.4293 | 13.7276 | 14.0852 | 13.9549 | 13.7908 | 13.5579 | 13.2637 | 12.7321 | 11.9538 | 10.9789 | 9.8844 | 8.8194 | 7.5682 | 6.7853 | 4.3774 | 0.074499 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.2913 | 25.1582 | 24.9785 | 24.5026 | 24.0345 | 23.4866 | 22.9723 | 22.4093 | 21.7071 | 20.9838 | 20.0155 | 18.8363 | 17.4952 | 16.2118 | 10.7974 | 4.1493 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.2913 | 25.1583 | 24.9789 | 24.5265 | 24.0743 | 23.4978 | 22.9044 | 22.1893 | 21.2835 | 20.2505 | 19.1104 | 17.8755 | 16.5277 | 15.4025 | 10.5962 | 4.0506 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.2913 | 25.2463 | 25.2023 | 25.1489 | 25.0945 | 25.0278 | 24.9422 | 24.824 | 24.6278 | 24.3501 | 24.0165 | 23.6696 | 23.2475 | 22.9497 | 22.6353 | 21.9641 | 20.6129
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.2913 | 25.1521 | 24.9567 | 24.4774 | 24.0074 | 23.4597 | 22.9372 | 22.3963 | 21.6999 | 20.9708 | 20.0195 | 18.9092 | 17.5769 | 16.2884 | 10.6474 | 3.897 | 0
East Claydon 132kV | NEWTON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.2913 | 25.2127 | 25.1181 | 24.9597 | 24.7632 | 24.5147 | 24.2477 | 23.8867 | 23.334 | 22.6658 | 21.9224 | 21.1986 | 20.3611 | 19.7493 | 17.8449 | 14.5616 | 10.3864
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.0403 | 20.9555 | 20.9547 | 20.7661 | 20.5638 | 20.3143 | 20.036 | 19.7567 | 19.5437 | 19.3465 | 19.1311 | 18.9055 | 18.7128 | 18.5327 | 16.7959 | 15.7638 | 11.9171
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.0403 | 20.9468 | 20.9405 | 20.7606 | 20.5677 | 20.327 | 20.0837 | 19.8398 | 19.6423 | 19.4512 | 19.2623 | 19.0478 | 18.8538 | 18.6681 | 16.8686 | 16.0102 | 14.6612
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.0403 | 20.9808 | 21.0068 | 20.9616 | 20.9194 | 20.8835 | 20.8424 | 20.7972 | 20.7465 | 20.6975 | 20.649 | 20.6057 | 20.5663 | 20.5292 | 20.4249 | 20.3132 | 20.0035
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.0403 | 20.9519 | 20.9447 | 20.758 | 20.5566 | 20.308 | 20.0283 | 19.7604 | 19.5538 | 19.3569 | 19.1504 | 18.9545 | 18.769 | 18.5909 | 16.7988 | 15.768 | 12.1586
East Claydon 132kV | PORTWAY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.0403 | 20.9647 | 20.9932 | 20.9087 | 20.808 | 20.6758 | 20.5386 | 20.4047 | 20.2865 | 20.1703 | 20.0541 | 19.9507 | 19.8518 | 19.7698 | 19.3186 | 18.645 | 16.9997
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.2727 | 17.2777 | 17.2811 | 17.2782 | 17.2688 | 17.2482 | 17.2096 | 17.1846 | 17.1582 | 17.1306 | 17.1002 | 17.0605 | 17.0266 | 16.9969 | 19.5318 | 19.1476 | 15.3493
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.2727 | 17.2767 | 17.2788 | 17.2755 | 17.266 | 17.2448 | 17.2124 | 17.1877 | 17.1624 | 17.1371 | 17.11 | 17.0764 | 17.0474 | 17.0159 | 16.8164 | 19.1916 | 18.8208
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.2727 | 17.2781 | 17.283 | 17.286 | 17.2883 | 17.2902 | 17.2907 | 17.2902 | 17.2884 | 17.2856 | 17.2823 | 17.2781 | 17.2731 | 17.2695 | 17.2585 | 17.2513 | 17.4208
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.2727 | 17.2776 | 17.2808 | 17.2778 | 17.2682 | 17.2472 | 17.2081 | 17.184 | 17.1579 | 17.1297 | 17.1007 | 17.0667 | 17.034 | 17.0052 | 19.5304 | 19.1475 | 15.3516
East Claydon 132kV | SECKLOW GATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.2727 | 17.2769 | 17.2799 | 17.2805 | 17.278 | 17.2703 | 17.2583 | 17.2483 | 17.2362 | 17.2253 | 17.2144 | 17.2038 | 17.1934 | 17.1836 | 17.1216 | 19.6944 | 19.4278
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 27.708 | 27.6791 | 27.5317 | 27.1453 | 26.7851 | 26.4373 | 26.1102 | 25.7595 | 25.4407 | 25.1531 | 24.8609 | 24.5903 | 23.5081 | 19.7172 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 27.708 | 27.6739 | 27.5255 | 27.1661 | 26.8234 | 26.5008 | 26.1944 | 25.8753 | 25.5883 | 25.3229 | 25.0754 | 24.8004 | 21.3232 | 13.4679 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 27.708 | 27.7269 | 27.6792 | 27.6314 | 27.5721 | 27.514 | 27.4564 | 27.4022 | 27.3408 | 27.2869 | 27.2434 | 27.2149 | 27.1981 | 27.1964 | 27.3591 | 27.3239 | 26.8013
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 27.708 | 27.6714 | 27.5046 | 27.124 | 26.7676 | 26.4252 | 26.096 | 25.7819 | 25.485 | 25.1994 | 24.9248 | 24.6842 | 24.5192 | 21.2492 | 0 | 0 | 0
East Claydon 132kV | SHENLEY WOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 27.708 | 27.7161 | 27.6264 | 27.488 | 27.3292 | 27.1586 | 26.993 | 26.8304 | 26.6719 | 26.5241 | 26.3885 | 26.2721 | 26.1745 | 26.0979 | 21.0666 | 1.4785 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.1847 | 20.7397 | 21.7672 | 22.6566 | 23.5967 | 24.3106 | 24.7841 | 25.0867 | 25.1199 | 24.3727 | 23.3528 | 22.1224 | 20.6073 | 19.3023 | 14.8184 | 5.7525 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.1847 | 20.684 | 21.7504 | 22.5059 | 23.4227 | 23.8294 | 24.179 | 24.3608 | 24.3654 | 23.4297 | 22.2962 | 21.1091 | 19.6724 | 18.5164 | 14.2038 | 4.9906 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.1847 | 21.2749 | 21.1281 | 21.8653 | 22.5465 | 23.1964 | 23.8148 | 24.2622 | 24.6972 | 24.7199 | 24.6388 | 24.5219 | 24.245 | 24.0473 | 23.1594 | 21.6717 | 20.1111
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.1847 | 20.6553 | 21.581 | 22.3638 | 23.1602 | 23.8202 | 24.3689 | 24.8099 | 25.0491 | 24.5491 | 23.7052 | 22.5574 | 21.0722 | 19.6775 | 14.7458 | 4.394 | 0
East Claydon 132kV | SILVERSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.1847 | 20.6133 | 21.6079 | 22.3217 | 23.1493 | 23.6495 | 24.234 | 24.6616 | 24.9315 | 24.3142 | 23.5404 | 22.7748 | 21.816 | 21.078 | 18.8225 | 15.4948 | 11.4196
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.9349 | 15.8175 | 15.7289 | 15.5544 | 15.3879 | 15.0871 | 14.7613 | 14.3901 | 13.679 | 12.8515 | 11.5791 | 8.6549 | 4.308 | 0.034612 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.9349 | 15.8186 | 15.7341 | 15.552 | 15.3802 | 14.9952 | 14.5029 | 13.7973 | 12.5945 | 10.9859 | 7.2982 | 3.4817 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.9349 | 15.8557 | 15.8367 | 15.8181 | 15.7914 | 15.745 | 15.6722 | 15.5184 | 15.2193 | 14.717 | 14.0692 | 13.3775 | 12.4949 | 11.8545 | 10.8588 | 10.3578 | 6.247
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.9349 | 15.8167 | 15.7274 | 15.5427 | 15.3716 | 15.0627 | 14.7301 | 14.3513 | 13.6318 | 12.7944 | 11.5091 | 8.4207 | 4.0207 | 0 | 0 | 0 | 0
East Claydon 132kV | STEEPLE CLAYDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.9349 | 15.8404 | 15.7904 | 15.7257 | 15.651 | 15.5212 | 15.3197 | 14.9119 | 14.0451 | 12.8629 | 11.4975 | 9.34 | 5.9592 | 3.4668 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 66.9308 | 83.4045 | 98.7817 | 93.9044 | 79.7349 | 58.5013 | 36.0565 | 10.6065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 66.9308 | 83.2788 | 98.6768 | 94.1976 | 80.3889 | 57.0421 | 30.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 66.9308 | 82.0273 | 97.6525 | 109.5203 | 112.2481 | 113.9219 | 114.1325 | 110.9119 | 100.2202 | 82.3074 | 57.9419 | 32.1286 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 66.9308 | 84.763 | 98.8363 | 96.2817 | 82.029 | 62.3564 | 40.6735 | 18.2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | STONY STRATFORD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 66.9308 | 85.7035 | 104.4339 | 112.7757 | 109.6307 | 101.4201 | 90.9596 | 73.2646 | 36.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Best View | Headroom (MW) | 32.4125 | 31.5784 | 31.5688 | 31.453 | 31.2859 | 31.0542 | 30.8126 | 30.5302 | 30.1825 | 29.8175 | 29.3158 | 28.6915 | 27.975 | 27.3176 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.4125 | 31.5783 | 31.568 | 31.4613 | 31.3026 | 31.0546 | 30.766 | 30.3996 | 29.9405 | 29.3952 | 28.79 | 28.1487 | 27.4464 | 26.8956 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.4125 | 32.405 | 32.4002 | 31.5826 | 31.5809 | 31.574 | 31.5608 | 31.5349 | 31.4796 | 31.3775 | 31.2353 | 31.0802 | 30.8813 | 30.7425 | 30.6406 | 30.3172 | 29.6576
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.4125 | 31.5783 | 31.5642 | 31.4438 | 31.2764 | 31.0469 | 30.8039 | 30.5458 | 30.2133 | 29.8513 | 29.3661 | 28.7919 | 28.09 | 27.4405 | 0 | 0 | 0
East Claydon 132kV | Tattenhoe Primary | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.4125 | 32.4032 | 31.5793 | 31.5642 | 31.5261 | 31.4569 | 31.3604 | 31.2108 | 30.971 | 30.6601 | 30.3055 | 29.9601 | 29.5588 | 29.2618 | 28.3229 | 17.7208 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.3237 | 11.1148 | 10.9536 | 10.848 | 10.7472 | 10.5602 | 10.3288 | 10.0043 | 9.4719 | 8.7991 | 8.0141 | 7.1992 | 6.2492 | 5.4564 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.3237 | 11.1145 | 10.9522 | 10.8464 | 10.7452 | 10.5585 | 10.3273 | 10.0048 | 9.4743 | 8.7999 | 8.0205 | 7.2119 | 6.2643 | 5.4716 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.3237 | 11.1363 | 11.1263 | 11.1153 | 11.1 | 11.0769 | 11.0432 | 10.9765 | 10.8493 | 10.6398 | 10.3632 | 10.0677 | 9.6911 | 9.415 | 9.0026 | 8.2644 | 7.3769
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.3237 | 11.1128 | 10.9465 | 10.8361 | 10.7316 | 10.5714 | 10.4006 | 10.2111 | 9.8798 | 9.5033 | 8.9238 | 8.1991 | 6.6219 | 5.6926 | 0 | 0 | 0
East Claydon 132kV | THENFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.3237 | 11.1277 | 11.1057 | 11.0683 | 11.0248 | 10.9567 | 10.8605 | 10.6787 | 10.3035 | 9.7946 | 9.1967 | 8.6093 | 7.8972 | 7.3701 | 5.6857 | 2.6736 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.0151 | 24.1466 | 27.2948 | 29.1615 | 29.6498 | 29.7438 | 29.847 | 29.8631 | 29.2493 | 28.1743 | 26.7893 | 25.3051 | 23.5999 | 22.1276 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.0151 | 24.1456 | 27.2907 | 29.1566 | 29.6436 | 29.7384 | 29.8422 | 29.8621 | 29.2517 | 28.1668 | 26.7977 | 25.3283 | 23.6262 | 19.4193 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.0151 | 23.5225 | 25.8949 | 28.0293 | 28.7681 | 29.4497 | 30.0711 | 30.6067 | 30.8921 | 30.9776 | 30.958 | 30.9106 | 30.6724 | 30.3683 | 29.2091 | 27.4939 | 25.3337
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.0151 | 24.3748 | 27.4071 | 29.6606 | 30.1926 | 30.524 | 30.7264 | 30.9426 | 30.5402 | 29.8217 | 28.6411 | 27.1222 | 25.2539 | 23.4007 | 0 | 0 | 0
East Claydon 132kV | TOWCESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.0151 | 24.1878 | 27.3919 | 29.4612 | 30.1122 | 30.448 | 30.7943 | 31.0512 | 30.8425 | 30.206 | 29.281 | 28.337 | 27.1724 | 26.2722 | 22.952 | 2.1319 | 0
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.6637 | 26.0414 | 25.8767 | 25.4515 | 25.0117 | 24.5561 | 24.1015 | 23.6403 | 23.2157 | 22.832 | 22.4265 | 21.9935 | 21.6334 | 21.2798 | 20.3176 | 16.806 | 12.6893
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.6637 | 26.0072 | 25.8311 | 25.4301 | 25.0195 | 24.5937 | 24.1779 | 23.7447 | 23.3538 | 22.989 | 22.631 | 22.2329 | 21.8943 | 21.3708 | 19.1068 | 15.9113 | 12.3744
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.6637 | 25.9723 | 25.9298 | 25.8711 | 25.8186 | 25.7663 | 25.7073 | 25.6388 | 25.5491 | 25.4855 | 25.4292 | 25.3859 | 25.3384 | 25.3038 | 25.2853 | 26.6287 | 26.0069
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.6637 | 26.0355 | 25.8553 | 25.4337 | 24.9956 | 24.54 | 24.0785 | 23.6463 | 23.2344 | 22.8527 | 22.4711 | 22.1159 | 21.7778 | 21.4256 | 20.2887 | 16.7537 | 12.6061
East Claydon 132kV | VICTORIA ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.6637 | 26.0519 | 25.9586 | 25.8015 | 25.6147 | 25.394 | 25.1741 | 24.9519 | 24.7446 | 24.5533 | 24.377 | 24.2238 | 24.0962 | 24.031 | 24.4885 | 22.9513 | 21.105
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 40.4752 | 40.3434 | 40.1724 | 40.6123 | 40.8424 | 40.8565 | 40.7067 | 40.3152 | 39.5535 | 38.9962 | 38.3731 | 36.8542 | 36.2794 | 36.2162 | 32.1664 | 30.519 | 27.0419
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 40.4752 | 40.3429 | 40.1695 | 40.5328 | 40.7798 | 40.6139 | 40.4893 | 40.1906 | 39.6 | 39.1361 | 38.6555 | 38.1907 | 36.8726 | 36.7617 | 32.1766 | 30.8307 | 27.9589
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 40.4752 | 40.4079 | 40.3337 | 40.9437 | 41.4251 | 41.8023 | 42.1662 | 42.3996 | 42.474 | 42.5273 | 42.5723 | 42.612 | 42.6538 | 42.6651 | 42.3921 | 42.08 | 41.3467
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 40.4752 | 40.3373 | 40.1515 | 40.5956 | 40.8284 | 40.8467 | 40.6949 | 40.3342 | 39.5872 | 39.0323 | 38.4258 | 37.9019 | 36.7876 | 36.2618 | 32.1694 | 30.5367 | 27.0439
East Claydon 132kV | WAVENDON GATE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 40.4752 | 40.3918 | 40.2896 | 40.8916 | 41.3862 | 41.4892 | 41.652 | 41.6805 | 41.3903 | 41.1689 | 40.9092 | 40.6918 | 40.4798 | 40.292 | 39.0917 | 37.7845 | 36.0948
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.7703 | 10.7039 | 10.6466 | 10.5016 | 10.3625 | 10.2091 | 10.0354 | 9.7871 | 9.3479 | 8.7718 | 7.9807 | 7.0743 | 5.9461 | 5.1015 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.7703 | 10.7036 | 10.6454 | 10.5002 | 10.3612 | 10.1927 | 9.9796 | 9.6316 | 9.0637 | 8.2834 | 7.3686 | 6.4403 | 5.3274 | 4.5961 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.7703 | 10.7356 | 10.7207 | 10.706 | 10.683 | 10.6496 | 10.5993 | 10.5031 | 10.3239 | 10.0345 | 9.6522 | 9.2493 | 8.7178 | 8.3432 | 7.9234 | 7.514 | 6.54
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.7703 | 10.6999 | 10.6351 | 10.4816 | 10.3386 | 10.1965 | 10.0586 | 9.9279 | 9.6589 | 9.2981 | 8.6508 | 7.7989 | 6.6588 | 5.9607 | 0 | 0 | 0
East Claydon 132kV | WICKEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.7703 | 10.7221 | 10.6875 | 10.6349 | 10.5745 | 10.4772 | 10.3349 | 10.0809 | 9.6193 | 8.9678 | 8.1988 | 7.4498 | 6.5322 | 5.889 | 4.7973 | 1.5317 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.3503 | 13.2766 | 13.2125 | 13.06 | 12.9148 | 12.6719 | 12.4833 | 11.3673 | 10.8944 | 10.129 | 8.8451 | 7.1894 | 5.0408 | 0.043488 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.3503 | 13.2736 | 13.2083 | 13.0451 | 12.8927 | 12.5941 | 11.3843 | 10.9747 | 9.8596 | 8.3213 | 6.5134 | 4.3746 | 0 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.3503 | 13.3092 | 13.3036 | 13.2958 | 13.2774 | 13.2422 | 13.1821 | 13.0447 | 12.7836 | 12.4598 | 11.2182 | 10.6358 | 9.7861 | 9.1455 | 8.1521 | 6.3885 | 4.3738
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.3503 | 13.2759 | 13.2111 | 13.0473 | 12.8972 | 12.6514 | 12.4702 | 11.3496 | 10.842 | 10.0569 | 8.7535 | 7.0773 | 4.9025 | 0 | 0 | 0 | 0
East Claydon 132kV | WINSLOW 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.3503 | 13.2953 | 13.2632 | 13.2132 | 13.1498 | 13.0362 | 12.8647 | 12.5569 | 11.1932 | 10.1536 | 8.7922 | 7.4249 | 5.7494 | 4.3558 | 0 | 0 | 0
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.1049 | 15.1564 | 15.2656 | 15.2023 | 15.0157 | 14.7994 | 14.5783 | 14.2894 | 13.8522 | 13.3993 | 12.808 | 12.0265 | 11.1216 | 10.4675 | 8.0239 | 5.0764 | 1.9122
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.1049 | 15.1572 | 15.2662 | 15.2163 | 15.0412 | 14.8214 | 14.5742 | 14.2081 | 13.6933 | 13.0964 | 12.4397 | 11.6618 | 10.783 | 10.2182 | 8.1078 | 5.3469 | 2.0782
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.1049 | 15.1553 | 15.2712 | 15.4226 | 15.445 | 15.4554 | 15.4508 | 15.3965 | 15.2661 | 15.047 | 14.7541 | 14.4214 | 13.9702 | 13.675 | 13.364 | 12.849 | 12.1211
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.1049 | 15.1618 | 15.2477 | 15.2199 | 15.0402 | 14.8519 | 14.6518 | 14.4479 | 14.0908 | 13.7329 | 13.194 | 12.4729 | 11.5666 | 10.8412 | 8.0907 | 4.9509 | 2.1624
East Claydon 132kV | WOLVERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.1049 | 15.1819 | 15.3315 | 15.4314 | 15.3879 | 15.2831 | 15.1528 | 14.9264 | 14.5579 | 14.0944 | 13.5751 | 13.0045 | 12.3237 | 11.9095 | 10.7235 | 9.026 | 6.7992
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.3347 | 15.2605 | 15.2303 | 15.112 | 14.9938 | 14.7624 | 14.4965 | 14.1386 | 13.6926 | 13.1919 | 12.5878 | 11.9252 | 11.2049 | 10.6936 | 9.9648 | 6.8269 | 4.1824
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.3347 | 15.2229 | 15.137 | 14.8938 | 14.6612 | 14.3297 | 13.9608 | 13.5013 | 12.9471 | 12.3249 | 11.6142 | 10.8465 | 10.0082 | 9.3807 | 7.9702 | 4.1798 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.3347 | 15.2735 | 15.2575 | 15.24 | 15.2119 | 15.1701 | 15.1158 | 15.0238 | 14.8596 | 14.6173 | 14.2989 | 13.9631 | 13.5317 | 13.2632 | 13.011 | 12.6716 | 13.3457
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.3347 | 15.2182 | 15.1209 | 14.8688 | 14.6325 | 14.339 | 14.0401 | 13.7314 | 13.326 | 12.9142 | 12.3431 | 11.667 | 10.8413 | 10.1196 | 6.7466 | 2.9811 | 0
Enderby 132kV | ALLIANCE AND LEICESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.3347 | 15.2528 | 15.2112 | 15.1296 | 15.0343 | 14.8992 | 14.7386 | 14.4942 | 14.1311 | 13.6919 | 13.1756 | 12.6819 | 12.0994 | 11.7804 | 12.171 | 10.3686 | 8.3753
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 36.1502 | 36.0006 | 35.8227 | 35.3952 | 34.9632 | 34.5079 | 33.9958 | 33.4149 | 32.8475 | 31.6823 | 25.4824 | 18.2918 | 10.015 | 2.2392 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 36.1502 | 36.0014 | 35.8219 | 35.4254 | 35.016 | 34.585 | 34.1238 | 33.6116 | 32.463 | 26.176 | 19.0181 | 11.4103 | 2.8208 | 0 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 36.1502 | 36.0745 | 36.0065 | 35.9301 | 35.8685 | 35.8031 | 35.7362 | 35.6698 | 35.5934 | 35.5179 | 35.4399 | 35.36 | 35.2818 | 34.8351 | 31.2092 | 29.2857 | 20.9827
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 36.1502 | 35.9941 | 35.8001 | 35.3779 | 34.9493 | 34.4991 | 33.986 | 33.4382 | 32.8898 | 32.0164 | 26.305 | 19.3833 | 10.8358 | 2.1551 | 0 | 0 | 0
Enderby 132kV | BARDON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 36.1502 | 36.0517 | 35.9485 | 35.7908 | 35.5974 | 35.3716 | 35.127 | 34.8652 | 34.6022 | 34.3658 | 32.6893 | 27.4868 | 21.2753 | 17.1849 | 3.1733 | 0 | 0
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 37.1727 | 37.0663 | 36.9464 | 36.7103 | 36.4993 | 36.3217 | 36.1509 | 36.08 | 36.0241 | 35.9933 | 35.9572 | 35.9163 | 35.9019 | 35.812 | 32.4158 | 32.7487 | 30.6242
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 37.1727 | 37.068 | 36.9483 | 36.7245 | 36.5162 | 36.3395 | 36.1753 | 36.1161 | 36.0858 | 36.0823 | 36.1193 | 36.1185 | 36.0905 | 35.975 | 32.5926 | 31.2318 | 30.7223
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 37.1727 | 37.1027 | 37.0331 | 36.9641 | 36.8964 | 32.4259 | 32.4299 | 32.4555 | 32.4838 | 32.5152 | 32.5461 | 33.0006 | 35.7699 | 35.7686 | 35.7585 | 35.6449 | 32.8373
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 37.1727 | 37.0624 | 36.9328 | 36.7002 | 36.4914 | 36.3165 | 36.1456 | 36.0868 | 36.0372 | 36.0075 | 35.9819 | 35.9731 | 35.9695 | 35.8677 | 32.422 | 32.7482 | 30.6057
Enderby 132kV | BEAUMONT LEYS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 37.1727 | 37.0886 | 36.9995 | 36.8847 | 36.7675 | 36.6565 | 36.5392 | 36.5539 | 36.5968 | 36.6666 | 36.7978 | 36.9358 | 37.0056 | 36.9721 | 36.5894 | 35.7866 | 36.1288
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.3467 | 20.2076 | 20.0276 | 19.5611 | 19.1019 | 18.6909 | 17.4199 | 16.8569 | 16.6966 | 16.3201 | 15.8185 | 15.217 | 14.6728 | 14.1117 | 11.3703 | 7.5534 | 2.5566
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.3467 | 20.2122 | 20.036 | 19.6065 | 19.1736 | 18.7702 | 18.5055 | 16.9034 | 16.8656 | 16.6555 | 16.3403 | 15.9075 | 15.4929 | 15.016 | 12.2168 | 8.7343 | 4.5536
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.3467 | 20.296 | 20.2409 | 20.185 | 20.1344 | 20.0836 | 20.0327 | 20.115 | 20.2242 | 20.2293 | 20.2325 | 20.2471 | 20.2675 | 20.2911 | 20.4401 | 20.6512 | 20.0547
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.3467 | 20.1992 | 19.9982 | 19.5388 | 19.0849 | 18.6823 | 17.418 | 16.8651 | 16.7245 | 16.3643 | 15.903 | 15.4149 | 14.9073 | 14.3746 | 11.3991 | 7.5525 | 2.5213
Enderby 132kV | BIRSTALL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.3467 | 20.2648 | 20.1648 | 20.0065 | 19.8086 | 19.5802 | 19.3493 | 19.3368 | 19.3454 | 19.1504 | 18.9669 | 18.8216 | 18.6917 | 18.5743 | 16.9339 | 15.7991 | 13.7677
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.0276 | 23.9097 | 23.7889 | 23.4366 | 23.1086 | 22.7136 | 22.387 | 21.9469 | 21.5227 | 21.1893 | 20.8134 | 20.4153 | 20.1488 | 19.9006 | 15.8603 | 13.0863 | 8.7569
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.0276 | 23.8547 | 23.6511 | 23.1407 | 22.6575 | 22.1226 | 21.6463 | 21.0728 | 20.5215 | 20.0723 | 19.7199 | 16.2599 | 16.167 | 15.9466 | 13.34 | 9.5898 | 4.9216
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.0276 | 23.9527 | 23.8822 | 23.7936 | 23.7404 | 23.663 | 23.6391 | 23.5674 | 23.4805 | 23.3952 | 23.3066 | 23.2198 | 23.1408 | 23.0778 | 23.1392 | 23.2308 | 22.4918
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.0276 | 23.844 | 23.6174 | 23.0744 | 22.5714 | 22.0146 | 21.4975 | 20.9044 | 20.2965 | 19.8427 | 16.2477 | 16.1348 | 15.8988 | 15.5743 | 12.6694 | 8.4707 | 2.8425
Enderby 132kV | BRAUNSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.0276 | 23.92 | 23.8072 | 23.6054 | 23.3924 | 23.105 | 22.8762 | 22.5676 | 22.2372 | 21.9568 | 21.6695 | 21.4406 | 21.2579 | 21.1202 | 20.2068 | 16.4287 | 14.9452
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.0341 | 13.0178 | 12.9968 | 13.337 | 13.2572 | 13.049 | 12.8001 | 12.4504 | 11.8438 | 11.1117 | 10.1117 | 8.931 | 7.489 | 2.2647 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.0341 | 12.9965 | 12.9446 | 13.1705 | 13.0188 | 12.6944 | 12.2835 | 11.6998 | 10.8427 | 9.7535 | 8.4923 | 7.1814 | 2.8529 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.0341 | 13.0315 | 13.0299 | 13.3776 | 13.3767 | 13.3597 | 13.3165 | 13.2012 | 12.9591 | 12.5366 | 11.9666 | 11.3474 | 10.5347 | 9.9872 | 9.2285 | 8.1921 | 6.8886
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.0341 | 12.9959 | 12.9379 | 13.2126 | 13.0721 | 12.8294 | 12.5704 | 12.2743 | 11.7395 | 11.1297 | 10.199 | 9.0276 | 7.523 | 2.1796 | 0 | 0 | 0
Enderby 132kV | COALVILLE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.0341 | 13.0186 | 12.9987 | 13.336 | 13.2819 | 13.1824 | 13.0249 | 12.6998 | 12.0926 | 11.2596 | 10.2713 | 9.2946 | 8.1003 | 7.3753 | 3.2095 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 52.8599 | 46.8377 | 43.6218 | 38.4895 | 31.3104 | 20.229 | 7.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 52.8599 | 46.0923 | 41.8666 | 34.7217 | 25.8038 | 12.3795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 52.8599 | 50.2938 | 47.2396 | 48.6566 | 48.0266 | 46.8871 | 44.9142 | 41.2181 | 34.371 | 23.4971 | 9.2225 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 52.8599 | 46.0931 | 41.5005 | 34.4185 | 25.4274 | 13.7188 | 1.0167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | COALVILLE 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 52.8599 | 47.3214 | 46.2324 | 45.434 | 42.077 | 36.8754 | 30.0952 | 19.124 | 0.97664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.2878 | 10.3359 | 10.1181 | 10.0027 | 9.9 | 9.5751 | 9.1374 | 8.5121 | 7.6661 | 6.6627 | 5.4839 | 4.1897 | 2.7344 | 1.6331 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.2878 | 10.2655 | 9.9452 | 9.6099 | 9.3098 | 8.8142 | 8.2029 | 7.4059 | 6.3777 | 5.169 | 3.8114 | 2.3411 | 0.68904 | 0 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.2878 | 10.3345 | 10.3762 | 10.4136 | 10.4372 | 10.4342 | 10.3571 | 10.2007 | 9.9005 | 9.4177 | 8.7856 | 8.1078 | 7.2246 | 6.6708 | 6.0008 | 7.4754 | 5.7942
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.2878 | 10.2703 | 9.9319 | 9.5967 | 9.2961 | 8.8913 | 8.4038 | 7.8877 | 7.1656 | 6.412 | 5.348 | 4.0335 | 2.4019 | 0.87107 | 0 | 0 | 0
Enderby 132kV | DESFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.2878 | 10.3234 | 10.3495 | 10.2837 | 10.2124 | 10.0436 | 9.7713 | 9.3165 | 8.5839 | 7.644 | 6.5602 | 5.4732 | 4.1792 | 3.4391 | 0.88721 | 0 | 0
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1946 | 20.058 | 19.9021 | 19.496 | 19.119 | 18.7493 | 18.3994 | 18.0662 | 17.4925 | 17.3493 | 17.0257 | 16.522 | 16.1313 | 15.7978 | 12.6803 | 8.9983 | 4.0072
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1946 | 20.0409 | 19.8578 | 19.4163 | 18.9906 | 18.5919 | 18.213 | 17.5367 | 17.3303 | 17.1299 | 16.8322 | 16.4145 | 16.0945 | 15.8035 | 13.289 | 9.3028 | 4.7657
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1946 | 20.1327 | 20.0726 | 20.0143 | 19.9441 | 19.8731 | 19.7999 | 19.7335 | 19.6681 | 19.6204 | 19.5812 | 19.5556 | 19.5424 | 19.5413 | 19.7971 | 20.0514 | 19.3903
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1946 | 20.0285 | 19.8202 | 19.3536 | 18.9224 | 18.5051 | 18.1062 | 17.4875 | 17.2435 | 17.0021 | 16.6175 | 16.1608 | 15.7239 | 15.3307 | 11.5254 | 7.4151 | 1.928
Enderby 132kV | GROBY ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1946 | 20.0938 | 19.9813 | 19.8136 | 19.6219 | 19.4122 | 19.2055 | 19.0167 | 18.8487 | 18.7235 | 18.574 | 18.4383 | 18.3502 | 18.3199 | 17.4752 | 15.6568 | 13.4046
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.726 | 21.4813 | 21.3636 | 21.1072 | 20.891 | 20.6674 | 20.3719 | 20.0263 | 19.6426 | 19.2804 | 18.8651 | 18.3815 | 16.8938 | 16.7825 | 14.4507 | 13.0321 | 11.2368
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.726 | 21.4849 | 21.3704 | 21.1376 | 20.9337 | 20.7099 | 20.4475 | 20.1468 | 19.8264 | 19.5183 | 19.1932 | 18.8082 | 18.3882 | 17.9339 | 15.1454 | 13.7547 | 12.2651
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.726 | 21.6734 | 21.4557 | 21.38 | 21.3437 | 21.3218 | 21.2802 | 21.2328 | 21.1827 | 21.1255 | 21.0638 | 20.9967 | 20.9235 | 20.8402 | 20.5448 | 20.549 | 20.2595
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.726 | 21.4782 | 21.3521 | 21.0979 | 20.8829 | 20.661 | 20.3644 | 20.0342 | 19.6592 | 19.298 | 18.8948 | 18.4495 | 17.9514 | 16.8167 | 14.4609 | 13.0399 | 11.2393
Enderby 132kV | HAMILTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.726 | 21.5072 | 21.4301 | 21.3154 | 21.2147 | 21.099 | 20.9572 | 20.7976 | 20.6176 | 20.4491 | 20.2711 | 20.0891 | 19.8739 | 19.6481 | 18.1747 | 16.9012 | 16.407
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.6322 | 19.5777 | 19.5137 | 19.4042 | 19.3017 | 19.2114 | 19.1397 | 19.1963 | 19.1368 | 19.0893 | 19.047 | 19.0049 | 18.9759 | 18.9524 | 20.7925 | 19.6396 | 12.8634
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.6322 | 19.578 | 19.5147 | 19.4068 | 19.3043 | 19.2167 | 19.1443 | 19.2034 | 19.1478 | 19.1017 | 19.0611 | 19.0206 | 18.9938 | 18.969 | 16.7215 | 19.8486 | 18.8532
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.6322 | 19.5859 | 19.5405 | 19.4954 | 19.4504 | 19.4063 | 19.3664 | 19.4335 | 19.4153 | 19.4 | 19.3887 | 19.3811 | 19.3792 | 19.3855 | 19.3475 | 19.3328 | 19.1141
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.6322 | 19.5755 | 19.5063 | 19.3983 | 19.2965 | 19.2069 | 19.1334 | 19.1941 | 19.1351 | 19.0869 | 19.0488 | 19.019 | 18.9909 | 18.9635 | 20.7694 | 19.6239 | 12.8542
Enderby 132kV | HIGHFIELDS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.6322 | 19.5856 | 19.532 | 19.4686 | 19.4008 | 19.336 | 19.2755 | 19.3884 | 19.3323 | 19.2821 | 19.2379 | 19.2147 | 19.1991 | 19.1913 | 19.1017 | 21.3305 | 20.5767
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 26.3255 | 26.2483 | 26.1675 | 25.8073 | 25.4499 | 24.9862 | 24.4999 | 23.8893 | 23.1942 | 22.409 | 21.5067 | 20.4926 | 19.473 | 18.5929 | 26.2407 | 20.1543 | 25.1613
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 26.3255 | 26.1509 | 25.9311 | 25.2596 | 24.6177 | 23.9138 | 23.1757 | 22.3176 | 21.3656 | 20.29 | 19.1376 | 17.876 | 16.5763 | 15.4211 | 21.4471 | 13.7947 | 17.5618
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 26.3255 | 26.2768 | 26.2445 | 26.2044 | 26.1402 | 26.0558 | 25.9461 | 25.7802 | 25.5001 | 25.075 | 24.5493 | 24.0105 | 23.3394 | 22.9371 | 22.5527 | 21.8453 | 20.0861
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 26.3255 | 26.139 | 25.8894 | 25.1973 | 24.5474 | 23.8637 | 23.1626 | 22.4624 | 21.66 | 20.8145 | 19.784 | 30.2326 | 28.8966 | 27.5366 | 20.8826 | 0 | 0
Enderby 132kV | HINCKLEY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 26.3255 | 26.2326 | 26.1373 | 25.9203 | 25.6698 | 25.3427 | 24.9741 | 24.4874 | 23.8141 | 22.9624 | 22.0206 | 21.1229 | 20.1034 | 19.5258 | 29.0315 | 13.6257 | 9.1304
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 37.8578 | 37.7636 | 37.6527 | 37.4003 | 37.1388 | 36.9123 | 36.7259 | 36.4461 | 36.1082 | 35.8317 | 35.5422 | 35.2275 | 34.9961 | 34.7789 | 33.228 | 30.7387 | 27.4496
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 37.8578 | 37.7169 | 37.5383 | 37.143 | 36.7476 | 36.405 | 36.1067 | 35.7258 | 35.2776 | 34.8767 | 34.4911 | 34.0677 | 33.7073 | 33.3727 | 30.9171 | 27.9879 | 24.3073
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 37.8578 | 37.7918 | 37.7177 | 37.6403 | 37.5556 | 37.5283 | 37.549 | 37.516 | 37.4513 | 37.3897 | 37.3289 | 37.2757 | 37.2311 | 37.2 | 37.1896 | 37.1931 | 36.5331
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 37.8578 | 37.71 | 37.5136 | 37.093 | 36.6803 | 36.3453 | 36.0084 | 35.5997 | 35.1045 | 34.6443 | 34.185 | 33.7509 | 33.3221 | 32.942 | 30.2829 | 26.9489 | 22.526
Enderby 132kV | Hockley Farm Road 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 37.8578 | 37.7643 | 37.6489 | 37.483 | 37.288 | 37.1264 | 37.023 | 36.8618 | 36.6276 | 36.4268 | 36.2413 | 36.0867 | 35.946 | 35.8541 | 35.0695 | 33.6251 | 31.5012
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.7661 | 19.2683 | 19.2456 | 19.2161 | 19.1868 | 19.158 | 19.1295 | 19.101 | 19.0728 | 19.0423 | 19.011 | 18.3247 | 10.033 | 2.2432 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.7661 | 19.2683 | 19.2456 | 19.2161 | 19.1868 | 19.1581 | 19.1285 | 19.1 | 19.0721 | 19.0436 | 19.0153 | 11.4308 | 2.8259 | 0 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.7661 | 19.3536 | 19.2502 | 19.2314 | 19.2121 | 19.1922 | 19.1725 | 19.152 | 19.1316 | 19.1114 | 19.0918 | 19.0723 | 19.0519 | 19.0317 | 18.938 | 18.8392 | 18.751
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.7661 | 19.2683 | 19.2456 | 19.2165 | 19.1876 | 19.1588 | 19.1302 | 19.1017 | 19.0735 | 19.043 | 19.012 | 18.9804 | 10.8553 | 2.159 | 0 | 0 | 0
Enderby 132kV | INTERLINK PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.7661 | 19.2691 | 19.2486 | 19.2268 | 19.2045 | 19.1807 | 19.1572 | 19.1328 | 19.1089 | 19.0834 | 19.0578 | 19.0327 | 19.0077 | 17.2158 | 3.179 | 0 | 0
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 38.6524 | 38.5619 | 38.4843 | 38.2217 | 37.9778 | 37.7295 | 37.5032 | 37.2469 | 37.0168 | 36.8183 | 36.6142 | 36.3867 | 36.2089 | 36.0494 | 33.3584 | 31.4488 | 28.6583
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 38.6524 | 38.5634 | 38.4865 | 38.2393 | 38.0037 | 37.7685 | 37.553 | 37.3199 | 37.1093 | 36.9304 | 36.7617 | 36.5604 | 36.4034 | 36.2498 | 33.617 | 32.0758 | 29.7552
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 38.6524 | 38.6035 | 38.581 | 38.536 | 38.4863 | 38.4302 | 38.3796 | 38.3259 | 38.2669 | 38.2142 | 38.1688 | 38.1333 | 38.1069 | 38.0899 | 38.1196 | 38.1251 | 37.7175
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 38.6524 | 38.5571 | 38.4657 | 38.2075 | 37.9666 | 37.7211 | 37.493 | 37.2579 | 37.0347 | 36.8372 | 36.65 | 36.4732 | 36.3013 | 36.135 | 33.3639 | 31.445 | 28.6416
Enderby 132kV | JUPITER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 38.6524 | 38.5857 | 38.5468 | 38.441 | 38.3279 | 38.1953 | 38.0765 | 37.9488 | 37.8233 | 37.715 | 37.6208 | 37.5395 | 37.4739 | 37.4283 | 37.0096 | 36.1483 | 33.7524
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 39.8063 | 39.6351 | 39.4222 | 38.9305 | 38.4601 | 37.9802 | 37.5143 | 37.0652 | 36.6435 | 36.246 | 35.8722 | 35.4771 | 35.1748 | 34.9054 | 29.4504 | 26.7066 | 21.8156
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 39.8063 | 39.6355 | 39.4216 | 38.9552 | 38.5018 | 38.0442 | 37.5987 | 37.1752 | 36.7857 | 36.4315 | 36.1054 | 35.7011 | 35.3769 | 35.0667 | 29.7013 | 27.6321 | 23.5568
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 39.8063 | 39.7035 | 39.6018 | 39.4951 | 39.3905 | 39.2781 | 39.1764 | 39.0658 | 38.9362 | 38.8158 | 38.7064 | 38.6126 | 38.5341 | 38.4733 | 38.4479 | 38.4376 | 38.0388
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 39.8063 | 39.627 | 39.3927 | 38.9071 | 38.4402 | 37.9632 | 37.4918 | 37.0787 | 36.6747 | 36.2787 | 35.9305 | 35.6121 | 35.3214 | 35.0469 | 29.4568 | 26.7059 | 21.7927
Enderby 132kV | LEICESTER 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 39.8063 | 39.6755 | 39.5318 | 39.326 | 39.0981 | 38.838 | 38.5854 | 38.3394 | 38.0857 | 37.8451 | 37.6215 | 37.4259 | 37.2596 | 37.1166 | 36.9218 | 35.3782 | 34.1003
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 151.2022 | 148.1562 | 144.5396 | 136.0397 | 128.7795 | 113.2488 | 108.2048 | 98.8446 | 89.0223 | 79.9532 | 69.9672 | 58.5709 | 50.3966 | 42.3376 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 151.2022 | 147.8311 | 143.7182 | 134.5966 | 127.3259 | 111.2457 | 104.2698 | 94.0057 | 83.6849 | 73.9996 | 64.186 | 52.7113 | 43.6844 | 34.5474 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 151.2022 | 149.1905 | 147.2802 | 145.0253 | 143.1636 | 141.2066 | 140.5383 | 138.6067 | 136.2671 | 133.9615 | 131.7369 | 129.626 | 127.6927 | 126.1161 | 124.4072 | 123.3974 | 108.9628
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 151.2022 | 147.6577 | 143.1432 | 133.6949 | 126.814 | 110.0059 | 102.3234 | 91.7389 | 80.231 | 69.1573 | 57.6229 | 46.3965 | 37.4574 | 27.6307 | 0 | 0 | 0
Enderby 132kV | LEICESTER 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 151.2022 | 148.7574 | 146.0983 | 141.9304 | 137.4932 | 132.4093 | 128.9898 | 125.2152 | 113.3919 | 108.7467 | 103.4405 | 98.6591 | 94.7342 | 91.4493 | 73.8382 | 38.6977 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 137.7912 | 133.5762 | 128.5721 | 110.3105 | 101.5122 | 89.4973 | 77.1816 | 64.8273 | 51.4053 | 37.692 | 7.4831 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 137.7912 | 133.4427 | 128.1971 | 110.2286 | 101.2821 | 89.3796 | 77.1224 | 65.3041 | 52.6397 | 39.8587 | 26.8933 | 5.7147 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 137.7912 | 136.2296 | 133.527 | 131.6214 | 129.6209 | 127.4735 | 125.3727 | 124.0929 | 122.2851 | 108.4317 | 107.2194 | 105.5548 | 103.3383 | 101.7861 | 100.8722 | 98.5381 | 80.33
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 137.7912 | 133.1725 | 127.2839 | 109.4621 | 99.5301 | 87.2018 | 74.5502 | 63.4762 | 50.8589 | 38.0047 | 10.5541 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | LEICESTER EAST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 137.7912 | 134.7109 | 131.4901 | 126.6037 | 121.0788 | 108.8917 | 104.4078 | 99.8235 | 93.4122 | 86.0651 | 78.678 | 72.0706 | 64.8483 | 59.7093 | 23.682 | 0 | 0
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 22.4199 | 22.327 | 22.188 | 21.8337 | 21.487 | 21.1484 | 20.8333 | 20.5055 | 20.2115 | 19.9171 | 19.6047 | 19.2607 | 19.0189 | 18.8186 | 15.9506 | 12.7685 | 9.0036
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 22.4199 | 22.3285 | 22.1884 | 21.8491 | 21.5101 | 21.1851 | 20.8706 | 20.5609 | 20.2859 | 20.0413 | 19.8095 | 19.4839 | 19.2372 | 18.9981 | 16.5271 | 13.4491 | 10.1999
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 22.4199 | 22.3696 | 22.3205 | 22.2705 | 22.204 | 22.138 | 22.0703 | 21.995 | 21.9029 | 21.8233 | 21.7492 | 21.6882 | 21.6371 | 21.5973 | 21.6406 | 21.6481 | 21.1574
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 22.4199 | 22.3197 | 22.1625 | 21.8102 | 21.4612 | 21.1213 | 20.7986 | 20.4964 | 20.2132 | 19.9184 | 19.6301 | 19.3604 | 19.1255 | 18.899 | 15.9256 | 12.7336 | 8.9606
Enderby 132kV | LEICESTER EAST 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 22.4199 | 22.3493 | 22.2615 | 22.1262 | 21.966 | 21.7913 | 21.6212 | 21.4487 | 21.2743 | 21.1003 | 20.9421 | 20.8074 | 20.7011 | 20.6083 | 19.9459 | 18.741 | 16.4313
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.5321 | 20.4451 | 20.3364 | 20.0711 | 19.8233 | 19.6536 | 19.5157 | 19.3171 | 19.1605 | 19.0586 | 18.9877 | 16.91 | 16.854 | 16.749 | 15.401 | 12.9455 | 9.7143
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.5321 | 20.4451 | 20.3356 | 20.084 | 19.8426 | 19.6654 | 19.526 | 19.3385 | 19.1914 | 19.0908 | 19.0207 | 18.9664 | 16.9207 | 16.8835 | 15.8935 | 13.9903 | 11.2827
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.5321 | 20.4917 | 20.4512 | 20.4078 | 20.3612 | 20.3631 | 20.375 | 20.3355 | 20.2875 | 20.2477 | 20.2164 | 20.1922 | 20.1819 | 20.1806 | 20.2961 | 20.3947 | 20.0197
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.5321 | 20.4399 | 20.3185 | 20.0575 | 19.8125 | 19.6458 | 19.5068 | 19.3268 | 19.1764 | 19.0705 | 18.9998 | 16.9245 | 16.905 | 16.8364 | 15.4159 | 12.9477 | 9.7
Enderby 132kV | LEICESTER NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.5321 | 20.4758 | 20.4078 | 20.3049 | 20.1851 | 20.1038 | 20.0512 | 19.934 | 19.8247 | 19.7316 | 19.6495 | 19.5905 | 19.55 | 19.5284 | 19.2345 | 16.9925 | 16.0579
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 116.0089 | 113.0103 | 109.2657 | 92.5755 | 88.169 | 81.2059 | 73.3647 | 66.2685 | 59.3777 | 52.6383 | 44.5503 | 34.788 | 27.2187 | 19.0333 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 116.0089 | 112.8444 | 108.7985 | 92.5109 | 87.4982 | 80.0689 | 72.1714 | 65.318 | 59.1155 | 52.846 | 46.6258 | 38.5341 | 31.7028 | 24.0934 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 116.0089 | 114.4913 | 112.9277 | 111.3098 | 109.673 | 91.3442 | 90.7472 | 90.3949 | 90.0712 | 89.64 | 89.3416 | 89.214 | 89.2313 | 89.1611 | 88.8432 | 105.007 | 81.45
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 116.0089 | 112.6077 | 108.0845 | 92.2536 | 86.2665 | 78.5313 | 69.8511 | 62.808 | 55.5785 | 48.0795 | 39.8082 | 31.6562 | 23.8062 | 15.1595 | 0 | 0 | 0
Enderby 132kV | LEICESTER NORTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 116.0089 | 113.8489 | 111.3167 | 107.5404 | 103.126 | 91.8923 | 90.1652 | 88.507 | 86.7772 | 84.4399 | 82.2935 | 80.6585 | 79.0512 | 77.4439 | 63.3731 | 25.2547 | 0
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 22.244 | 22.1842 | 22.093 | 21.8873 | 21.6736 | 21.4906 | 21.2874 | 21.1223 | 20.9879 | 20.882 | 20.8098 | 18.7883 | 18.7763 | 18.7467 | 18.8323 | 15.1808 | 13.0921
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 22.244 | 22.1855 | 22.0932 | 21.8977 | 21.6925 | 21.5006 | 21.3074 | 21.1463 | 21.0164 | 20.91 | 20.8323 | 20.7853 | 18.7944 | 18.7768 | 18.2662 | 17.741 | 16.0151
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 22.244 | 22.201 | 22.1554 | 22.1032 | 22.0584 | 22.0385 | 22.0171 | 21.9621 | 21.9 | 21.8399 | 21.7861 | 21.7335 | 21.6844 | 21.6408 | 21.5304 | 21.4289 | 21.118
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 22.244 | 22.1808 | 22.0805 | 21.8743 | 21.6573 | 21.4723 | 21.265 | 21.1084 | 20.9765 | 20.8731 | 20.8078 | 18.7898 | 18.7852 | 18.7641 | 18.8217 | 15.1401 | 13.0549
Enderby 132kV | LERO 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 22.244 | 22.1937 | 22.1321 | 22.0408 | 21.9315 | 21.8306 | 21.7273 | 21.6172 | 21.5061 | 21.3889 | 21.2804 | 21.2073 | 21.1442 | 21.0959 | 20.8706 | 18.6442 | 17.8662
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 38.2676 | 38.1799 | 38.0553 | 37.8235 | 37.586 | 37.3374 | 37.2353 | 36.8578 | 36.4373 | 36.0427 | 35.5886 | 35.0592 | 34.806 | 34.5848 | 33.6147 | 30.1244 | 29.5372
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 38.2676 | 38.1788 | 38.0543 | 37.8226 | 37.5804 | 37.3311 | 37.2041 | 36.8482 | 36.4955 | 36.1391 | 35.7557 | 35.3233 | 35.0549 | 34.7886 | 33.5612 | 30.0889 | 29.4931
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 38.2676 | 38.1976 | 38.1197 | 38.0268 | 37.9599 | 37.8977 | 37.9517 | 37.9023 | 37.8326 | 37.749 | 37.6596 | 37.5551 | 37.441 | 37.3434 | 37.1214 | 36.9025 | 36.5497
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 38.2676 | 38.1776 | 38.0474 | 37.8158 | 37.5771 | 37.3248 | 37.2153 | 36.841 | 36.4149 | 36.0096 | 35.5537 | 35.041 | 34.7931 | 34.5759 | 33.5849 | 30.1208 | 29.5316
Enderby 132kV | MANSFIELD ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 38.2676 | 38.206 | 38.1155 | 37.9937 | 37.8528 | 37.7017 | 37.6857 | 37.4777 | 37.2585 | 37.0346 | 36.7894 | 36.5543 | 36.389 | 36.2322 | 35.4039 | 34.6555 | 33.9037
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.8812 | 11.4883 | 11.3011 | 10.7939 | 10.2968 | 9.7266 | 9.1662 | 8.546 | 7.802 | 7.0466 | 6.0392 | 4.8022 | 3.4155 | 2.0872 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.8812 | 11.4717 | 11.2803 | 10.7969 | 10.318 | 9.7315 | 9.1062 | 8.3561 | 7.4226 | 6.3776 | 5.2255 | 3.9672 | 2.6177 | 0 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.8812 | 11.8483 | 11.439 | 11.3875 | 11.3174 | 11.2349 | 11.1408 | 11.0146 | 10.8143 | 10.5384 | 10.2047 | 9.8634 | 9.442 | 9.1353 | 8.7483 | 8.0578 | 6.6425
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.8812 | 11.4799 | 11.271 | 10.77 | 10.2768 | 9.7103 | 9.1454 | 8.567 | 7.8473 | 7.0917 | 6.1219 | 5.0001 | 3.6493 | 2.2125 | 0 | 0 | 0
Enderby 132kV | MANTLE LANE COALVILLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.8812 | 11.5212 | 11.4151 | 11.2392 | 11.0272 | 10.7688 | 10.4871 | 10.1105 | 9.5555 | 8.89 | 8.154 | 7.4452 | 6.641 | 6.0413 | 3.2578 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.2764 | 2.2135 | 2.2282 | 2.1205 | 2.0334 | 1.8261 | 1.5956 | 1.2769 | 0.80184 | 0.22986 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.2764 | 2.2052 | 2.2061 | 2.0769 | 1.9666 | 1.71 | 1.4028 | 0.97729 | 0.3724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.2764 | 2.2424 | 2.2758 | 2.3061 | 2.3307 | 2.3409 | 2.3314 | 2.2655 | 2.1129 | 1.8448 | 1.4533 | 1.037 | 0.49337 | 0.13971 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.2764 | 2.2023 | 2.1935 | 2.0684 | 1.9622 | 1.7795 | 1.5804 | 1.354 | 0.97729 | 0.55117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | NAILSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.2764 | 2.2276 | 2.2617 | 2.2473 | 2.238 | 2.1713 | 2.0745 | 1.8591 | 1.4532 | 0.89853 | 0.1928 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.5618 | 2.4538 | 2.4674 | 2.406 | 2.3337 | 2.1465 | 1.9207 | 1.5727 | 1.0132 | 0.29906 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.5618 | 2.4188 | 2.3834 | 2.2155 | 2.0464 | 1.7748 | 1.4623 | 1.0281 | 0.3787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.5618 | 2.5635 | 2.4729 | 2.4939 | 2.4975 | 2.4836 | 2.4525 | 2.3667 | 2.1834 | 1.8733 | 1.4621 | 1.0271 | 0.44465 | 0.0591 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.5618 | 2.4179 | 2.3781 | 2.2139 | 2.048 | 1.8162 | 1.5839 | 1.3313 | 0.90572 | 0.43179 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | OSBASTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.5618 | 2.448 | 2.4539 | 2.4253 | 2.3742 | 2.2704 | 2.1314 | 1.8671 | 1.3705 | 0.69523 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 40.205 | 40.0927 | 39.9383 | 39.6234 | 39.338 | 39.0489 | 38.8419 | 38.5485 | 38.2722 | 37.9981 | 37.6973 | 37.3637 | 37.0776 | 36.7967 | 35.0949 | 33.5114 | 28.9192
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 40.205 | 40.0943 | 39.9412 | 39.6385 | 39.361 | 39.072 | 38.8591 | 38.5724 | 38.3136 | 38.0631 | 37.8202 | 37.5044 | 37.2149 | 36.9273 | 35.4087 | 33.606 | 29.4292
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 40.205 | 40.1187 | 40.0302 | 39.9349 | 39.8606 | 39.7878 | 39.7745 | 39.6853 | 39.5833 | 39.4832 | 39.3889 | 39.302 | 39.2244 | 39.1552 | 38.943 | 38.6489 | 38.0921
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 40.205 | 40.0885 | 39.9229 | 39.6101 | 39.3252 | 39.0354 | 38.8224 | 38.5451 | 38.2714 | 37.9929 | 37.7052 | 37.4251 | 37.1542 | 36.8828 | 35.1293 | 33.5172 | 28.9424
Enderby 132kV | REDCROSS STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 40.205 | 40.1106 | 39.9981 | 39.8466 | 39.7012 | 39.5287 | 39.4384 | 39.2578 | 39.0764 | 38.8888 | 38.7058 | 38.5437 | 38.3925 | 38.2565 | 37.467 | 36.2343 | 34.95
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 23.1803 | 23.0413 | 22.8622 | 22.4131 | 21.9861 | 21.5681 | 21.1888 | 20.8061 | 20.4805 | 20.218 | 19.9853 | 19.8081 | 16.0828 | 16.0325 | 14.0165 | 9.8473 | 4.4602
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 23.1803 | 23.0426 | 22.8623 | 22.4375 | 22.0233 | 21.6266 | 21.2566 | 20.8985 | 20.5899 | 20.3491 | 20.1428 | 19.9236 | 19.8036 | 19.743 | 14.8309 | 11.0744 | 6.5358
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 23.1803 | 23.1112 | 23.0419 | 22.9723 | 22.8878 | 22.7972 | 22.7085 | 22.6186 | 22.5137 | 22.4238 | 22.3449 | 22.2804 | 22.2325 | 22.2014 | 22.2613 | 22.3239 | 21.6549
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 23.1803 | 23.0325 | 22.8306 | 22.3857 | 21.9585 | 21.5427 | 21.1584 | 20.8079 | 20.4964 | 20.2337 | 20.0159 | 19.8579 | 19.7667 | 16.085 | 14.0051 | 9.8091 | 4.3954
Enderby 132kV | SALUTATION 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 23.1803 | 23.0824 | 22.9688 | 22.7964 | 22.5981 | 22.378 | 22.1665 | 21.9588 | 21.751 | 21.5684 | 21.4083 | 21.2782 | 21.1779 | 21.1075 | 20.4655 | 16.2454 | 15.0022
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 19.2498 | 19.0863 | 18.888 | 18.3565 | 17.8598 | 17.3646 | 16.9125 | 16.4379 | 16.0318 | 15.7584 | 13.3297 | 13.2408 | 13.0479 | 12.7847 | 10.3813 | 6.5232 | 1.3612
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 19.2498 | 19.0857 | 18.884 | 18.3832 | 17.9061 | 17.4369 | 17.007 | 16.5673 | 16.1872 | 15.8885 | 15.6992 | 13.3388 | 13.277 | 13.1288 | 11.0676 | 7.6429 | 3.2975
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 19.2498 | 19.1869 | 19.1265 | 19.0618 | 18.9891 | 18.9166 | 18.8415 | 18.7753 | 18.7004 | 18.6357 | 18.5858 | 18.5562 | 18.5513 | 18.5671 | 18.9073 | 19.061 | 18.3911
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 19.2498 | 19.0744 | 18.8475 | 18.3168 | 17.8214 | 17.3262 | 16.8651 | 16.4373 | 16.0496 | 15.7665 | 13.354 | 13.2984 | 13.1567 | 12.9284 | 10.292 | 6.3651 | 1.1032
Enderby 132kV | STONEYGATE 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 19.2498 | 19.1465 | 19.0297 | 18.8414 | 18.623 | 18.3744 | 18.1391 | 17.9078 | 17.6864 | 17.4906 | 17.3182 | 17.1788 | 17.0661 | 16.9891 | 16.2841 | 13.4537 | 11.9534
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.5402 | 16.5518 | 16.5302 | 16.4397 | 16.3245 | 16.1614 | 16.022 | 15.9265 | 15.8442 | 15.7743 | 13.8424 | 13.7213 | 13.5836 | 13.428 | 11.838 | 9.361 | 6.3606
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.5402 | 16.5511 | 16.5298 | 16.4445 | 16.3357 | 16.1854 | 16.0518 | 15.9726 | 15.9237 | 15.905 | 15.9252 | 15.8778 | 15.7712 | 15.637 | 13.2142 | 10.8952 | 8.3323
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.5402 | 16.5573 | 16.5587 | 16.5648 | 16.5675 | 16.5608 | 16.5652 | 16.5846 | 16.6055 | 16.6336 | 16.6674 | 16.7018 | 16.7282 | 16.7485 | 19.2213 | 19.1521 | 16.8572
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.5402 | 16.5507 | 16.5249 | 16.4336 | 16.3178 | 16.1559 | 16.0153 | 15.9365 | 15.865 | 15.7977 | 13.89 | 13.8303 | 13.7103 | 13.5646 | 11.8531 | 9.3666 | 6.3517
Enderby 132kV | THURMASTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.5402 | 16.5571 | 16.5502 | 16.5352 | 16.5117 | 16.4611 | 16.4265 | 16.436 | 16.4573 | 16.4867 | 16.5401 | 16.592 | 16.6019 | 16.6134 | 15.527 | 14.4864 | 13.1623
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.6636 | 13.6542 | 13.6248 | 13.4238 | 13.1355 | 12.669 | 12.1091 | 11.3576 | 10.5404 | 9.5186 | 8.3221 | 7.0255 | 5.7011 | 4.5901 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.6636 | 13.6472 | 13.5973 | 13.33 | 12.958 | 12.414 | 11.7761 | 10.9528 | 10.0549 | 8.9377 | 7.6949 | 6.371 | 5.0295 | 3.9042 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.6636 | 13.67 | 13.6743 | 13.6765 | 13.6741 | 13.6644 | 13.6429 | 13.593 | 13.5103 | 13.299 | 12.9743 | 12.5981 | 12.0943 | 11.7622 | 11.5079 | 11.0621 | 9.6369
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.6636 | 13.6446 | 13.5821 | 13.2846 | 12.8872 | 12.3593 | 11.7591 | 11.0893 | 10.3477 | 9.4939 | 8.3949 | 7.162 | 5.7833 | 4.4666 | 0 | 0 | 0
Enderby 132kV | THURNBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.6636 | 13.6623 | 13.6511 | 13.6016 | 13.5104 | 13.3517 | 13.1286 | 12.7711 | 12.3106 | 11.6093 | 10.7965 | 10.0179 | 9.1369 | 8.5833 | 6.6873 | 2.9764 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.5806 | 20.5015 | 20.4423 | 20.2899 | 20.1554 | 19.964 | 19.7654 | 19.5089 | 19.2582 | 19.035 | 16.8473 | 16.656 | 16.2637 | 15.9602 | 15.4837 | 13.1393 | 5.5751
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.5806 | 20.4531 | 20.3237 | 20.0309 | 19.7775 | 19.5032 | 19.2549 | 19.0378 | 16.816 | 16.5965 | 16.1776 | 15.6164 | 14.9498 | 14.461 | 13.1389 | 9.9648 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.5806 | 20.5474 | 20.473 | 20.4504 | 12.2518 | 12.206 | 12.1443 | 12.044 | 11.8759 | 11.6304 | 11.3197 | 11.0009 | 10.5872 | 10.3467 | 10.2517 | 10.8702 | 10.0008
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.5806 | 20.4483 | 20.3041 | 19.999 | 19.7389 | 19.4787 | 19.2521 | 19.0815 | 18.9807 | 16.7956 | 16.5557 | 16.1202 | 15.4734 | 14.8776 | 12.8386 | 9.2682 | 0
Enderby 132kV | WHETSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.5806 | 20.4922 | 20.4204 | 20.3197 | 20.2191 | 20.054 | 19.87 | 19.632 | 19.3548 | 19.0739 | 16.8559 | 16.7187 | 16.361 | 16.1264 | 16.1166 | 14.4863 | 12.2175
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 52.2599 | 52.1356 | 51.9878 | 51.5865 | 51.2774 | 50.8601 | 50.4759 | 50.0674 | 49.7123 | 49.4362 | 49.1391 | 48.5621 | 48.3427 | 48.0467 | 45.7317 | 41.1127 | 35.8232
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 52.2599 | 52.0828 | 51.856 | 51.2928 | 50.8349 | 50.2963 | 49.7898 | 49.2757 | 48.8904 | 48.3209 | 47.9294 | 47.4102 | 47.0163 | 46.6009 | 43.4683 | 38.1635 | 32.5389
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 52.2599 | 52.1917 | 52.1244 | 52.0546 | 52.0361 | 51.9462 | 51.8537 | 51.767 | 51.6647 | 51.5848 | 51.5217 | 51.4771 | 51.4578 | 51.4563 | 51.7286 | 51.9614 | 51.1416
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 52.2599 | 52.0691 | 51.8158 | 51.22 | 50.7423 | 50.1706 | 49.6268 | 49.1212 | 48.5185 | 48.0834 | 47.6103 | 47.1372 | 46.6829 | 46.1838 | 40.9568 | 35.7163 | 28.9615
Enderby 132kV | WIGSTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 52.2599 | 52.1448 | 52.0131 | 51.8018 | 51.6493 | 51.3711 | 51.1067 | 50.8507 | 50.5976 | 50.3796 | 50.1899 | 50.0336 | 49.9239 | 49.86 | 49.0787 | 46.2836 | 43.4595
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 67.8845 | 65.8313 | 64.3676 | 55.9451 | 50.4191 | 42.7549 | 36.0187 | 26.6325 | 16.6118 | 4.8722 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 67.8845 | 65.4012 | 63.4767 | 53.5103 | 46.1632 | 37.2826 | 29.3133 | 18.8126 | 7.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 67.8845 | 66.9708 | 66.4567 | 65.997 | 25.6441 | 24.4336 | 23.843 | 21.9532 | 18.9118 | 14.7971 | 9.7531 | 1.8088 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 67.8845 | 65.2839 | 63.1661 | 52.667 | 45.063 | 36.374 | 29.123 | 20.7959 | 11.5384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 67.8845 | 66.2958 | 65.3904 | 63.3403 | 57.2166 | 54.1494 | 50.8966 | 45.3527 | 38.3698 | 30.2933 | 21.4958 | 13.2743 | 0.37118 | 0 | 0 | 0 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 43.1689 | 42.9049 | 42.6827 | 41.8088 | 40.9368 | 40.0004 | 39.3309 | 38.5309 | 38.002 | 31.7239 | 31.33 | 30.4621 | 29.44 | 28.4648 | 22.2959 | 13.4343 | 2.7265
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 43.1689 | 42.8961 | 42.655 | 41.7572 | 40.8675 | 39.9355 | 39.2607 | 38.4801 | 37.9816 | 31.7116 | 31.3138 | 30.5 | 29.5351 | 28.6181 | 22.5041 | 13.8778 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 43.1689 | 43.0849 | 43.08 | 43.0345 | 42.9212 | 42.7737 | 42.7674 | 42.5951 | 42.3442 | 42.0437 | 41.706 | 41.3883 | 41.0259 | 40.8242 | 40.914 | 40.776 | 39.1975
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 43.1689 | 42.8792 | 42.583 | 41.6505 | 40.7435 | 39.8107 | 39.1794 | 38.5024 | 38.0161 | 31.7371 | 31.4493 | 30.7813 | 29.8091 | 28.743 | 21.3284 | 11.7588 | 0
Enderby 132kV | WIGSTON MAGNA 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 43.1689 | 43.0208 | 42.9546 | 42.6691 | 42.2748 | 41.7829 | 41.4879 | 40.9549 | 40.3699 | 39.7823 | 39.2173 | 38.7458 | 38.3197 | 38.1139 | 31.9109 | 29.4101 | 24.5463
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.061 | 11.0258 | 10.9822 | 10.863 | 10.7453 | 10.537 | 10.306 | 10.028 | 9.5433 | 8.9877 | 8.1174 | 6.999 | 5.6209 | 2.2862 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.061 | 11.0246 | 10.979 | 10.864 | 10.7473 | 10.4879 | 10.1497 | 9.6646 | 8.8727 | 7.8508 | 6.6621 | 5.4392 | 2.88 | 0 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.061 | 11.0482 | 11.0355 | 11.0225 | 11.0032 | 10.9749 | 10.9313 | 10.8446 | 10.6742 | 10.3815 | 9.9824 | 9.5481 | 9.0009 | 8.6016 | 7.9648 | 7.9953 | 6.7626
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.061 | 11.0238 | 10.9748 | 10.8569 | 10.7405 | 10.5338 | 10.3025 | 10.0375 | 9.5617 | 9.0084 | 8.1487 | 7.0605 | 5.6911 | 2.2003 | 0 | 0 | 0
Enderby 132kV | WORTHINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.061 | 11.0387 | 11.0127 | 10.9721 | 10.9234 | 10.843 | 10.721 | 10.4766 | 9.9612 | 9.2437 | 8.3908 | 7.5459 | 6.5378 | 5.7989 | 3.2399 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.237 | 22.1275 | 22.0184 | 21.7088 | 21.3884 | 21.0861 | 20.812 | 20.5116 | 20.2512 | 20.0454 | 19.8315 | 19.5616 | 19.39 | 19.2226 | 16.8138 | 15.1268 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.237 | 22.126 | 21.992 | 21.682 | 21.361 | 21.0605 | 20.7835 | 20.5006 | 20.2634 | 20.0655 | 19.8835 | 19.6247 | 19.4399 | 19.25 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.237 | 22.1823 | 22.1498 | 22.1306 | 22.0705 | 22.0108 | 21.9516 | 21.8988 | 21.8394 | 21.7929 | 21.7596 | 21.7437 | 21.7453 | 21.7627 | 22.1124 | 22.3741 | 21.9386
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.237 | 22.1167 | 21.9671 | 21.648 | 21.3233 | 21.0089 | 20.7134 | 20.4428 | 20.1957 | 19.9635 | 19.7409 | 19.5359 | 19.3373 | 19.1259 | 0 | 0 | 0
Grendon 132kV | ABINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.237 | 22.1551 | 22.0657 | 21.9611 | 21.8075 | 21.6437 | 21.4902 | 21.3457 | 21.2049 | 21.0791 | 20.9793 | 20.9053 | 20.8599 | 20.8492 | 20.5051 | 19.3032 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.8316 | 16.7325 | 16.6663 | 16.4836 | 16.2821 | 16.0559 | 15.8228 | 15.5286 | 15.2119 | 14.8913 | 14.521 | 14.0933 | 13.7353 | 13.4192 | 11.8941 | 9.8943 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.8316 | 16.7319 | 16.664 | 16.4809 | 16.2794 | 16.0501 | 15.803 | 15.4766 | 15.0836 | 14.6469 | 14.1668 | 13.6354 | 13.1417 | 12.7613 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.8316 | 16.82 | 16.7496 | 16.7352 | 16.7162 | 16.6922 | 16.6663 | 16.621 | 16.5546 | 16.4609 | 16.3433 | 16.2184 | 16.0703 | 15.9642 | 15.9283 | 15.7978 | 15.2793
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.8316 | 16.729 | 16.6537 | 16.4585 | 16.247 | 16.0111 | 15.7614 | 15.4775 | 15.1218 | 14.76 | 14.2999 | 13.7722 | 13.2623 | 12.804 | 0 | 0 | 0
Grendon 132kV | BANBURY LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.8316 | 16.7531 | 16.7167 | 16.6585 | 16.58 | 16.4745 | 16.3544 | 16.1838 | 15.9564 | 15.6876 | 15.3817 | 15.0836 | 14.7819 | 14.562 | 13.7868 | 11.7578 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 35.9862 | 35.5007 | 35.3802 | 35 | 34.5707 | 34.1459 | 33.7401 | 33.3889 | 33.1825 | 30.6572 | 30.1332 | 29.9188 | 29.6275 | 29.2725 | 26.6752 | 22.9388 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 35.9862 | 35.4994 | 35.3749 | 34.9945 | 34.5655 | 34.1194 | 33.6887 | 33.3391 | 33.1658 | 30.1732 | 30.08 | 29.7994 | 29.4244 | 28.9803 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 35.9862 | 35.6479 | 35.5717 | 35.5571 | 35.5411 | 35.5065 | 35.4699 | 35.4342 | 35.3815 | 35.3362 | 35.2917 | 35.2569 | 35.2161 | 35.1767 | 35.2002 | 35.2114 | 34.4403
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 35.9862 | 35.5035 | 35.375 | 34.9918 | 34.5625 | 34.1185 | 33.6678 | 33.3274 | 33.1611 | 30.1535 | 29.9799 | 29.6333 | 29.2004 | 28.6839 | 0 | 0 | 0
Grendon 132kV | BOOTHVILLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 35.9862 | 35.56 | 35.5232 | 35.4324 | 35.2567 | 35.0504 | 34.8242 | 34.6007 | 34.3708 | 34.178 | 33.9941 | 33.8331 | 33.6708 | 33.5373 | 33.014 | 25.5175 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.6365 | 17.6096 | 17.1749 | 17.0095 | 16.912 | 16.7472 | 16.5288 | 16.2377 | 15.8566 | 15.3498 | 14.7151 | 14.0242 | 13.2113 | 12.5651 | 10.4148 | 7.6055 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.6365 | 17.6047 | 17.1645 | 17.0037 | 16.9053 | 16.6015 | 16.1755 | 15.6017 | 14.72 | 13.6071 | 12.3238 | 10.977 | 9.4022 | 8.1041 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.6365 | 17.6287 | 17.6536 | 17.2443 | 17.2794 | 17.2783 | 17.2144 | 17.0941 | 16.8659 | 16.496 | 16.0134 | 15.5011 | 14.8473 | 14.3733 | 13.5794 | 12.2494 | 10.7103
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.6365 | 17.6132 | 17.169 | 17.0145 | 16.9159 | 16.6932 | 16.3848 | 16.0508 | 15.4892 | 14.849 | 13.8769 | 12.6573 | 11.1102 | 9.6032 | 0 | 0 | 0
Grendon 132kV | BRACKMILLS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.6365 | 17.6286 | 17.2262 | 17.1947 | 17.204 | 17.1139 | 16.9327 | 16.6056 | 15.9759 | 15.1341 | 14.1511 | 13.1841 | 12.0187 | 11.1724 | 8.7437 | 5.2693 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.4545 | 7.4339 | 7.4237 | 7.3887 | 7.3434 | 7.2806 | 7.1992 | 7.058 | 6.8343 | 6.4821 | 6.0067 | 5.4734 | 4.8085 | 4.3431 | 2.4308 | 0.98613 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.4545 | 7.4272 | 7.4045 | 7.3321 | 7.2438 | 7.0393 | 6.7528 | 6.3315 | 5.6974 | 4.882 | 3.9357 | 2.9529 | 1.7995 | 0.91174 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.4545 | 7.4544 | 7.433 | 7.4292 | 7.4218 | 7.4063 | 7.3775 | 7.3073 | 7.1492 | 6.8495 | 6.4244 | 5.9538 | 5.337 | 4.9246 | 4.3255 | 3.4884 | 2.511
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.4545 | 7.4271 | 7.4033 | 7.3305 | 7.2455 | 7.0879 | 6.9032 | 6.6855 | 6.3056 | 5.8613 | 5.1753 | 4.3078 | 3.1948 | 2.1633 | 0 | 0 | 0
Grendon 132kV | BRUNTINGTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.4545 | 7.4335 | 7.424 | 7.4038 | 7.3747 | 7.3181 | 7.2175 | 6.9941 | 6.5501 | 5.9171 | 5.1568 | 4.4031 | 3.4854 | 2.9119 | 1.0409 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.3518 | 13.3021 | 13.2483 | 13.1304 | 13.0193 | 12.9116 | 12.8086 | 12.7035 | 12.6053 | 12.5436 | 11.371 | 11.2072 | 10.9386 | 10.6978 | 9.8749 | 8.6056 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.3518 | 13.3017 | 13.247 | 13.1291 | 13.0182 | 12.9036 | 12.7828 | 12.6495 | 12.5478 | 11.2849 | 10.945 | 10.5 | 9.9503 | 9.5568 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.3518 | 13.327 | 13.3054 | 13.2833 | 13.2559 | 13.2239 | 13.1853 | 13.133 | 13.0486 | 12.9268 | 12.7811 | 12.6466 | 12.5371 | 11.4236 | 11.3813 | 11.1081 | 10.5978
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.3518 | 13.3006 | 13.2416 | 13.1174 | 13.0048 | 12.8985 | 12.8017 | 12.7233 | 12.6121 | 12.5449 | 11.3376 | 11.0325 | 10.5053 | 9.997 | 0 | 0 | 0
Grendon 132kV | BUGBROOKE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.3518 | 13.3162 | 13.28 | 13.2293 | 13.1729 | 13.0996 | 13.0104 | 12.8908 | 12.708 | 12.5548 | 11.3532 | 11.1175 | 10.7272 | 10.4242 | 9.6486 | 8.3894 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0078 | 15.0774 | 15.0947 | 14.9551 | 14.8792 | 14.5929 | 14.338 | 11.4326 | 7.1634 | 2.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0078 | 15.0638 | 15.0884 | 14.948 | 14.8726 | 14.5005 | 13.1757 | 7.3262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0078 | 15.0908 | 15.1535 | 15.2222 | 15.3058 | 15.2706 | 15.2343 | 15.1656 | 15.0337 | 14.8284 | 14.56 | 14.277 | 12.202 | 9.1761 | 4.998 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0078 | 15.0774 | 15.0947 | 14.9551 | 14.8792 | 14.5371 | 13.8421 | 9.6073 | 3.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | BURTON LATIMER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0078 | 15.0975 | 15.1686 | 15.1848 | 15.2369 | 15.0836 | 14.9283 | 14.6808 | 14.276 | 9.2591 | 2.134 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 37.4721 | 37.3551 | 37.2272 | 36.9562 | 36.6618 | 36.4133 | 36.163 | 35.8868 | 35.6174 | 35.3759 | 35.1923 | 34.9038 | 34.6832 | 34.4616 | 33.0384 | 29.7335 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 37.4721 | 37.3541 | 37.2226 | 36.9505 | 36.6535 | 36.4024 | 36.1325 | 35.8711 | 35.6293 | 35.4085 | 35.262 | 34.9319 | 34.6481 | 34.3553 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 37.4721 | 37.4024 | 37.3606 | 37.341 | 37.2889 | 37.2628 | 37.2087 | 37.1559 | 37.0702 | 36.9924 | 36.964 | 36.9113 | 36.8672 | 36.8331 | 36.8916 | 36.7675 | 36.2159
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 37.4721 | 37.3567 | 37.2234 | 36.9558 | 36.6638 | 36.4195 | 36.1503 | 35.9012 | 35.6396 | 35.3581 | 35.1557 | 34.8732 | 34.5912 | 34.2921 | 0 | 0 | 0
Grendon 132kV | CAMPBELL STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 37.4721 | 37.3757 | 37.2885 | 37.2013 | 37.0633 | 36.9375 | 36.7936 | 36.6533 | 36.4847 | 36.309 | 36.2099 | 36.0756 | 35.9559 | 35.8566 | 35.0549 | 25.4219 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 36.3349 | 36.0466 | 35.7063 | 34.6815 | 33.965 | 33.1021 | 31.8764 | 30.5217 | 28.9077 | 27.1949 | 25.2057 | 23.1275 | 20.7577 | 18.7869 | 13.4174 | 1.7945 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 36.3349 | 36.004 | 35.6364 | 34.5226 | 33.682 | 32.2403 | 30.4169 | 28.2084 | 25.5551 | 22.5638 | 19.2405 | 15.5885 | 11.5566 | 8.542 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 36.3349 | 36.2077 | 36.149 | 36.0952 | 36.2036 | 36.2225 | 35.979 | 35.6366 | 35.0436 | 34.1433 | 33.0078 | 31.8348 | 30.3617 | 29.3832 | 32.0031 | 30.1751 | 26.4695
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 36.3349 | 36.0006 | 35.5914 | 34.4411 | 33.5894 | 32.4058 | 30.8522 | 29.2439 | 27.1946 | 25.1391 | 22.3597 | 19.0929 | 15.1598 | 11.6979 | 0 | 0 | 0
Grendon 132kV | CANNON STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 36.3349 | 36.1469 | 36.0042 | 35.6696 | 35.5081 | 35.012 | 34.2068 | 33.1153 | 31.5317 | 29.6113 | 27.4625 | 25.3869 | 22.9566 | 21.3462 | 19.4308 | 10.8701 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.8692 | 11.7274 | 11.6716 | 11.3658 | 10.978 | 9.2035 | 8.7624 | 8.2381 | 7.6823 | 7.074 | 6.325 | 5.5072 | 4.6321 | 3.9072 | 1.4729 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.8692 | 11.7264 | 11.6675 | 11.3569 | 10.964 | 10.3802 | 9.7545 | 8.9809 | 7.9645 | 6.7805 | 5.4399 | 4.011 | 3.9331 | 2.5724 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.8692 | 11.7978 | 11.8313 | 11.8463 | 11.8205 | 10.4627 | 10.4331 | 10.3239 | 10.1244 | 9.8024 | 9.3801 | 8.9395 | 8.3928 | 7.9886 | 7.4004 | 8.0213 | 6.637
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.8692 | 11.7196 | 11.6451 | 11.3266 | 10.9236 | 10.3731 | 9.7984 | 9.2098 | 8.5532 | 7.8051 | 6.7207 | 5.4383 | 3.9112 | 2.4022 | 0 | 0 | 0
Grendon 132kV | CHAPEL BRAMPTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.8692 | 11.7752 | 11.7884 | 11.7108 | 11.5269 | 11.2595 | 10.9846 | 10.5632 | 9.8898 | 9.0495 | 8.073 | 7.1206 | 7.516 | 6.652 | 4.3098 | 0.78625 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 27.7199 | 27.7303 | 27.8938 | 28.1381 | 28.4213 | 28.6687 | 28.8912 | 29.0663 | 29.33 | 29.5633 | 29.6119 | 29.5305 | 29.4463 | 29.3577 | 28.9428 | 25.1889 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 27.7199 | 27.7221 | 27.8875 | 28.0833 | 28.3448 | 28.4903 | 28.6719 | 28.8391 | 29.1623 | 29.4596 | 29.6075 | 29.5583 | 29.5016 | 29.422 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 27.7199 | 27.7039 | 27.8221 | 28.0386 | 28.2589 | 28.4547 | 28.6497 | 28.7966 | 29.0194 | 29.2549 | 29.4215 | 29.5364 | 29.6458 | 29.7313 | 29.5949 | 29.1737 | 28.8135
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 27.7199 | 27.7303 | 27.8938 | 28.1381 | 28.4213 | 28.6687 | 28.8912 | 29.0714 | 29.3462 | 29.5764 | 29.6119 | 29.5173 | 29.419 | 29.3162 | 0 | 0 | 0
Grendon 132kV | CORBY CENTRAL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 27.7199 | 27.7242 | 27.8981 | 28.1226 | 28.4097 | 28.5778 | 28.7887 | 28.974 | 29.3089 | 29.6101 | 29.7611 | 29.7487 | 29.7324 | 29.695 | 29.1888 | 14.1127 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 34.8369 | 34.6563 | 34.4774 | 34.1344 | 33.8941 | 33.9663 | 33.845 | 33.6101 | 33.373 | 30.5799 | 30.5343 | 30.4824 | 30.3339 | 29.988 | 27.9288 | 24.0902 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 34.8369 | 34.661 | 34.4952 | 34.1701 | 33.9322 | 33.7918 | 33.5919 | 33.3664 | 30.4666 | 30.0694 | 29.6119 | 28.9573 | 27.882 | 26.7728 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 34.8369 | 34.7758 | 34.6305 | 34.5393 | 34.5334 | 34.8031 | 34.993 | 35.0553 | 35.0678 | 35.0737 | 35.0607 | 35.0734 | 35.0387 | 35.0161 | 35.4576 | 34.4343 | 33.1921
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 34.8369 | 34.6563 | 34.4774 | 34.1344 | 33.8941 | 33.9128 | 33.7433 | 33.5115 | 33.3231 | 30.5 | 30.2605 | 29.722 | 28.8897 | 27.7441 | 0 | 0 | 0
Grendon 132kV | CORBY No2 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 34.8369 | 34.6956 | 34.5915 | 34.4364 | 34.3439 | 34.4443 | 34.487 | 34.3617 | 34.059 | 33.8075 | 33.6588 | 33.5149 | 33.284 | 30.5522 | 29.1389 | 14.1245 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 110.7679 | 110.6416 | 110.5219 | 109.9907 | 109.5824 | 109.1517 | 108.5991 | 108.0013 | 107.2272 | 106.3873 | 105.455 | 104.299 | 102.9604 | 101.7318 | 96.3579 | 25.2309 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 110.7679 | 110.6359 | 110.55 | 110.0152 | 109.6017 | 108.8453 | 107.9784 | 106.9187 | 105.4576 | 103.7619 | 101.9652 | 96.2094 | 76.99 | 61.9205 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 110.7679 | 110.7749 | 110.7705 | 110.8242 | 110.8981 | 111.1677 | 111.2432 | 111.2737 | 111.2502 | 110.7325 | 110.4312 | 109.9949 | 109.3661 | 108.9511 | 108.5759 | 94.8292 | 77.2592
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 110.7679 | 110.6409 | 110.52 | 109.9866 | 109.5763 | 109.0182 | 108.3352 | 107.6626 | 106.6316 | 105.5577 | 104.0078 | 101.8947 | 87.6864 | 70.2788 | 0 | 0 | 0
Grendon 132kV | CORBY No2 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 110.7679 | 110.7169 | 110.7577 | 110.6638 | 110.6397 | 110.4429 | 110.204 | 109.8313 | 109.1005 | 108.1599 | 107.1286 | 105.8729 | 101.6653 | 91.5842 | 66.2676 | 14.1362 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.1764 | 9.0422 | 9.0285 | 8.99 | 8.9485 | 8.8162 | 8.5341 | 8.1806 | 7.7313 | 7.1312 | 6.394 | 5.6035 | 4.6604 | 3.8973 | 1.4952 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.1764 | 9.0409 | 9.0153 | 8.9764 | 8.9362 | 8.6192 | 8.0558 | 7.2959 | 6.155 | 4.7239 | 3.0816 | 1.366 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.1764 | 9.0528 | 9.0492 | 9.0465 | 9.041 | 9.0284 | 9.0087 | 8.9645 | 8.8764 | 8.7277 | 8.1895 | 7.602 | 6.8572 | 6.3177 | 5.5922 | 4.2886 | 2.5979
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.1764 | 9.0416 | 9.0161 | 8.9752 | 8.9336 | 8.6839 | 8.2751 | 7.8255 | 7.1005 | 6.2865 | 5.0603 | 3.5347 | 1.5867 | 0 | 0 | 0 | 0
Grendon 132kV | DENTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.1764 | 9.0482 | 9.0312 | 9.0181 | 8.9991 | 8.9633 | 8.9062 | 8.7219 | 7.9724 | 6.9776 | 5.8165 | 4.6804 | 3.3114 | 2.3052 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.3651 | 5.2916 | 5.2779 | 5.0586 | 4.9299 | 4.6311 | 4.3107 | 3.8872 | 3.2794 | 2.4622 | 1.4515 | 0.36325 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.3651 | 5.2847 | 5.2671 | 5.0255 | 4.8743 | 4.3106 | 3.6316 | 2.6791 | 1.1546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.3651 | 5.36 | 5.4213 | 5.503 | 5.6112 | 5.5937 | 5.5452 | 5.3966 | 5.0629 | 4.503 | 3.7607 | 2.969 | 1.9608 | 1.2255 | 0.15216 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.3651 | 5.2886 | 5.2697 | 5.0425 | 4.9065 | 4.4508 | 3.9651 | 3.4118 | 2.4406 | 1.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | DESBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.3651 | 5.33 | 5.381 | 5.3803 | 5.4341 | 5.2641 | 5.0173 | 4.528 | 3.5031 | 2.1306 | 0.52592 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.8839 | 9.67 | 9.5569 | 9.2904 | 9.0313 | 8.7589 | 8.4787 | 8.1275 | 7.6811 | 7.0849 | 6.3525 | 5.5671 | 4.6302 | 3.8719 | 1.4855 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.8839 | 9.6717 | 9.5558 | 9.2902 | 9.0287 | 8.5633 | 8.0035 | 7.2485 | 6.115 | 4.6932 | 3.0616 | 1.3572 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.8839 | 9.7304 | 9.7043 | 9.6807 | 9.6431 | 9.5899 | 9.5145 | 9.3744 | 9.1129 | 8.6886 | 8.1363 | 7.5527 | 6.8127 | 6.2767 | 5.5559 | 4.2607 | 2.5811
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.8839 | 9.6692 | 9.5437 | 9.2745 | 9.0151 | 8.6275 | 8.2214 | 7.7747 | 7.0544 | 6.2457 | 5.0274 | 3.5118 | 1.5764 | 0 | 0 | 0 | 0
Grendon 132kV | EARLS BARTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.8839 | 9.7071 | 9.642 | 9.5488 | 9.4353 | 9.2727 | 9.056 | 8.6653 | 7.9206 | 6.9323 | 5.7787 | 4.65 | 3.2899 | 2.2902 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.0572 | 22.9997 | 22.9282 | 22.8209 | 22.7508 | 22.6784 | 22.6032 | 22.5521 | 22.4691 | 22.3514 | 22.1962 | 22.0207 | 21.8053 | 21.6396 | 21.1187 | 20.2893 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.0572 | 22.9994 | 22.9286 | 22.8215 | 22.7408 | 22.5883 | 22.4016 | 22.2087 | 21.9337 | 21.5898 | 21.209 | 20.799 | 20.3238 | 20.0038 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.0572 | 23.0081 | 22.9572 | 22.9043 | 22.8705 | 22.8337 | 22.7927 | 22.7562 | 22.6924 | 22.592 | 22.4628 | 22.3309 | 22.1623 | 22.053 | 21.9114 | 21.3975 | 20.8476
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.0572 | 22.9997 | 22.9282 | 22.8209 | 22.7508 | 22.6392 | 22.5212 | 22.4335 | 22.277 | 22.0877 | 21.7822 | 21.3913 | 20.9094 | 20.5093 | 0 | 0 | 0
Grendon 132kV | EARLSTREES 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.0572 | 23.0042 | 22.945 | 22.8778 | 22.8298 | 22.7705 | 22.698 | 22.6193 | 22.4629 | 22.2515 | 22.0157 | 21.7815 | 21.4769 | 21.2482 | 20.5415 | 14.0892 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.9384 | 23.3633 | 23.905 | 23.9103 | 24.0652 | 24.1433 | 24.3157 | 24.4403 | 24.6835 | 24.5309 | 24.2751 | 23.949 | 23.719 | 23.4657 | 21.16 | 16.3645 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.9384 | 23.3617 | 23.8989 | 23.9037 | 24.0586 | 24.1407 | 24.3149 | 24.4532 | 24.713 | 24.5577 | 24.3342 | 24.0326 | 23.8038 | 23.5426 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.9384 | 23.3203 | 23.7771 | 24.1761 | 24.5963 | 25.0915 | 25.5545 | 25.9471 | 26.3914 | 26.644 | 26.8704 | 27.1006 | 27.3261 | 27.5231 | 27.7116 | 27.601 | 26.6623
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.9384 | 23.3829 | 23.864 | 23.9449 | 24.1257 | 24.4278 | 24.6551 | 24.8378 | 24.9976 | 24.7853 | 24.4666 | 24.1012 | 23.7318 | 23.3338 | 0 | 0 | 0
Grendon 132kV | ELLESMERE AVENUE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.9384 | 23.4227 | 24.0459 | 24.3483 | 24.7581 | 25.0568 | 25.4335 | 25.8023 | 26.2615 | 26.2794 | 26.2326 | 26.2058 | 26.2067 | 26.2149 | 25.4608 | 23.5757 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.451 | 18.4204 | 18.4226 | 18.4 | 18.3828 | 18.3418 | 18.3048 | 18.3675 | 18.4727 | 18.5891 | 18.6111 | 18.6184 | 18.8312 | 18.798 | 18.4839 | 18.1632 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.451 | 18.3977 | 18.3688 | 18.2725 | 18.1835 | 18.0456 | 17.0748 | 17.071 | 17.0675 | 17.0618 | 17.0138 | 16.9243 | 16.8011 | 16.613 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.451 | 18.4175 | 18.4075 | 18.3953 | 18.3813 | 18.3501 | 18.3205 | 18.3489 | 18.396 | 18.452 | 18.4679 | 18.4842 | 18.5022 | 18.5042 | 18.3973 | 18.2836 | 17.8376
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.451 | 18.3961 | 18.362 | 18.266 | 18.1773 | 18.0392 | 17.0714 | 17.0616 | 17.0443 | 17.017 | 16.9233 | 16.7846 | 16.6197 | 16.4044 | 0 | 0 | 0
Grendon 132kV | EMPINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.451 | 18.4083 | 18.3966 | 18.3618 | 18.3256 | 18.2501 | 18.1624 | 18.1724 | 18.2089 | 18.251 | 18.1989 | 18.1416 | 18.0753 | 17.1388 | 16.9962 | 14.2611 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.5439 | 12.5354 | 12.5258 | 12.473 | 12.4281 | 12.3877 | 12.3623 | 11.5994 | 11.4464 | 11.1034 | 10.6013 | 10.0307 | 9.3119 | 8.996 | 7.9712 | 6.309 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.5439 | 12.5203 | 12.4861 | 12.4031 | 11.6129 | 11.5225 | 11.266 | 10.8424 | 10.1336 | 9.2243 | 8.1718 | 7.0732 | 5.7852 | 4.709 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.5439 | 12.5335 | 12.5234 | 12.512 | 12.4992 | 12.4733 | 12.4349 | 12.3764 | 11.612 | 11.3675 | 10.9015 | 10.3684 | 9.6708 | 9.2005 | 8.5066 | 7.4421 | 6.1874
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.5439 | 12.5192 | 12.4807 | 12.3984 | 11.6125 | 11.5385 | 11.367 | 11.1409 | 10.7326 | 10.2339 | 9.4613 | 8.4882 | 7.2373 | 5.9976 | 0 | 0 | 0
Grendon 132kV | EXTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.5439 | 12.5286 | 12.5107 | 12.4778 | 12.435 | 12.3838 | 11.619 | 11.4817 | 10.9812 | 10.22 | 9.305 | 8.3969 | 7.2938 | 6.5949 | 4.8451 | 2.2324 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.2088 | 10.2069 | 10.18 | 10.0221 | 9.8525 | 9.6435 | 9.4288 | 9.1467 | 8.8448 | 8.4704 | 8.024 | 7.517 | 6.9797 | 6.5898 | 2.978 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.2088 | 10.1614 | 10.0675 | 9.7744 | 9.4785 | 9.1023 | 8.6878 | 8.1734 | 7.6139 | 6.9685 | 6.2864 | 3.6928 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.2088 | 10.214 | 10.2099 | 10.2132 | 10.2088 | 10.1956 | 10.1582 | 10.0783 | 9.9304 | 9.6901 | 9.3877 | 9.0746 | 8.6772 | 8.4357 | 8.1861 | 7.8654 | 6.3259
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.2088 | 10.1609 | 10.0553 | 9.7522 | 9.454 | 9.113 | 8.7372 | 8.3375 | 7.8327 | 7.3405 | 6.7512 | 6.0855 | 3.6941 | 0.18422 | 0 | 0 | 0
Grendon 132kV | FARNDON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.2088 | 10.2035 | 10.1771 | 10.101 | 9.9991 | 9.8394 | 9.6475 | 9.3683 | 9.011 | 8.5479 | 8.0448 | 7.5649 | 7.012 | 5.8332 | 0.23913 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 48.0263 | 47.836 | 47.6046 | 46.8403 | 46.1759 | 45.5032 | 44.8333 | 44.1326 | 43.4098 | 42.6895 | 41.9067 | 41.2789 | 35.1466 | 34.9292 | 16.9798 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 48.0263 | 47.8337 | 47.6396 | 46.8892 | 46.2246 | 45.4222 | 44.6281 | 43.7165 | 42.725 | 41.7991 | 35.2982 | 34.8367 | 33.9738 | 26.9493 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 48.0263 | 48.0154 | 47.9556 | 47.9447 | 47.9285 | 47.8938 | 47.8354 | 47.7077 | 47.504 | 47.2406 | 46.8704 | 46.5046 | 46.0767 | 45.7814 | 45.4677 | 44.7353 | 43.3239
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 48.0263 | 47.836 | 47.6046 | 46.8403 | 46.1759 | 45.4374 | 44.7008 | 43.9535 | 43.1134 | 42.3183 | 41.4325 | 35.1022 | 34.5525 | 26.5975 | 0 | 0 | 0
Grendon 132kV | FIELD STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 48.0263 | 47.9221 | 47.8689 | 47.6464 | 47.4285 | 47.0922 | 46.755 | 46.3101 | 45.6872 | 44.9692 | 44.0968 | 43.306 | 42.4862 | 41.9294 | 35.2902 | 14.2798 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.6744 | 17.6685 | 17.6599 | 17.6312 | 17.6043 | 17.5658 | 17.5162 | 17.4233 | 17.299 | 16.8198 | 16.453 | 16.0222 | 15.4705 | 15.0909 | 13.389 | 1.7907 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.6744 | 17.6544 | 17.6267 | 17.5621 | 17.5018 | 17.3341 | 16.885 | 16.5395 | 15.9609 | 15.2026 | 14.3186 | 13.4022 | 11.5321 | 8.5239 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.6744 | 17.6676 | 17.6611 | 17.6543 | 17.645 | 17.6248 | 17.5893 | 17.5098 | 17.3663 | 16.9093 | 16.5871 | 16.1819 | 15.6452 | 15.2865 | 14.7655 | 14.0573 | 13.2961
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.6744 | 17.6548 | 17.6266 | 17.5633 | 17.5057 | 17.3825 | 17.2928 | 16.884 | 16.594 | 16.2013 | 15.5745 | 14.7724 | 13.7337 | 11.6732 | 0 | 0 | 0
Grendon 132kV | HARROLD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.6744 | 17.6625 | 17.6481 | 17.625 | 17.5989 | 17.5443 | 17.4567 | 17.3051 | 16.7486 | 16.2243 | 15.5811 | 14.9395 | 14.1544 | 13.6533 | 12.4391 | 10.7876 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 37.7254 | 37.9294 | 38.1017 | 37.8952 | 37.7587 | 37.2181 | 36.6161 | 35.9565 | 35.4076 | 33.4195 | 33.0546 | 32.5411 | 31.9173 | 31.3 | 27.6336 | 22.3699 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 37.7254 | 37.9048 | 38.1106 | 37.8808 | 37.7464 | 37.1404 | 36.4708 | 35.6875 | 33.4866 | 33.0101 | 32.2475 | 31.2519 | 30.1741 | 29.2411 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 37.7254 | 37.9689 | 38.1596 | 38.3562 | 38.5809 | 38.5455 | 38.4902 | 38.4089 | 38.2798 | 38.0938 | 37.8504 | 37.6058 | 37.3032 | 37.0689 | 36.823 | 36.4657 | 35.1263
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 37.7254 | 37.9277 | 38.0972 | 37.8851 | 37.7437 | 37.1476 | 36.4871 | 35.7878 | 33.5282 | 33.2275 | 32.6066 | 31.7467 | 30.6815 | 29.6244 | 0 | 0 | 0
Grendon 132kV | HAZELWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 37.7254 | 37.9626 | 38.2568 | 38.3436 | 38.4948 | 38.2249 | 37.9162 | 37.5128 | 36.9757 | 36.4008 | 35.8138 | 35.3712 | 33.5181 | 33.3331 | 32.0394 | 14.1186 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.6285 | 11.5972 | 11.5531 | 11.5151 | 11.4173 | 11.3112 | 11.1722 | 10.9669 | 10.6794 | 10.287 | 9.7791 | 9.2113 | 8.5457 | 8.0636 | 6.4879 | 4.5793 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.6285 | 11.5455 | 11.4276 | 11.2405 | 10.9882 | 10.6495 | 10.2454 | 9.7214 | 8.9589 | 8.0329 | 6.9814 | 5.8902 | 4.6355 | 3.5382 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.6285 | 11.5905 | 11.5505 | 11.5797 | 11.547 | 11.5121 | 11.4354 | 11.3041 | 11.068 | 10.6987 | 10.2235 | 9.7197 | 9.0791 | 8.6371 | 7.9289 | 6.9365 | 5.7863
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.6285 | 11.5426 | 11.4177 | 11.2301 | 10.9724 | 10.6699 | 10.3366 | 9.9848 | 9.4476 | 8.8763 | 8.0589 | 7.0593 | 5.7903 | 4.5024 | 0 | 0 | 0
Grendon 132kV | HOLWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.6285 | 11.5779 | 11.5115 | 11.4883 | 11.3804 | 11.2305 | 11.0167 | 10.6746 | 10.0785 | 9.2984 | 8.3928 | 7.51 | 6.4425 | 5.7295 | 3.7316 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.7936 | 14.5161 | 13.8907 | 12.2852 | 10.8236 | 9.1447 | 7.5116 | 5.672 | 3.5539 | 0.99716 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.7936 | 14.5194 | 13.9646 | 12.4121 | 10.9851 | 8.826 | 6.5368 | 3.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.7936 | 14.7853 | 14.6628 | 14.5425 | 14.4269 | 14.1807 | 13.927 | 13.4587 | 12.665 | 11.3931 | 9.7934 | 8.1235 | 6.0537 | 4.5524 | 2.4796 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.7936 | 14.5145 | 13.8873 | 12.2788 | 10.8134 | 8.8264 | 6.8674 | 4.7664 | 1.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.7936 | 14.7256 | 14.4644 | 13.9541 | 13.4145 | 12.5092 | 11.549 | 10.0897 | 7.7178 | 4.5936 | 1.0587 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 14.8127 | 14.5349 | 13.9087 | 12.3011 | 10.8376 | 9.1566 | 7.5213 | 5.6793 | 3.5585 | 0.99846 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 14.8127 | 14.5382 | 13.9827 | 12.4282 | 10.9994 | 8.8374 | 6.5452 | 3.6394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 14.8127 | 14.8045 | 14.6818 | 14.5613 | 14.4455 | 14.1991 | 13.945 | 13.4761 | 12.6814 | 11.4079 | 9.8061 | 8.134 | 6.0615 | 4.5583 | 2.4828 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 14.8127 | 14.5333 | 13.9053 | 12.2947 | 10.8274 | 8.8379 | 6.8763 | 4.7725 | 1.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | IRTHLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 14.8127 | 14.7447 | 14.4831 | 13.9722 | 13.4318 | 12.5254 | 11.564 | 10.1027 | 7.7277 | 4.5996 | 1.0601 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 96.8684 | 96.5714 | 96.3618 | 95.0958 | 93.9883 | 92.1221 | 90.7414 | 89.0903 | 87.1294 | 84.7751 | 81.8135 | 78.634 | 74.9722 | 71.708 | 55.6826 | 29.7732 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 96.8684 | 96.5467 | 96.3772 | 95.0534 | 93.8825 | 91.8526 | 89.6553 | 86.7772 | 82.881 | 78.2371 | 72.4021 | 65.6297 | 58.7066 | 52.5363 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 96.8684 | 96.9337 | 97.0026 | 97.2119 | 97.4055 | 96.9494 | 96.9277 | 96.6301 | 95.9734 | 94.8648 | 93.3005 | 91.6515 | 89.5554 | 88.0797 | 86.1806 | 82.9508 | 76.5259
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 96.8684 | 96.5554 | 96.3157 | 95.0017 | 93.8495 | 92.1223 | 90.3379 | 88.3843 | 85.6266 | 82.6472 | 78.2472 | 72.6254 | 65.0651 | 57.7979 | 0 | 0 | 0
Grendon 132kV | KETTERING 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 96.8684 | 96.7445 | 96.8829 | 96.6773 | 96.4793 | 95.8009 | 95.0497 | 93.7395 | 91.4363 | 88.425 | 84.7589 | 81.1757 | 77.4843 | 73.9154 | 62.9302 | 16.6812 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.7606 | 19.8545 | 19.9909 | 20.0471 | 20.1067 | 20.162 | 20.2222 | 20.2384 | 20.2427 | 20.1931 | 20.043 | 19.856 | 19.6275 | 19.4397 | 18.6867 | 17.3764 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.7606 | 19.8489 | 19.9986 | 20.0342 | 20.0927 | 20.0941 | 20.1251 | 20.0924 | 20.0325 | 19.8886 | 19.6295 | 19.3287 | 18.99 | 18.7889 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.7606 | 19.8387 | 19.9584 | 20.0705 | 20.1687 | 20.2622 | 20.3639 | 20.4179 | 20.4709 | 20.4914 | 20.4545 | 20.4027 | 20.3097 | 20.2519 | 20.1219 | 19.8662 | 19.4627
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.7606 | 19.8545 | 19.9909 | 20.0471 | 20.1067 | 20.1651 | 20.2331 | 20.2721 | 20.2656 | 20.2157 | 20.0059 | 19.7056 | 19.3181 | 19.0225 | 0 | 0 | 0
Grendon 132kV | KETTERING NORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.7606 | 19.8578 | 20.0222 | 20.115 | 20.2203 | 20.2647 | 20.3419 | 20.3671 | 20.3757 | 20.312 | 20.1444 | 19.9576 | 19.7321 | 19.5727 | 19.0768 | 16.6566 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.9218 | 19.871 | 19.8087 | 11.4344 | 11.2457 | 11.0001 | 10.7211 | 10.2553 | 9.5328 | 8.4073 | 6.9274 | 5.308 | 3.315 | 1.8958 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.9218 | 19.8209 | 19.6895 | 19.3986 | 19.1679 | 18.949 | 16.6703 | 15.669 | 13.7671 | 11.1987 | 8.1922 | 5.1087 | 1.4583 | 0 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.9218 | 19.8825 | 19.8435 | 11.633 | 11.5991 | 11.5254 | 11.3912 | 11.0946 | 10.5012 | 9.4879 | 8.1416 | 6.6988 | 4.8344 | 3.5609 | 1.6879 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.9218 | 19.8154 | 19.6702 | 19.3763 | 19.1521 | 18.9555 | 16.8784 | 16.498 | 15.4633 | 14.1383 | 11.974 | 9.2093 | 5.622 | 2.2024 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.9218 | 19.867 | 19.8 | 19.6905 | 19.5733 | 19.3723 | 19.115 | 16.9742 | 15.971 | 13.9529 | 11.4721 | 9.0115 | 5.9998 | 3.994 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 85.4867 | 86.1895 | 86.196 | 79.6463 | 79.2866 | 78.7331 | 78.1313 | 77.0897 | 75.5519 | 73.1213 | 69.7478 | 66.0178 | 61.4614 | 58.1426 | 49.0671 | 25.6044 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 85.4867 | 86.086 | 85.9434 | 85.2857 | 84.6692 | 83.2842 | 81.466 | 78.6984 | 74.259 | 68.3169 | 61.184 | 53.7819 | 45.0656 | 38.1606 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 85.4867 | 86.0671 | 86.0664 | 79.9396 | 79.9924 | 79.9601 | 79.7999 | 79.2804 | 78.1645 | 76.1548 | 73.3481 | 70.2956 | 66.2518 | 63.4677 | 59.2369 | 52.6888 | 44.9009
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 85.4867 | 86.1301 | 85.9574 | 85.3061 | 84.6785 | 83.6111 | 82.3742 | 80.9122 | 78.2141 | 75.0043 | 69.8185 | 63.2558 | 54.78 | 46.7222 | 0 | 0 | 0
Grendon 132kV | KIBWORTH 33KV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 85.4867 | 86.1837 | 86.1893 | 86.0371 | 85.882 | 85.4736 | 84.8394 | 83.4485 | 80.5392 | 76.1981 | 70.7405 | 65.2691 | 58.5451 | 54.0166 | 41.9463 | 14.3455 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.0021 | 16.8874 | 16.7725 | 16.469 | 16.1698 | 15.8447 | 15.5578 | 15.2032 | 14.0413 | 13.9714 | 13.8147 | 13.5637 | 13.3438 | 13.1147 | 11.3533 | 8.4969 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.0021 | 16.8864 | 16.7688 | 16.4646 | 16.1649 | 15.8424 | 15.5545 | 15.2107 | 14.0438 | 13.9819 | 13.8497 | 13.6174 | 13.3953 | 13.1542 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.0021 | 16.9418 | 16.9175 | 16.895 | 16.8898 | 16.862 | 16.8471 | 16.8171 | 16.7735 | 16.7385 | 16.7128 | 16.6987 | 16.6953 | 16.7026 | 16.8682 | 17.0005 | 16.5761
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.0021 | 16.8823 | 16.753 | 16.4378 | 16.1468 | 15.8074 | 15.507 | 15.1687 | 14.0348 | 13.9371 | 13.7537 | 13.5291 | 13.2817 | 13.0022 | 0 | 0 | 0
Grendon 132kV | KINGSTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.0021 | 16.923 | 16.8648 | 16.7732 | 16.6699 | 16.5267 | 16.4119 | 16.2639 | 16.1174 | 15.9879 | 15.873 | 15.7804 | 15.7037 | 15.662 | 15.1764 | 13.5214 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.1071 | 1.9333 | 1.7227 | 1.1935 | 0.94877 | 0.71571 | 0.11021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.1071 | 1.8712 | 1.5835 | 0.91109 | 0.48675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.1071 | 1.9935 | 1.9072 | 1.8213 | 1.9339 | 2.0594 | 1.9656 | 1.7825 | 1.4475 | 0.90055 | 0.19396 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.1071 | 1.8706 | 1.5642 | 0.86007 | 0.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | LITTLE IRCHESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.1071 | 1.9556 | 1.803 | 1.5637 | 1.529 | 1.3413 | 0.89051 | 0.20441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.4872 | 15.7414 | 15.9066 | 15.833 | 15.8174 | 15.6812 | 15.5455 | 15.2256 | 14.6998 | 13.8355 | 12.5212 | 11.1043 | 9.3914 | 8.1128 | 4.784 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.4872 | 15.6896 | 15.7794 | 15.5438 | 15.3826 | 14.7247 | 13.9619 | 12.7873 | 10.9293 | 8.4767 | 5.4846 | 2.4344 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.4872 | 15.4769 | 15.6313 | 15.7698 | 15.9097 | 16.0126 | 16.064 | 15.9521 | 15.613 | 14.9039 | 13.8895 | 12.7857 | 11.3005 | 10.2616 | 8.5741 | 5.8516 | 2.6383
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.4872 | 15.762 | 15.8329 | 15.6176 | 15.4336 | 14.9066 | 14.4716 | 13.8628 | 12.7151 | 11.3541 | 9.1035 | 6.3431 | 2.8375 | 0 | 0 | 0 | 0
Grendon 132kV | MARKET HARBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.4872 | 15.7403 | 15.9079 | 15.9353 | 15.9969 | 15.88 | 15.6746 | 15.1196 | 13.853 | 12.0862 | 9.8529 | 7.6716 | 5.0295 | 3.1748 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.4168 | 20.4339 | 20.505 | 19.4574 | 19.4981 | 19.4906 | 19.4204 | 19.3327 | 16.5643 | 16.1005 | 14.9509 | 13.4677 | 11.6093 | 10.2947 | 7.1672 | 2.1185 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.4168 | 20.3254 | 20.2391 | 19.8638 | 19.6809 | 19.3779 | 16.3704 | 15.2707 | 13.1189 | 10.2385 | 6.6981 | 3.0096 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.4168 | 20.4012 | 20.4171 | 19.4504 | 19.4858 | 19.514 | 19.4614 | 19.3644 | 16.6161 | 16.2055 | 15.1264 | 13.7772 | 11.9519 | 10.6984 | 8.9558 | 5.875 | 1.5935
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.4168 | 20.3229 | 20.2136 | 19.8302 | 19.6438 | 19.403 | 16.5069 | 15.9338 | 14.5869 | 12.9138 | 10.1362 | 6.6584 | 2.2722 | 0 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 11KV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.4168 | 20.3834 | 20.3794 | 20.2424 | 20.2541 | 20.078 | 19.7203 | 19.3367 | 15.8867 | 13.771 | 10.8967 | 8.0146 | 4.4985 | 2.0454 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 41.2288 | 41.2532 | 41.288 | 40.6614 | 40.7123 | 40.681 | 40.5275 | 40.1693 | 39.6013 | 38.5779 | 36.9073 | 34.9141 | 32.4558 | 30.6979 | 26.0777 | 19.188 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 41.2288 | 41.21 | 41.1728 | 40.929 | 40.6816 | 40.0185 | 38.9156 | 37.1755 | 34.325 | 30.6037 | 26.08 | 21.3478 | 15.8396 | 11.0706 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 41.2288 | 41.2431 | 41.265 | 40.6839 | 40.7648 | 40.8195 | 40.7469 | 40.531 | 40.0502 | 39.0452 | 37.4815 | 35.6916 | 33.3016 | 31.6482 | 29.2542 | 25.2397 | 19.8559
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 41.2288 | 41.2085 | 41.1594 | 40.9004 | 40.6358 | 40.116 | 39.2376 | 38.1252 | 36.235 | 34.0477 | 30.53 | 26.1184 | 20.517 | 14.9403 | 0 | 0 | 0
Grendon 132kV | MELTON MOWBRAY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 41.2288 | 41.2353 | 41.245 | 41.2189 | 41.2171 | 41.1088 | 40.793 | 40.001 | 38.1519 | 35.2889 | 31.6018 | 27.9019 | 23.3716 | 20.2328 | 11.8267 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 34.7916 | 34.7084 | 34.5788 | 34.2498 | 33.9234 | 33.6047 | 33.3169 | 33.0344 | 32.7952 | 32.6033 | 32.4311 | 32.3129 | 31.5479 | 31.4185 | 30.036 | 27.7616 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 34.7916 | 34.7075 | 34.5748 | 34.2452 | 33.9175 | 33.5984 | 33.3053 | 33.0304 | 32.8015 | 32.6109 | 32.4523 | 32.3182 | 31.5556 | 31.4558 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 34.7916 | 34.7482 | 34.6871 | 34.6085 | 34.5315 | 34.4563 | 34.3826 | 34.3227 | 34.2599 | 34.2095 | 34.1683 | 34.1405 | 34.1183 | 34.104 | 34.1795 | 34.1695 | 33.6697
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 34.7916 | 34.7063 | 34.559 | 34.2151 | 33.8836 | 33.5434 | 33.2366 | 32.9747 | 32.7349 | 32.5351 | 32.3756 | 32.3097 | 31.5301 | 31.3649 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 34.7916 | 34.7392 | 34.6538 | 34.5104 | 34.3412 | 34.1565 | 33.9879 | 33.8415 | 33.707 | 33.5848 | 33.4799 | 33.3975 | 33.3265 | 33.2766 | 32.8745 | 25.441 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 104.8125 | 104.2725 | 103.6434 | 102.2575 | 100.8529 | 99.4738 | 98.1587 | 96.6708 | 95.1143 | 93.5379 | 91.8217 | 89.7668 | 87.8463 | 86.3803 | 77.7807 | 45.408 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 104.8125 | 104.2678 | 103.6132 | 102.2245 | 100.8159 | 99.2504 | 97.6299 | 95.7896 | 93.5718 | 91.1223 | 88.5479 | 85.5187 | 82.4071 | 79.6982 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 104.8125 | 104.5384 | 104.3709 | 104.1223 | 103.9415 | 103.7627 | 103.5378 | 103.264 | 102.7878 | 102.1635 | 101.4656 | 100.7424 | 99.8936 | 99.304 | 99.1016 | 97.5914 | 93.7012
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 104.8125 | 104.2567 | 103.5617 | 102.136 | 100.7204 | 99.1992 | 97.6968 | 96.2294 | 94.4581 | 92.538 | 90.2213 | 87.2589 | 84.1839 | 81.1019 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 104.8125 | 104.419 | 104.0025 | 103.5369 | 102.9331 | 102.2237 | 101.4692 | 100.5623 | 99.2015 | 97.5757 | 95.8779 | 94.2193 | 92.352 | 90.9964 | 85.8162 | 25.441 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 104.8125 | 104.2725 | 103.6434 | 102.2575 | 100.8529 | 99.4738 | 98.1587 | 96.6708 | 95.1143 | 93.5379 | 91.8217 | 89.7668 | 87.8463 | 86.3803 | 77.7807 | 45.408 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 104.8125 | 104.2678 | 103.6132 | 102.2245 | 100.8159 | 99.2504 | 97.6299 | 95.7896 | 93.5718 | 91.1223 | 88.5479 | 85.5187 | 82.4071 | 79.6982 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 104.8125 | 104.5384 | 104.3709 | 104.1223 | 103.9415 | 103.7627 | 103.5378 | 103.264 | 102.7878 | 102.1635 | 101.4656 | 100.7424 | 99.8936 | 99.304 | 99.1016 | 97.5914 | 93.7012
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 104.8125 | 104.2567 | 103.5617 | 102.136 | 100.7204 | 99.1992 | 97.6968 | 96.2294 | 94.4581 | 92.538 | 90.2213 | 87.2589 | 84.1839 | 81.1019 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 104.8125 | 104.419 | 104.0025 | 103.5369 | 102.9331 | 102.2237 | 101.4692 | 100.5623 | 99.2015 | 97.5757 | 95.8779 | 94.2193 | 92.352 | 90.9964 | 85.8162 | 25.441 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Best View | Headroom (MW) | 20.6485 | 20.5534 | 20.4438 | 20.1915 | 19.955 | 19.7355 | 19.541 | 19.3566 | 19.2151 | 19.128 | 19.0705 | 16.929 | 16.9115 | 16.8508 | 15.785 | 13.6672 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.6485 | 20.5527 | 20.4412 | 20.1892 | 19.9531 | 19.7364 | 19.5426 | 19.3633 | 19.226 | 19.1353 | 19.0769 | 16.9306 | 16.9235 | 16.8735 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.6485 | 20.6032 | 20.5604 | 20.5174 | 20.4652 | 20.4118 | 20.3593 | 20.3096 | 20.2558 | 20.2097 | 20.1725 | 20.1453 | 20.1292 | 20.1232 | 20.2117 | 20.2463 | 19.8243
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.6485 | 20.5478 | 20.4231 | 20.1577 | 19.916 | 19.6882 | 19.4865 | 19.3171 | 19.1857 | 19.1019 | 19.0618 | 16.9223 | 16.8761 | 16.7653 | 0 | 0 | 0
Grendon 132kV | Northampton East 11kv S Stn | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.6485 | 20.5818 | 20.509 | 20.4038 | 20.2835 | 20.1556 | 20.0333 | 19.9191 | 19.8096 | 19.7174 | 19.6385 | 19.5763 | 19.5291 | 19.4955 | 19.1771 | 16.9754 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 88.7214 | 87.939 | 87.3897 | 86.0284 | 84.5954 | 83.0806 | 81.5091 | 79.6658 | 77.5079 | 74.9006 | 71.7783 | 68.2707 | 64.5313 | 61.386 | 48.4448 | 30.2763 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 88.7214 | 87.9301 | 87.3614 | 86.0062 | 84.5694 | 82.6093 | 80.3655 | 77.3104 | 73.0485 | 68.0675 | 62.4739 | 56.4523 | 49.7549 | 44.1162 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 88.7214 | 88.2566 | 88.1238 | 87.9439 | 87.8191 | 87.6316 | 87.3776 | 86.9751 | 86.2528 | 85.1494 | 83.7312 | 81.859 | 79.4806 | 77.7866 | 75.7502 | 71.7969 | 64.9692
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 88.7214 | 87.9235 | 87.3082 | 85.9069 | 84.4496 | 82.6241 | 80.6629 | 78.6312 | 75.4933 | 72.1937 | 67.6459 | 62.168 | 55.4645 | 48.8843 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 88.7214 | 88.1007 | 87.7866 | 87.376 | 86.8136 | 86.0562 | 85.1229 | 83.7667 | 81.4887 | 78.0676 | 74.1682 | 70.3846 | 65.9114 | 62.6669 | 52.7269 | 25.556 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 88.7214 | 87.939 | 87.3897 | 86.0284 | 84.5954 | 83.0806 | 81.5091 | 79.6658 | 77.5079 | 74.9006 | 71.7783 | 68.2707 | 64.5313 | 61.386 | 48.4448 | 30.2763 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 88.7214 | 87.9301 | 87.3614 | 86.0062 | 84.5694 | 82.6093 | 80.3655 | 77.3104 | 73.0485 | 68.0675 | 62.4739 | 56.4523 | 49.7549 | 44.1162 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 88.7214 | 88.2566 | 88.1238 | 87.9439 | 87.8191 | 87.6316 | 87.3776 | 86.9751 | 86.2528 | 85.1494 | 83.7312 | 81.859 | 79.4806 | 77.7866 | 75.7502 | 71.7969 | 64.9692
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 88.7214 | 87.9235 | 87.3082 | 85.9069 | 84.4496 | 82.6241 | 80.6629 | 78.6312 | 75.4933 | 72.1937 | 67.6459 | 62.168 | 55.4645 | 48.8843 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON EAST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 88.7214 | 88.1007 | 87.7866 | 87.376 | 86.8136 | 86.0562 | 85.1229 | 83.7667 | 81.4887 | 78.0676 | 74.1682 | 70.3846 | 65.9114 | 62.6669 | 52.7269 | 25.556 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.8254 | 24.829 | 24.7596 | 24.5185 | 24.2546 | 23.9408 | 23.6169 | 23.5325 | 23.1208 | 22.7475 | 22.3382 | 21.9328 | 21.726 | 21.5716 | 17.8168 | 15.7152 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.8254 | 24.8284 | 24.7568 | 24.5156 | 24.2512 | 23.9387 | 23.6069 | 23.5322 | 23.1382 | 22.7721 | 22.3868 | 21.9609 | 21.7302 | 21.5608 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.8254 | 24.8328 | 24.8177 | 24.8059 | 24.7884 | 24.767 | 24.7431 | 24.8771 | 24.8477 | 24.8176 | 24.7728 | 24.7197 | 24.6792 | 24.6417 | 24.4573 | 24.2501 | 23.668
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.8254 | 24.8303 | 24.7424 | 24.4959 | 24.212 | 23.9053 | 23.5439 | 23.4346 | 22.9755 | 22.5405 | 22.0883 | 21.7053 | 21.5585 | 21.496 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.8254 | 24.8543 | 24.8346 | 24.7631 | 24.6604 | 24.5 | 24.3364 | 24.4517 | 24.2172 | 23.9919 | 23.7311 | 23.4691 | 23.3057 | 23.1545 | 22.282 | 21.4043 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 120.3999 | 120.4473 | 120.5839 | 119.8174 | 119.177 | 117.5811 | 116.7529 | 116.0511 | 115.3863 | 106.3858 | 104.4638 | 103.2541 | 101.8174 | 100.3123 | 90.9884 | 44.4086 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 120.3999 | 120.4437 | 120.5645 | 119.7967 | 119.1561 | 118.1459 | 117.1479 | 116.2752 | 115.3834 | 104.7314 | 103.9673 | 102.001 | 100.56 | 98.3741 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 120.3999 | 120.5635 | 120.8057 | 121.0481 | 121.2973 | 121.1229 | 121.3841 | 121.6737 | 121.7894 | 121.6705 | 121.4616 | 121.2476 | 120.8107 | 120.4981 | 120.1174 | 119.9025 | 116.352
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 120.3999 | 120.4534 | 120.4943 | 119.7656 | 119.1303 | 118.2806 | 117.3145 | 116.5738 | 115.646 | 106.4134 | 104.3953 | 102.6667 | 100.3254 | 97.7461 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 120.3999 | 120.5856 | 120.9312 | 120.8977 | 120.8583 | 120.5956 | 120.4042 | 120.3313 | 119.8654 | 118.634 | 117.3067 | 116.1847 | 115.7899 | 115.1623 | 104.3126 | 24.881 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 120.3999 | 120.4473 | 120.5839 | 119.8174 | 119.177 | 117.5811 | 116.7529 | 116.0511 | 115.3863 | 106.3858 | 104.4638 | 103.2541 | 101.8174 | 100.3123 | 90.9884 | 44.4086 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 120.3999 | 120.4437 | 120.5645 | 119.7967 | 119.1561 | 118.1459 | 117.1479 | 116.2752 | 115.3834 | 104.7314 | 103.9673 | 102.001 | 100.56 | 98.3741 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 120.3999 | 120.5635 | 120.8057 | 121.0481 | 121.2973 | 121.1229 | 121.3841 | 121.6737 | 121.7894 | 121.6705 | 121.4616 | 121.2476 | 120.8107 | 120.4981 | 120.1174 | 119.9025 | 116.352
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 120.3999 | 120.4534 | 120.4943 | 119.7656 | 119.1303 | 118.2806 | 117.3145 | 116.5738 | 115.646 | 106.4134 | 104.3953 | 102.6667 | 100.3254 | 97.7461 | 0 | 0 | 0
Grendon 132kV | NORTHAMPTON WEST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 120.3999 | 120.5856 | 120.9312 | 120.8977 | 120.8583 | 120.5956 | 120.4042 | 120.3313 | 119.8654 | 118.634 | 117.3067 | 116.1847 | 115.7899 | 115.1623 | 104.3126 | 24.881 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.6078 | 21.7464 | 21.8965 | 21.9006 | 21.9516 | 21.9258 | 19.0237 | 18.8985 | 18.8504 | 18.3647 | 17.3296 | 16.5062 | 15.4619 | 14.7332 | 13.1093 | 10.1555 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.6078 | 21.6714 | 21.714 | 21.4711 | 21.2861 | 20.8842 | 20.4175 | 19.7526 | 18.9019 | 17.2637 | 15.6091 | 13.8059 | 11.7213 | 9.8991 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.6078 | 21.6937 | 21.7826 | 21.8566 | 21.9301 | 21.9749 | 19.0953 | 18.9918 | 18.8286 | 18.3734 | 17.3839 | 16.6623 | 15.6519 | 14.9664 | 13.8036 | 11.8517 | 9.4762
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.6078 | 21.6763 | 21.6939 | 21.4621 | 21.2774 | 20.9804 | 20.6397 | 20.2545 | 19.7332 | 18.8549 | 17.3469 | 15.7511 | 13.667 | 11.5455 | 0 | 0 | 0
Grendon 132kV | OAKHAM 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.6078 | 21.7126 | 21.8214 | 21.8112 | 21.822 | 21.6998 | 21.5226 | 21.119 | 20.4806 | 19.1945 | 17.484 | 16.0907 | 14.2931 | 13.0804 | 9.758 | 4.638 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 63.2441 | 63.2765 | 63.378 | 63.231 | 63.1378 | 62.9111 | 59.7047 | 59.2615 | 58.6739 | 57.1856 | 55.0566 | 52.6884 | 49.9644 | 48.1072 | 43.7726 | 25.4644 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 63.2441 | 63.1153 | 62.9917 | 62.3234 | 61.7349 | 60.5397 | 59.0638 | 57.1392 | 54.3021 | 50.3196 | 45.6341 | 40.7096 | 34.9731 | 30.0996 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 63.2441 | 63.2233 | 63.2614 | 63.2814 | 63.2868 | 63.2085 | 60.1421 | 59.6833 | 58.9548 | 57.4448 | 55.3687 | 53.1444 | 50.2556 | 48.3029 | 45.1617 | 40.2649 | 34.4306
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 63.2441 | 63.1132 | 62.9468 | 62.2796 | 61.6867 | 60.7196 | 59.6069 | 58.5073 | 56.7401 | 54.391 | 50.7524 | 46.2299 | 40.5313 | 34.8828 | 0 | 0 | 0
Grendon 132kV | OAKHAM 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 63.2441 | 63.2087 | 63.228 | 63.0606 | 62.8934 | 62.4439 | 61.7921 | 60.6308 | 58.4819 | 55.1445 | 51.1195 | 47.1509 | 42.3391 | 39.1455 | 30.6285 | 14.2671 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.1029 | 19.0414 | 18.963 | 18.7778 | 18.6028 | 18.4284 | 18.3021 | 18.2601 | 18.2173 | 17.4725 | 17.4661 | 17.3825 | 17.2097 | 17.0334 | 15.8744 | 14.0396 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.1029 | 19.0462 | 18.9756 | 18.8014 | 18.6321 | 18.4588 | 18.3211 | 18.2524 | 17.7577 | 17.4485 | 17.3924 | 17.1449 | 16.7814 | 16.5195 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.1029 | 19.0821 | 19.0609 | 19.0395 | 19.0152 | 18.986 | 18.9822 | 19.0254 | 19.0595 | 19.0869 | 19.1075 | 19.0771 | 19.0158 | 19.0117 | 19.0912 | 18.8741 | 18.3734
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.1029 | 19.0414 | 18.963 | 18.7778 | 18.6028 | 18.4317 | 18.3106 | 18.2821 | 18.2255 | 17.7624 | 17.457 | 17.2816 | 16.9304 | 16.6143 | 0 | 0 | 0
Grendon 132kV | OAKLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.1029 | 19.0668 | 19.026 | 18.9612 | 18.8846 | 18.7876 | 18.7136 | 18.7217 | 18.7005 | 18.6554 | 18.6438 | 18.4702 | 18.2666 | 18.1875 | 17.2272 | 14.1127 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.5251 | 4.1419 | 4.1259 | 3.2653 | 3.2262 | 3.1677 | 3.0891 | 2.9322 | 2.6548 | 2.212 | 1.624 | 0.98424 | 0.18052 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.5251 | 4.1198 | 4.0734 | 3.9683 | 3.869 | 3.6428 | 3.341 | 2.8893 | 2.0857 | 1.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.5251 | 4.2017 | 4.123 | 3.2848 | 3.2658 | 3.2296 | 3.1705 | 3.0385 | 2.7839 | 2.354 | 1.7814 | 1.1669 | 0.37765 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.5251 | 4.1206 | 4.0721 | 3.9627 | 3.8624 | 3.6776 | 3.474 | 3.236 | 2.7529 | 2.2044 | 1.3238 | 0.20609 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLD DALBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.5251 | 4.1346 | 4.1082 | 4.0663 | 4.0191 | 3.9259 | 3.772 | 3.4501 | 2.7791 | 1.8563 | 0.76462 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.4086 | 15.3051 | 15.18 | 14.8258 | 14.5009 | 14.1444 | 13.7556 | 13.1915 | 12.385 | 11.2329 | 9.7619 | 8.1593 | 6.2251 | 4.7429 | 0.40832 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.4086 | 15.2931 | 15.1551 | 14.8121 | 14.4849 | 13.7739 | 12.8622 | 11.5649 | 9.459 | 6.7415 | 3.5878 | 0.32883 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.4086 | 15.3737 | 15.346 | 15.3087 | 15.2611 | 15.1784 | 15.0472 | 14.7705 | 14.2296 | 13.319 | 12.1161 | 10.8272 | 9.1747 | 7.9971 | 6.2596 | 3.2963 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.4086 | 15.2984 | 15.1558 | 14.8044 | 14.4778 | 13.909 | 13.2965 | 12.6017 | 11.3354 | 9.8608 | 7.5517 | 4.639 | 0.88637 | 0 | 0 | 0 | 0
Grendon 132kV | OLNEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.4086 | 15.3388 | 15.2638 | 15.1416 | 14.9995 | 14.7571 | 14.3911 | 13.653 | 12.148 | 10.0875 | 7.6628 | 5.2715 | 2.3628 | 0.28559 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.0494 | 10.9759 | 10.8743 | 10.6381 | 10.4177 | 10.1807 | 9.9297 | 9.622 | 7.0597 | 1.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.0494 | 10.9772 | 10.8845 | 10.655 | 10.433 | 10.029 | 9.5343 | 7.2202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.0494 | 11.0233 | 10.9966 | 10.9689 | 10.9349 | 10.8885 | 10.8194 | 10.6849 | 10.4246 | 10.0016 | 9.4486 | 8.8621 | 8.1214 | 7.5823 | 4.9257 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.0494 | 10.9759 | 10.8743 | 10.6381 | 10.4177 | 10.0769 | 9.7182 | 9.3277 | 3.8729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | OUNDLE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.0494 | 11.008 | 10.9559 | 10.8736 | 10.7763 | 10.6294 | 10.4245 | 10.0516 | 9.3062 | 8.3063 | 2.1031 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.3334 | 13.2976 | 13.2299 | 13.0857 | 12.9307 | 12.6576 | 12.4184 | 12.1592 | 11.8598 | 11.5456 | 11.1937 | 10.8442 | 10.4558 | 10.097 | 8.3615 | 1.7951 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.3334 | 13.3002 | 13.2488 | 13.1034 | 12.9453 | 12.6134 | 12.2743 | 11.8717 | 11.3935 | 10.8516 | 10.2519 | 9.5895 | 8.8742 | 8.3149 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.3334 | 13.3294 | 13.3272 | 13.3718 | 13.3809 | 13.3317 | 13.2804 | 13.2114 | 13.1046 | 12.9645 | 12.7959 | 12.6254 | 12.4182 | 12.2584 | 12.036 | 11.6863 | 11.0065
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.3334 | 13.2976 | 13.2299 | 13.0857 | 12.9307 | 12.6195 | 12.3379 | 12.0413 | 11.6686 | 11.2804 | 10.7736 | 10.1975 | 9.5125 | 8.879 | 0 | 0 | 0
Grendon 132kV | PARK FARM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.3334 | 13.3286 | 13.3215 | 13.3196 | 13.2819 | 13.1342 | 12.9878 | 12.793 | 12.5248 | 12.205 | 11.8517 | 11.5142 | 11.1316 | 10.8508 | 9.8552 | 8.1773 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.4875 | 15.4815 | 15.4727 | 15.4645 | 15.4537 | 15.4303 | 15.4012 | 15.3639 | 15.313 | 15.2589 | 15.1998 | 15.1356 | 15.0666 | 14.9966 | 14.7555 | 14.6526 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.4875 | 15.4815 | 15.4727 | 15.4645 | 15.4536 | 15.4303 | 15.4011 | 15.3634 | 15.3121 | 15.257 | 15.1986 | 15.1341 | 15.0646 | 14.9939 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.4875 | 15.4811 | 15.4729 | 15.4686 | 15.4692 | 15.4628 | 15.4563 | 15.4486 | 15.4333 | 15.4155 | 15.395 | 15.3721 | 15.3471 | 15.3181 | 15.192 | 15.1166 | 15.0457
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.4875 | 15.4847 | 15.4801 | 15.4749 | 15.468 | 15.446 | 15.4128 | 15.3703 | 15.3069 | 15.242 | 15.1696 | 14.622 | 14.544 | 14.4682 | 0 | 0 | 0
Grendon 132kV | PINEHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.4875 | 15.4831 | 15.4774 | 15.4741 | 15.4697 | 15.4543 | 15.4374 | 15.4145 | 15.381 | 15.3454 | 15.3058 | 15.2636 | 15.2148 | 15.1649 | 14.7445 | 14.656 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.603 | 17.544 | 17.4765 | 17.3042 | 17.1303 | 16.9466 | 16.7554 | 16.5291 | 16.2325 | 15.8545 | 15.3937 | 14.873 | 14.2493 | 13.7263 | 10.9496 | 8.047 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.603 | 17.5463 | 17.4857 | 17.3157 | 17.1323 | 16.7936 | 16.3849 | 15.846 | 15.0673 | 14.1351 | 13.0721 | 11.9493 | 10.6695 | 9.6134 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.603 | 17.6011 | 17.5646 | 17.5683 | 17.5702 | 17.5684 | 17.5588 | 17.5218 | 17.4189 | 17.2161 | 16.93 | 16.6213 | 16.2214 | 15.9455 | 15.6365 | 14.8534 | 13.6509
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.603 | 17.5444 | 17.4775 | 17.306 | 17.1329 | 16.8601 | 16.5676 | 16.2423 | 15.7147 | 15.1685 | 14.3691 | 13.35 | 12.0701 | 10.829 | 0 | 0 | 0
Grendon 132kV | PYTCHLEY ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.603 | 17.5631 | 17.537 | 17.502 | 17.454 | 17.3774 | 17.2684 | 17.0542 | 16.6192 | 16.047 | 15.3778 | 14.7253 | 13.9368 | 13.3536 | 11.3777 | 8.5513 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Best View | Headroom (MW) | 14.8459 | 14.5674 | 13.9399 | 12.3287 | 10.8619 | 9.1771 | 7.5381 | 5.692 | 3.5665 | 1.0007 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.8459 | 14.5708 | 14.014 | 12.456 | 11.024 | 8.8572 | 6.5599 | 3.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.8459 | 14.8376 | 14.7147 | 14.5939 | 14.4779 | 14.2309 | 13.9763 | 13.5063 | 12.7099 | 11.4334 | 9.8281 | 8.1522 | 6.0751 | 4.5686 | 2.4884 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.8459 | 14.5659 | 13.9364 | 12.3223 | 10.8517 | 8.8577 | 6.8917 | 4.7832 | 1.9566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | Raunds 11kv | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.8459 | 14.7777 | 14.5156 | 14.0035 | 13.4619 | 12.5535 | 11.5899 | 10.1254 | 7.7451 | 4.6099 | 1.0625 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.3814 | 1.329 | 1.2605 | 1.0879 | 0.92124 | 0.74805 | 0.56996 | 0.33008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.3814 | 1.3285 | 1.2584 | 1.0859 | 0.91948 | 0.6265 | 0.27228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.3814 | 1.3654 | 1.3486 | 1.3309 | 1.3051 | 1.2676 | 1.2143 | 1.1132 | 0.91957 | 0.61075 | 0.20705 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.3814 | 1.3267 | 1.2514 | 1.0731 | 0.90474 | 0.65334 | 0.39181 | 0.10556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | ROADE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.3814 | 1.35 | 1.3122 | 1.2499 | 1.1776 | 1.068 | 0.92005 | 0.6513 | 0.098255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.2724 | 7.085 | 6.8261 | 6.3071 | 5.801 | 5.2757 | 4.7962 | 4.2862 | 3.5677 | 1.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.2724 | 7.0941 | 6.8617 | 6.364 | 5.8768 | 5.355 | 4.9084 | 3.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.2724 | 7.1957 | 7.1172 | 7.0931 | 7.0533 | 7.013 | 7.0037 | 6.9595 | 6.9505 | 6.8978 | 6.8563 | 6.8283 | 6.0772 | 4.5702 | 2.4893 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.2724 | 7.0834 | 6.8227 | 6.3007 | 5.7908 | 5.2625 | 4.7799 | 4.2714 | 1.9572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | RUSHDEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.2724 | 7.1568 | 7.0184 | 6.867 | 6.6802 | 6.4324 | 6.2436 | 6.0281 | 5.9082 | 4.6115 | 1.0628 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.09 | 1.0001 | 0.89113 | 0.61735 | 0.49078 | 0.37022 | 0.057009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.09 | 0.96792 | 0.8191 | 0.47129 | 0.25178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.09 | 1.0312 | 0.98653 | 0.94211 | 1.0004 | 1.0653 | 1.0168 | 0.92202 | 0.74876 | 0.46583 | 0.10033 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.09 | 0.96762 | 0.80913 | 0.44489 | 0.21493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | SHARNBROOK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.09 | 1.0116 | 0.93266 | 0.80887 | 0.79093 | 0.69383 | 0.46064 | 0.10573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.2432 | 14.9573 | 14.3129 | 12.6586 | 11.1525 | 9.4226 | 7.7398 | 5.8443 | 3.6619 | 1.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.2432 | 14.9607 | 14.389 | 12.7893 | 11.319 | 9.0942 | 6.7354 | 3.7451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.2432 | 15.2347 | 15.1084 | 14.9844 | 14.8653 | 14.6117 | 14.3503 | 13.8678 | 13.05 | 11.7394 | 10.0911 | 8.3704 | 6.2376 | 4.6908 | 2.555 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.2432 | 14.9556 | 14.3094 | 12.652 | 11.142 | 9.0947 | 7.0761 | 4.9112 | 2.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | THRAPSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.2432 | 15.1731 | 14.904 | 14.3782 | 13.8222 | 12.8894 | 11.9 | 10.3963 | 7.9523 | 4.7332 | 1.0909 | 0 | 0 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.5915 | 10.5763 | 10.5607 | 10.5138 | 10.4659 | 10.3994 | 10.3086 | 10.1096 | 9.7451 | 9.1355 | 8.3085 | 7.4032 | 6.2568 | 5.4867 | 4.1367 | 1.9478 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.5915 | 10.5427 | 10.4804 | 10.3235 | 10.174 | 9.8171 | 9.3466 | 8.6496 | 7.4848 | 5.9727 | 4.2124 | 2.3909 | 0.23399 | 0 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.5915 | 10.574 | 10.5564 | 10.5383 | 10.5108 | 10.4612 | 10.3787 | 10.1968 | 9.8349 | 9.2166 | 8.385 | 7.4883 | 6.3236 | 5.5363 | 4.3797 | 2.6396 | 0.71492
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.5915 | 10.5407 | 10.4721 | 10.3097 | 10.1562 | 9.8795 | 9.5748 | 9.2265 | 8.522 | 7.697 | 6.4001 | 4.7567 | 2.6397 | 0.62765 | 0 | 0 | 0
Grendon 132kV | UPPINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.5915 | 10.5616 | 10.5252 | 10.4681 | 10.401 | 10.272 | 10.061 | 9.6121 | 8.69 | 7.4157 | 5.9051 | 4.4111 | 2.588 | 1.4168 | 0 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Best View | Headroom (MW) | 37.8076 | 37.7451 | 37.6637 | 37.5126 | 37.3734 | 37.2333 | 37.0928 | 36.9542 | 36.8195 | 36.6931 | 36.5673 | 36.4427 | 36.3208 | 36.1869 | 35.2282 | 33.9482 | 32.339
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 37.8076 | 37.7483 | 37.672 | 37.5286 | 37.391 | 37.2559 | 37.1238 | 36.9879 | 36.8641 | 36.7493 | 36.6378 | 36.5015 | 36.389 | 36.2744 | 18.9783 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Falling Short | Headroom (MW) | 37.8076 | 37.7675 | 37.7275 | 37.6887 | 37.6502 | 37.6113 | 37.5665 | 37.5234 | 37.4788 | 37.4379 | 37.4002 | 37.3674 | 37.34 | 37.3173 | 37.251 | 37.1655 | 36.8771
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | Leading the Way | Headroom (MW) | 37.8076 | 37.7451 | 22.4747 | 22.3104 | 22.1592 | 22.0075 | 21.8558 | 21.7074 | 21.5657 | 21.4289 | 21.2909 | 21.1546 | 21.0202 | 20.8736 | 12.5049 | 0 | 0
Grendon 132kV | Wellingborough 132/11kv (Reserve) | Primary Substation | 11 | System Transformation | Headroom (MW) | 37.8076 | 37.7594 | 37.705 | 37.6359 | 37.5618 | 37.4829 | 37.4025 | 37.3232 | 37.2479 | 37.1758 | 37.1083 | 37.0466 | 36.9943 | 36.9497 | 36.6269 | 35.0713 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 36.3633 | 36.0748 | 35.7342 | 34.7086 | 33.9916 | 33.128 | 31.9013 | 30.5456 | 28.9303 | 27.2161 | 25.2254 | 23.1455 | 20.7739 | 18.8016 | 13.4279 | 1.7959 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 36.3633 | 36.0322 | 35.6642 | 34.5496 | 33.7084 | 32.2655 | 30.4407 | 28.2304 | 25.575 | 22.5815 | 19.2555 | 15.6007 | 11.5656 | 8.5486 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 36.3633 | 36.236 | 36.1773 | 36.1234 | 36.2319 | 36.2508 | 36.0072 | 35.6645 | 35.071 | 34.17 | 33.0336 | 31.8597 | 30.3855 | 29.4062 | 32.0281 | 30.1987 | 26.4902
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 36.3633 | 36.0287 | 35.6192 | 34.468 | 33.6157 | 32.4312 | 30.8763 | 29.2667 | 27.2158 | 25.1587 | 22.3772 | 19.1078 | 15.1716 | 11.7071 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 36.3633 | 36.1752 | 36.0323 | 35.6975 | 35.5359 | 35.0394 | 34.2336 | 33.1412 | 31.5563 | 29.6345 | 27.484 | 25.4068 | 22.9745 | 21.3629 | 19.446 | 10.8786 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.0071 | 22.8867 | 22.7515 | 22.4247 | 22.1055 | 21.8065 | 21.5332 | 21.2593 | 21.0332 | 20.8882 | 20.7826 | 19.2248 | 18.9042 | 18.8573 | 17.5003 | 14.6241 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.0071 | 22.8855 | 22.7468 | 22.4196 | 22.1005 | 21.8044 | 21.5323 | 21.267 | 21.0493 | 20.9012 | 20.7979 | 19.2322 | 18.9133 | 18.8815 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.0071 | 22.95 | 22.9015 | 22.8533 | 22.7928 | 22.7321 | 22.6706 | 22.6143 | 22.5522 | 22.5066 | 22.4752 | 22.4559 | 22.4512 | 22.4609 | 22.6557 | 22.8086 | 22.2494
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.0071 | 22.8759 | 22.7176 | 22.371 | 22.0421 | 21.7245 | 21.4344 | 21.179 | 20.9659 | 20.8257 | 20.7568 | 18.9045 | 18.8658 | 18.7469 | 0 | 0 | 0
Grendon 132kV | WELLINGBOROUGH ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.0071 | 22.9227 | 22.8347 | 22.7056 | 22.5548 | 22.3918 | 22.2347 | 22.0842 | 21.9431 | 21.8345 | 21.7431 | 21.6669 | 21.6175 | 21.591 | 21.1596 | 18.9873 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.5158 | 21.267 | 21.1038 | 20.6709 | 20.2636 | 19.8834 | 19.5674 | 19.2461 | 18.9744 | 18.8418 | 16.4678 | 16.208 | 15.8091 | 15.4011 | 13.1081 | 9.5659 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.5158 | 21.2655 | 21.0981 | 20.6651 | 20.2585 | 19.8139 | 19.4159 | 19.035 | 16.5043 | 16.2838 | 15.7259 | 14.9539 | 14.0337 | 13.2215 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.5158 | 21.3585 | 21.3173 | 21.2753 | 21.2376 | 21.1996 | 21.1694 | 21.1254 | 21.0156 | 20.8506 | 20.6493 | 20.4559 | 20.2293 | 20.0919 | 20.13 | 19.6493 | 18.7056
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.5158 | 21.257 | 21.0789 | 20.6302 | 20.2227 | 19.8003 | 19.4506 | 19.1469 | 18.8811 | 16.4888 | 16.1852 | 15.5794 | 14.7194 | 13.8132 | 0 | 0 | 0
Grendon 132kV | WOOTTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.5158 | 21.3247 | 21.2392 | 21.0943 | 20.9206 | 20.7246 | 20.5404 | 20.3142 | 19.9563 | 19.5385 | 19.1339 | 18.8662 | 16.5388 | 16.4207 | 15.4021 | 12.8942 | 0
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.2253 | 22.1822 | 22.1074 | 21.9748 | 21.8603 | 21.8128 | 21.7266 | 21.5873 | 21.4159 | 21.1559 | 20.8568 | 20.5525 | 20.2029 | 19.9495 | 19.1227 | 17.3431 | 15.6996
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.2253 | 22.154 | 22.0388 | 21.7988 | 21.5844 | 21.426 | 21.2402 | 21.0345 | 20.8241 | 20.4631 | 20.0716 | 19.63 | 19.1236 | 18.6982 | 16.9065 | 14.5957 | 12.0349
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.2253 | 22.1857 | 22.1315 | 22.0723 | 22.0389 | 22.0831 | 22.0873 | 22.047 | 21.9776 | 21.8082 | 21.5875 | 21.3568 | 21.0458 | 20.8574 | 20.533 | 20.023 | 19.3014
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.2253 | 22.1503 | 22.0256 | 21.7741 | 21.5529 | 21.4491 | 21.2846 | 21.1497 | 20.9909 | 20.7293 | 20.37 | 19.9548 | 19.4442 | 18.9352 | 16.6648 | 14.1878 | 11.8829
Lea Marston 132kV | APOLLO 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.2253 | 22.1795 | 22.1053 | 21.9985 | 21.9039 | 21.852 | 21.7652 | 21.6368 | 21.4569 | 21.0896 | 20.68 | 20.2897 | 19.7938 | 19.5041 | 18.5629 | 16.9365 | 15.3133
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1621 | 19.9886 | 20.0059 | 19.8904 | 19.7149 | 19.5215 | 19.3256 | 19.12 | 18.9347 | 18.8076 | 18.6807 | 18.4996 | 18.386 | 18.2691 | 16.6273 | 15.3758 | 13.5232
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1621 | 19.9242 | 19.8401 | 19.5226 | 19.128 | 18.688 | 18.2268 | 17.0293 | 16.806 | 16.4974 | 16.1779 | 15.8093 | 15.4694 | 15.1282 | 12.7474 | 10.2469 | 4.0881
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1621 | 20.071 | 19.9706 | 19.9443 | 19.8636 | 19.7737 | 19.6788 | 19.5852 | 19.4834 | 19.3802 | 19.2881 | 19.2052 | 19.1314 | 19.0661 | 18.9856 | 18.951 | 18.4584
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1621 | 19.9101 | 19.7967 | 19.4648 | 19.0571 | 18.5955 | 18.0988 | 16.9774 | 16.6537 | 16.2759 | 15.8969 | 15.5601 | 15.2444 | 14.144 | 12.065 | 9.364 | 3.546
Lea Marston 132kV | ATHERSTONE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1621 | 19.9654 | 19.9509 | 19.8481 | 19.6442 | 19.3941 | 19.131 | 18.8625 | 18.5844 | 18.3347 | 18.1209 | 17.0486 | 17.0262 | 16.9881 | 16.1888 | 15.0876 | 13.6584
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 30.4525 | 27.4458 | 27.5322 | 27.5936 | 27.6008 | 27.597 | 27.6694 | 27.7054 | 27.7236 | 27.7057 | 27.6873 | 27.6676 | 27.6508 | 27.6309 | 27.1391 | 26.9534 | 26.7462
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 30.4525 | 27.4434 | 27.5266 | 27.581 | 27.5819 | 27.5712 | 27.6367 | 27.6659 | 27.6782 | 27.6533 | 27.6286 | 27.6028 | 27.5794 | 27.5519 | 27.0161 | 26.7869 | 11.781
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 30.4525 | 27.5162 | 27.4769 | 27.543 | 27.5527 | 27.562 | 27.6274 | 27.6572 | 27.6795 | 27.6865 | 27.6934 | 27.7003 | 27.7024 | 27.697 | 27.5798 | 27.4539 | 27.31
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 30.4525 | 27.4562 | 27.5383 | 27.6085 | 27.6113 | 27.6109 | 27.6881 | 27.7219 | 27.7261 | 27.696 | 27.6665 | 27.6306 | 26.9879 | 26.9509 | 26.7443 | 26.5008 | 9.6469
Lea Marston 132kV | BIRCH COPPICE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 30.4525 | 27.4455 | 27.531 | 27.5948 | 27.6041 | 27.6014 | 27.675 | 27.7127 | 27.7323 | 27.7132 | 27.694 | 27.6761 | 27.6593 | 27.6411 | 27.1858 | 27.0099 | 26.8257
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.205 | 10.2115 | 10.3256 | 10.2256 | 10.1331 | 9.971 | 9.7949 | 9.2235 | 8.9192 | 8.32 | 7.5753 | 6.7832 | 5.8779 | 5.1498 | 2.7315 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.205 | 10.1457 | 10.1705 | 9.8796 | 9.6202 | 9.1413 | 8.8394 | 8.3782 | 7.7246 | 6.8952 | 5.9567 | 4.9752 | 3.8629 | 2.9364 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.205 | 10.2006 | 10.2683 | 10.2273 | 10.1918 | 10.1382 | 10.0821 | 9.9608 | 9.7225 | 9.1561 | 8.731 | 8.197 | 7.4879 | 7.029 | 6.4242 | 5.5159 | 4.2062
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.205 | 10.1502 | 10.1685 | 9.8601 | 9.6002 | 9.1332 | 8.8872 | 8.5968 | 8.1434 | 7.6374 | 6.9037 | 6.015 | 4.906 | 3.7844 | 0 | 0 | 0
Lea Marston 132kV | POLESWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.205 | 10.1852 | 10.2659 | 10.1553 | 10.031 | 9.8601 | 9.6645 | 9.1665 | 8.6798 | 7.9051 | 6.9904 | 6.0959 | 5.0192 | 4.3936 | 2.7223 | 0.080047 | 0
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 94.5891 | 92.4781 | 87.446 | 87.3081 | 87.0363 | 86.5411 | 86.0047 | 85.1023 | 83.7374 | 82.0688 | 79.9879 | 77.6538 | 75.1648 | 73.0603 | 63.7983 | 52.6007 | 40.3956
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 94.5891 | 92.4434 | 87.2954 | 86.5265 | 85.3543 | 83.8523 | 82.3153 | 80.3547 | 77.9112 | 77.2647 | 74.2136 | 70.923 | 67.4188 | 64.304 | 48.9492 | 30.7683 | 11.7645
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 94.5891 | 92.5759 | 92.5234 | 87.368 | 87.2619 | 87.1249 | 86.9931 | 86.7405 | 86.2464 | 85.3926 | 84.1602 | 82.7976 | 81.0283 | 79.8616 | 78.2909 | 77.9945 | 74.5157
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 94.5891 | 92.443 | 87.2683 | 86.4365 | 85.2101 | 83.243 | 81.7892 | 80.2184 | 78.1764 | 76.1243 | 73.4758 | 70.4768 | 66.3106 | 61.4062 | 45.9429 | 27.5849 | 9.6334
Lea Marston 132kV | TAMWORTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 94.5891 | 92.4643 | 87.4151 | 87.2454 | 86.891 | 86.3127 | 85.6626 | 84.6023 | 82.8821 | 82.6872 | 80.1346 | 77.6575 | 74.7585 | 72.9925 | 65.9173 | 57.0706 | 44.3324
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 34.8487 | 34.5859 | 33.6851 | 33.4414 | 33.1625 | 32.8751 | 32.6845 | 32.4171 | 32.1587 | 31.9738 | 31.6298 | 31.2289 | 30.9092 | 30.6344 | 28.7125 | 27.5598 | 24.6968
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 34.8487 | 34.4952 | 33.4413 | 32.8087 | 32.1746 | 31.5282 | 30.9906 | 30.3623 | 29.7331 | 31.3068 | 30.6293 | 29.8492 | 29.1352 | 28.4451 | 23.5205 | 18.3615 | 11.3166
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 34.8487 | 34.8307 | 34.5147 | 33.6662 | 33.5487 | 33.4469 | 33.3876 | 33.278 | 33.1133 | 32.9398 | 32.7028 | 32.4807 | 32.2282 | 32.1232 | 32.2346 | 34.1575 | 34.0277
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 34.8487 | 34.4883 | 33.408 | 32.7421 | 32.0978 | 30.9127 | 30.3663 | 29.8001 | 29.1975 | 28.6612 | 27.9924 | 27.2784 | 26.4834 | 25.2022 | 21.0679 | 15.9692 | 8.0369
Lea Marston 132kV | TAMWORTH GRID 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 34.8487 | 34.5721 | 33.6247 | 33.3908 | 33.0924 | 32.7738 | 32.5192 | 32.1897 | 31.7915 | 33.561 | 33.0747 | 32.6386 | 32.1986 | 31.8067 | 30.0471 | 28.1985 | 24.2406
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 55.4966 | 55.1883 | 55.0486 | 54.7461 | 54.4772 | 54.1943 | 53.9428 | 53.6276 | 53.3131 | 53.1084 | 52.1369 | 51.7524 | 51.3368 | 51.0251 | 49.4634 | 45.9313 | 40.9234
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 55.4966 | 55.079 | 54.7842 | 54.0665 | 53.4412 | 52.9781 | 51.9755 | 51.2935 | 50.5406 | 49.7933 | 49.0182 | 48.0475 | 47.132 | 46.3208 | 41.6841 | 34.9956 | 26.7482
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 55.4966 | 55.3718 | 55.1145 | 55.0126 | 54.9393 | 54.8556 | 54.7575 | 54.6313 | 54.4406 | 54.2053 | 53.9329 | 53.6643 | 53.3734 | 53.2607 | 53.3731 | 53.4137 | 50.9561
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 55.4966 | 55.0639 | 54.7321 | 53.9705 | 53.3237 | 52.3193 | 51.8339 | 51.2303 | 50.5544 | 49.9078 | 49.1388 | 48.2444 | 47.2157 | 46.1578 | 40.158 | 32.4631 | 23.5018
Lea Marston 132kV | TAMWORTH TOWN 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 55.4966 | 55.159 | 54.9777 | 54.6543 | 54.3369 | 53.9559 | 53.5852 | 53.2057 | 52.2205 | 51.76 | 51.147 | 50.4873 | 49.7617 | 49.3177 | 47.3269 | 43.4258 | 38.3205
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 49.2517 | 49.2102 | 49.1369 | 49.0057 | 48.8928 | 48.8471 | 48.7627 | 48.6254 | 48.4562 | 48.1994 | 47.9045 | 47.6058 | 47.2647 | 47.0207 | 46.2624 | 44.2453 | 42.6444
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 49.2517 | 49.1818 | 49.0681 | 48.8296 | 48.6169 | 48.4606 | 48.2773 | 48.0744 | 47.8675 | 47.5126 | 47.1306 | 46.7055 | 46.234 | 45.8728 | 43.8392 | 41.5443 | 38.9745
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 49.2517 | 49.2137 | 49.1609 | 49.1034 | 49.0715 | 49.1175 | 49.1233 | 49.0846 | 49.0168 | 48.8493 | 48.6309 | 48.403 | 48.096 | 47.9116 | 47.603 | 47.1201 | 46.463
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 49.2517 | 49.1781 | 49.0549 | 48.8048 | 48.5855 | 48.4837 | 48.3215 | 48.1891 | 48.0332 | 47.7759 | 47.4234 | 47.0196 | 46.5323 | 46.0712 | 43.6041 | 41.1358 | 38.8219
Lea Marston 132kV | TAMWORTH TOWN 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 49.2517 | 49.2075 | 49.1347 | 49.0295 | 48.9365 | 48.8863 | 48.8012 | 48.6748 | 48.4972 | 48.1334 | 47.7294 | 47.3471 | 46.8667 | 46.593 | 45.8082 | 43.8634 | 42.2598
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 17.6039 | 17.5766 | 17.5469 | 17.4773 | 17.4053 | 17.2323 | 16.9967 | 16.626 | 15.9951 | 15.1839 | 14.2243 | 13.2211 | 12.041 | 11.0492 | 7.8221 | 3.0361 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 17.6039 | 17.5403 | 17.4596 | 17.2786 | 17.0971 | 16.8146 | 16.4701 | 15.9922 | 15.2532 | 14.3212 | 13.2487 | 12.129 | 10.8242 | 9.7062 | 5.7593 | 0.24172 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 17.6039 | 17.573 | 17.5423 | 17.5129 | 17.4751 | 17.4207 | 17.3419 | 17.1932 | 16.9156 | 16.4597 | 15.8592 | 15.2171 | 14.3911 | 13.8469 | 13.0345 | 11.8374 | 10.3891
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 17.6039 | 17.5382 | 17.4514 | 17.2645 | 17.0812 | 16.8291 | 16.5681 | 16.2889 | 15.8125 | 15.2801 | 14.4671 | 13.4538 | 12.1511 | 10.8273 | 6.1426 | 0.76603 | 0
Lea Marston 132kV | WOOD END 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 17.6039 | 17.5596 | 17.51 | 17.4381 | 17.3547 | 17.2239 | 17.0341 | 16.6832 | 16.0257 | 15.1383 | 14.0952 | 13.0742 | 11.8382 | 11.0806 | 9.1361 | 6.1487 | 2.4063
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.9952 | 24.9178 | 24.8203 | 24.582 | 24.3494 | 24.1068 | 23.8994 | 23.6783 | 23.5077 | 23.3606 | 23.2089 | 23.0146 | 22.9002 | 22.7838 | 21.833 | 19.3652 | 16.8995
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.9952 | 24.8612 | 24.6872 | 24.2563 | 23.8433 | 23.4347 | 23.0572 | 22.6777 | 22.3468 | 22.0656 | 21.871 | 20.1937 | 20.1164 | 19.9762 | 18.1547 | 15.1103 | 11.3233
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.9952 | 24.9457 | 24.8963 | 24.8465 | 24.7893 | 24.7259 | 24.6585 | 24.6065 | 24.5438 | 24.4895 | 24.4492 | 24.4287 | 24.4264 | 24.4469 | 24.7442 | 24.8588 | 24.295
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.9952 | 24.8538 | 24.6579 | 24.2073 | 23.7851 | 23.3549 | 22.9577 | 22.5901 | 22.2498 | 21.9723 | 20.2026 | 20.1607 | 20.0334 | 19.8309 | 17.4982 | 14.0598 | 9.5131
Ratcliffe 132kV | BEESTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.9952 | 24.9157 | 24.8169 | 24.6602 | 24.478 | 24.2652 | 24.0652 | 23.88 | 23.699 | 23.5349 | 23.3904 | 23.2709 | 23.1808 | 23.1193 | 22.5054 | 20.2579 | 18.8759
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.7045 | 20.6081 | 20.4771 | 20.152 | 18.896 | 18.8195 | 18.6709 | 18.4586 | 18.224 | 17.9985 | 17.7394 | 17.4238 | 17.1422 | 16.8387 | 14.7932 | 11.8235 | 8.0096
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.7045 | 20.6066 | 20.4735 | 20.1613 | 18.8975 | 18.8228 | 18.6806 | 18.4846 | 18.2726 | 18.0723 | 17.8694 | 17.6057 | 17.3791 | 17.1413 | 15.3572 | 12.6541 | 9.4114
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.7045 | 20.6708 | 20.6325 | 20.5971 | 20.5506 | 20.5337 | 20.4832 | 20.4344 | 20.3789 | 20.332 | 20.2935 | 20.2678 | 20.2553 | 20.2528 | 20.3514 | 20.3805 | 18.7256
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.7045 | 20.6008 | 20.4534 | 20.1247 | 18.8912 | 18.8065 | 18.6461 | 18.4425 | 18.2132 | 17.9834 | 17.7398 | 17.4874 | 17.2199 | 16.9212 | 14.6756 | 11.6444 | 0
Ratcliffe 132kV | BILBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.7045 | 20.6471 | 20.5721 | 20.458 | 20.3198 | 20.1979 | 20.0463 | 18.879 | 18.851 | 18.8116 | 18.7657 | 18.7202 | 18.6778 | 18.6457 | 18.2559 | 17.1683 | 15.6423
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.0532 | 5.9943 | 5.9738 | 6.0237 | 6.0844 | 6.1831 | 6.2084 | 6.2299 | 6.2607 | 6.2856 | 6.3176 | 6.3602 | 6.3867 | 2.9776 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.0532 | 5.9849 | 5.9404 | 5.9493 | 5.9688 | 6.0295 | 6.0335 | 6.0342 | 6.0486 | 4.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.0532 | 5.9988 | 5.9884 | 6.0519 | 6.1143 | 6.2361 | 6.2608 | 6.2741 | 6.2784 | 6.2881 | 6.3009 | 6.321 | 6.3371 | 6.3646 | 6.4203 | 3.3514 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.0532 | 5.9833 | 5.9365 | 5.9516 | 5.9693 | 6.0922 | 6.1179 | 6.1487 | 6.1735 | 6.2027 | 4.785 | 0.95902 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.0532 | 5.9934 | 5.9629 | 6.0169 | 6.0766 | 6.1724 | 6.1959 | 6.2114 | 6.2291 | 6.2376 | 6.2535 | 5.5316 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.5451 | 11.7645 | 11.7954 | 10.9537 | 10.0951 | 8.4243 | 7.5231 | 6.3309 | 4.883 | 3.3091 | 1.4082 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.5451 | 10.9554 | 11.0011 | 10.1432 | 9.2796 | 8.1177 | 6.9409 | 5.4274 | 3.4936 | 1.3059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.5451 | 11.8429 | 12.0821 | 12.3227 | 12.4325 | 11.7551 | 11.8527 | 11.8143 | 11.5629 | 11.091 | 10.4577 | 9.7935 | 8.9273 | 8.3546 | 7.9714 | 6.7936 | 3.4817
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.5451 | 10.9668 | 10.9283 | 10.097 | 9.2448 | 8.223 | 7.1671 | 5.9965 | 4.3385 | 2.6229 | 0.41298 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | BRUSH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.5451 | 11.8734 | 12.1248 | 11.2918 | 11.0909 | 10.7126 | 10.3363 | 9.7046 | 8.5696 | 7.1467 | 5.5409 | 3.9678 | 2.147 | 0.87522 | 0 | 0 | 0
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 41.1504 | 41.0913 | 40.9732 | 40.6847 | 40.4366 | 40.2173 | 40.066 | 39.9829 | 39.8625 | 39.7388 | 39.6079 | 39.479 | 39.3864 | 39.2977 | 38.4763 | 37.1701 | 33.5041
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 41.1504 | 41.0921 | 40.9818 | 40.7172 | 40.48 | 40.2683 | 40.1227 | 40.0364 | 39.9389 | 39.8244 | 39.7055 | 39.5289 | 39.421 | 39.3193 | 38.5593 | 37.3103 | 31.3493
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 41.1504 | 41.1096 | 41.0435 | 40.9464 | 40.8866 | 40.8473 | 40.8224 | 40.851 | 40.8513 | 40.8382 | 40.8366 | 40.8459 | 40.8767 | 40.9198 | 41.2879 | 41.6163 | 41.4143
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 41.1504 | 41.0878 | 40.9597 | 40.6734 | 40.426 | 40.2062 | 40.0497 | 39.9821 | 39.87 | 39.7409 | 39.6133 | 39.5069 | 39.4201 | 39.334 | 38.3905 | 37.0506 | 11.9846
Ratcliffe 132kV | CASTLE ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 41.1504 | 41.1119 | 41.0317 | 40.8938 | 40.7587 | 40.6354 | 40.5463 | 40.5355 | 40.4848 | 40.4067 | 40.3456 | 40.3098 | 40.2984 | 40.3199 | 40.3502 | 39.7474 | 38.7256
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.1216 | 14.0668 | 14.0058 | 13.8694 | 13.7266 | 13.5818 | 13.4648 | 13.3371 | 13.2515 | 13.1901 | 13.128 | 13.03 | 13.0058 | 12.9828 | 12.5055 | 9.4278 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.1216 | 14.0036 | 13.855 | 13.487 | 13.1354 | 12.794 | 12.468 | 12.1248 | 11.8119 | 11.5281 | 11.2586 | 10.9486 | 10.6981 | 10.45 | 4.619 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.1216 | 14.0799 | 14.0377 | 13.9932 | 13.9378 | 13.8821 | 13.8261 | 13.7755 | 13.7182 | 13.6705 | 13.6324 | 13.6101 | 13.6021 | 13.6112 | 13.8227 | 13.9153 | 13.4284
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.1216 | 13.9955 | 13.8296 | 13.4432 | 13.083 | 12.7226 | 12.3735 | 12.0393 | 11.7126 | 11.4156 | 11.121 | 10.8402 | 10.5582 | 10.2544 | 2.2954 | 0 | 0
Ratcliffe 132kV | CHILWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.1216 | 14.0522 | 13.9682 | 13.8325 | 13.6746 | 13.5001 | 13.3287 | 13.1645 | 13.0098 | 12.8726 | 12.75 | 12.6542 | 12.5803 | 12.5373 | 12.0496 | 18.7664 | 12.3011
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.7992 | 22.5295 | 22.3346 | 21.908 | 21.5018 | 21.0871 | 20.7071 | 20.3204 | 19.9865 | 19.7181 | 19.452 | 19.118 | 18.8926 | 18.7195 | 14.9525 | 11.0904 | 5.501
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.7992 | 22.4963 | 22.2446 | 21.717 | 21.2131 | 20.7195 | 20.2556 | 19.7868 | 19.3914 | 19.0931 | 18.8639 | 16.0561 | 16.0329 | 15.9529 | 13.7934 | 9.4528 | 3.8567
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.7992 | 22.6061 | 22.5211 | 22.4607 | 22.3941 | 22.3223 | 22.2478 | 22.1756 | 22.0938 | 22.0346 | 21.9986 | 21.9728 | 21.9724 | 21.9944 | 22.3009 | 22.5349 | 21.6586
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.7992 | 22.4844 | 22.2049 | 21.6509 | 21.1311 | 20.6205 | 20.1331 | 19.6802 | 19.2682 | 18.9606 | 18.7635 | 16.0279 | 15.9645 | 15.7792 | 12.7083 | 7.6696 | 0.86286
Ratcliffe 132kV | CLIFTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.7992 | 22.5653 | 22.4078 | 22.2196 | 22.005 | 21.7519 | 21.5088 | 21.279 | 21.0649 | 20.8925 | 20.7559 | 20.628 | 20.5411 | 20.5022 | 19.7857 | 16.2157 | 14.2854
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 10.0793 | 9.934 | 9.8697 | 9.8178 | 9.7079 | 9.5794 | 9.442 | 9.3082 | 9.001 | 8.5156 | 7.8991 | 7.2496 | 6.4158 | 5.8268 | 4.3477 | 1.9741 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 10.0793 | 9.8902 | 9.7631 | 9.5266 | 9.25 | 8.7884 | 8.2387 | 7.5597 | 6.4739 | 5.13 | 3.5981 | 2.0053 | 0.1708 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 10.0793 | 10.0497 | 9.9205 | 9.9409 | 9.9078 | 9.8572 | 9.7817 | 9.6665 | 9.388 | 8.929 | 8.3267 | 7.6905 | 6.876 | 6.3175 | 5.5438 | 4.2967 | 2.634
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 10.0793 | 9.8876 | 9.7495 | 9.5077 | 9.227 | 8.837 | 8.4315 | 8.0462 | 7.3318 | 6.5493 | 5.3956 | 3.9801 | 2.1833 | 0 | 0 | 0 | 0
Ratcliffe 132kV | COTGRAVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 10.0793 | 9.9317 | 9.8625 | 9.8173 | 9.7005 | 9.5264 | 9.2947 | 8.9416 | 8.1838 | 7.1803 | 6.0153 | 4.8791 | 3.509 | 2.5886 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | EAST LEAKE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.0536 | 11.9427 | 11.8598 | 11.7466 | 11.4076 | 11.3887 | 11.2798 | 10.9731 | 10.5682 | 9.9176 | 9.0944 | 8.2176 | 7.0774 | 2.9176 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.0536 | 11.8697 | 11.6697 | 11.2423 | 10.8239 | 10.1575 | 9.2931 | 8.1438 | 6.6363 | 4.8142 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.0536 | 11.9679 | 11.9317 | 11.9394 | 11.9602 | 12.0105 | 11.9367 | 11.4233 | 11.369 | 10.9143 | 10.1932 | 9.4217 | 8.4179 | 7.7274 | 6.814 | 3.2839 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.0536 | 11.8647 | 11.6495 | 11.2016 | 10.7668 | 10.2388 | 9.5129 | 8.6858 | 7.5584 | 6.346 | 4.6537 | 0.93971 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | KEYWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.0536 | 11.9393 | 11.8415 | 11.7406 | 11.4072 | 11.3708 | 11.0539 | 10.4548 | 9.5002 | 8.2568 | 6.8085 | 5.3798 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0386 | 15.0016 | 14.9581 | 14.8864 | 14.8495 | 14.8177 | 14.7563 | 14.6933 | 14.6316 | 14.5735 | 14.5125 | 14.444 | 14.3825 | 14.321 | 13.9405 | 13.403 | 12.7364
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0386 | 15.0014 | 14.9576 | 14.8893 | 14.8547 | 14.8132 | 14.7543 | 14.6953 | 14.6399 | 14.587 | 14.5352 | 14.4741 | 14.4284 | 14.3821 | 14.0373 | 19.9833 | 19.4064
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0386 | 15.009 | 14.978 | 14.9466 | 14.9395 | 14.9337 | 14.9063 | 14.8799 | 14.8517 | 14.8233 | 14.7997 | 14.7769 | 14.7552 | 14.7357 | 14.6603 | 14.5731 | 14.4026
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0386 | 15.0005 | 14.9544 | 14.8834 | 14.8467 | 14.8152 | 14.7529 | 14.6954 | 14.6361 | 14.5793 | 14.5232 | 14.4681 | 14.4111 | 14.3536 | 20.417 | 19.8464 | 9.5704
Ratcliffe 132kV | LENTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0386 | 15.0055 | 14.969 | 14.9273 | 14.9168 | 14.8957 | 14.8531 | 14.8112 | 14.7712 | 14.7332 | 14.6958 | 14.6594 | 14.6294 | 14.6029 | 14.4441 | 20.6035 | 20.2331
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 28.0933 | 27.8137 | 27.6825 | 27.1396 | 26.5672 | 25.9675 | 25.4089 | 24.7284 | 24.0776 | 23.4689 | 22.7949 | 21.9125 | 21.1672 | 20.5425 | 16.6184 | 9.376 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 28.0933 | 27.731 | 27.4661 | 26.5498 | 25.5837 | 24.5439 | 23.471 | 22.1909 | 20.8301 | 19.5016 | 18.126 | 16.4474 | 14.8489 | 13.475 | 4.5936 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 28.0933 | 27.9758 | 27.8352 | 27.7126 | 27.5728 | 27.4311 | 27.2822 | 27.1074 | 26.882 | 26.6402 | 26.3778 | 26.119 | 25.8313 | 25.6413 | 25.674 | 25.5115 | 23.81
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 28.0933 | 27.721 | 27.4125 | 26.4466 | 25.4437 | 24.36 | 23.2291 | 22.007 | 20.6401 | 19.3328 | 17.8711 | 16.2672 | 14.5109 | 12.9123 | 2.2827 | 0 | 0
Ratcliffe 132kV | LONG EATON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 28.0933 | 27.8372 | 27.7273 | 27.3957 | 26.9886 | 26.504 | 26.0073 | 25.4228 | 24.7528 | 24.0845 | 23.4027 | 22.7335 | 22.0401 | 21.6137 | 19.0738 | 19.0274 | 12.2335
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 32.6071 | 32.3214 | 32.345 | 32.0775 | 31.6838 | 31.2916 | 30.921 | 30.5225 | 30.1439 | 29.8039 | 29.4449 | 29.0325 | 28.6749 | 28.3105 | 25.8376 | 22.1469 | 17.3557
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.6071 | 32.3154 | 32.3381 | 32.0448 | 31.631 | 31.2333 | 30.8475 | 30.4526 | 30.0948 | 29.7799 | 29.4739 | 29.0665 | 28.7358 | 28.3924 | 25.9334 | 21.9272 | 17.6072
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.6071 | 32.5413 | 32.4727 | 32.5349 | 32.4654 | 32.3953 | 32.3243 | 32.2573 | 32.1823 | 32.116 | 32.063 | 32.0281 | 32.011 | 31.9959 | 32.1731 | 32.2295 | 31.5773
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.6071 | 32.3067 | 32.2985 | 32.0052 | 31.5848 | 31.1679 | 30.7636 | 30.3734 | 29.9943 | 29.6254 | 29.2516 | 28.8874 | 28.515 | 28.1205 | 24.5018 | 20.3882 | 15.2342
Ratcliffe 132kV | LOUGHBOROUGH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.6071 | 32.361 | 32.4499 | 32.4123 | 32.2159 | 32.0061 | 31.8038 | 31.6064 | 31.4106 | 31.236 | 31.083 | 30.9549 | 30.8546 | 30.7886 | 30.0438 | 28.0649 | 25.8646
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Best View | Headroom (MW) | 11.5676 | 13.3261 | 13.5728 | 6.8005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 11.5676 | 6.8296 | 7.1902 | 0.26578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 11.5676 | 13.9543 | 15.872 | 17.7998 | 18.6809 | 13.2362 | 14.0135 | 13.6954 | 11.6559 | 7.8293 | 2.6881 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 11.5676 | 6.9213 | 6.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | LOUGHBOROUGH 132kV S STN (M32) | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 11.5676 | 14.199 | 16.2135 | 9.5222 | 7.8958 | 4.8338 | 1.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.5387 | 19.4709 | 16.5366 | 16.4549 | 16.2326 | 15.8651 | 15.273 | 14.7381 | 14.1711 | 13.51 | 12.7174 | 11.8391 | 7.6249 | 2.9138 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.5387 | 19.4706 | 16.5363 | 16.4634 | 16.2675 | 15.9025 | 15.3831 | 14.8592 | 14.2571 | 8.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.5387 | 19.5151 | 19.4615 | 19.4448 | 19.4337 | 19.4222 | 19.4063 | 19.3856 | 19.3641 | 16.6221 | 16.5689 | 16.4614 | 16.2631 | 15.5097 | 11.5712 | 3.2796 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.5387 | 19.47 | 16.5353 | 16.4449 | 16.2192 | 15.8575 | 15.2773 | 14.8387 | 14.3212 | 13.7253 | 9.7744 | 0.93848 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | MOUNTSORREL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.5387 | 19.4769 | 19.4529 | 16.5514 | 16.5562 | 16.5172 | 16.4055 | 16.2445 | 15.9619 | 15.5017 | 13.9239 | 6.575 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 40.3652 | 40.4225 | 40.4465 | 40.2958 | 40.1736 | 40.1084 | 40.0415 | 39.8487 | 39.7138 | 39.5843 | 39.4176 | 39.2261 | 39.0643 | 38.9045 | 37.8605 | 36.3782 | 34.8258
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 40.3652 | 40.4066 | 40.4327 | 40.2628 | 40.1316 | 40.0177 | 39.9333 | 39.7434 | 39.6211 | 39.5083 | 39.3663 | 39.1726 | 39.0171 | 38.8488 | 37.7253 | 36.1075 | 31.387
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 40.3652 | 40.3978 | 40.422 | 40.3951 | 40.3744 | 40.3881 | 40.4055 | 40.3438 | 40.2962 | 40.2557 | 40.2047 | 40.1607 | 40.1214 | 40.0825 | 39.9299 | 39.7036 | 39.2082
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 40.3652 | 40.4148 | 40.4256 | 40.2627 | 40.1287 | 40.0517 | 39.9729 | 39.7849 | 39.6493 | 39.5029 | 39.3221 | 39.1442 | 38.9662 | 38.7818 | 37.4468 | 35.816 | 11.999
Ratcliffe 132kV | NORTH WILFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 40.3652 | 40.4196 | 40.4688 | 40.3971 | 40.3441 | 40.2967 | 40.2801 | 40.1551 | 40.0715 | 39.9884 | 39.8766 | 39.7792 | 39.6931 | 39.6204 | 39.0779 | 38.1195 | 37.0427
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 75.6787 | 74.6899 | 73.5261 | 71.619 | 68.9267 | 58.7806 | 47.6695 | 35.7116 | 23.1581 | 9.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 75.6787 | 74.6861 | 73.5116 | 71.6924 | 61.108 | 45.1745 | 28.4276 | 10.1963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 75.6787 | 74.8829 | 74.0453 | 73.1925 | 72.9705 | 72.7816 | 72.0255 | 71.2907 | 70.5082 | 69.7212 | 69.0554 | 64.3727 | 57.8604 | 53.7132 | 54.0169 | 48.2411 | 19.0276
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 75.6787 | 74.6619 | 73.4289 | 71.5387 | 59.4105 | 43.4785 | 26.9639 | 11.3788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | NOTTINGHAM 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 75.6787 | 74.7924 | 73.8092 | 72.6882 | 72.3759 | 71.7852 | 67.1468 | 59.9082 | 49.5383 | 36.0956 | 21.6139 | 8.0762 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.5636 | 11.7587 | 11.5634 | 10.9713 | 10.1113 | 8.4379 | 7.5352 | 6.3411 | 4.8908 | 3.3144 | 1.4104 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.5636 | 10.973 | 11.0187 | 10.1595 | 9.2945 | 8.1307 | 6.952 | 5.4361 | 3.4992 | 1.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.5636 | 11.8619 | 11.8194 | 11.7937 | 11.7633 | 11.7285 | 11.674 | 11.5704 | 11.3758 | 11.0741 | 10.4745 | 9.8092 | 8.9416 | 8.368 | 7.9842 | 6.8045 | 3.4873
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.5636 | 10.9844 | 10.9459 | 10.1132 | 9.2596 | 8.2362 | 7.1786 | 6.0061 | 4.3454 | 2.6271 | 0.41365 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | QUORN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.5636 | 11.8234 | 11.7145 | 11.3099 | 11.1087 | 10.7298 | 10.3529 | 9.7202 | 8.5834 | 7.1582 | 5.5498 | 3.9742 | 2.1504 | 0.87662 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.5214 | 11.7403 | 11.7711 | 10.9312 | 10.0744 | 8.407 | 7.5076 | 6.3179 | 4.8729 | 3.3023 | 1.4053 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.5214 | 10.9329 | 10.9785 | 10.1223 | 9.2605 | 8.101 | 6.9266 | 5.4162 | 3.4864 | 1.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.5214 | 11.8185 | 12.0573 | 12.2973 | 12.407 | 11.731 | 11.8283 | 11.79 | 11.5391 | 11.0682 | 10.4362 | 9.7734 | 8.909 | 8.3374 | 7.955 | 6.7797 | 3.4746
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.5214 | 10.9443 | 10.9059 | 10.0762 | 9.2258 | 8.2061 | 7.1524 | 5.9842 | 4.3296 | 2.6175 | 0.41213 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SHEPSHED 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.5214 | 11.849 | 12.0998 | 11.2686 | 11.0681 | 10.6906 | 10.3151 | 9.6846 | 8.552 | 7.132 | 5.5295 | 3.9596 | 2.1426 | 0.87342 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SNEINTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.4101 | 8.3354 | 8.3731 | 8.3791 | 8.3878 | 8.2902 | 8.1714 | 7.9324 | 7.4792 | 6.6442 | 5.5417 | 4.3936 | 2.91 | 1.9054 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.4101 | 8.3299 | 8.3513 | 8.8339 | 8.8146 | 8.4458 | 8.087 | 7.3522 | 6.0265 | 4.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.4101 | 8.3368 | 8.3444 | 8.2749 | 8.2189 | 8.0832 | 7.9118 | 7.6214 | 7.1052 | 6.2256 | 5.0567 | 3.7964 | 2.1898 | 1.0576 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.4101 | 8.329 | 8.3585 | 8.8358 | 8.8178 | 8.5923 | 8.3596 | 8.0769 | 7.4094 | 6.5515 | 5.1122 | 0.93857 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SOUTH CROXTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.4101 | 8.3234 | 8.3382 | 8.2755 | 8.2226 | 8.0718 | 7.7981 | 7.2146 | 6.0628 | 4.4135 | 2.4154 | 0.48084 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.2011 | 20.2152 | 20.2267 | 20.0992 | 19.9709 | 19.863 | 19.7951 | 19.7 | 19.619 | 19.5413 | 19.45 | 19.3419 | 19.2551 | 19.1654 | 18.663 | 17.0267 | 15.9306
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.2011 | 20.2086 | 20.2051 | 20.085 | 19.9625 | 19.8547 | 19.7836 | 19.6919 | 19.6176 | 19.5492 | 19.4766 | 19.3704 | 19.2894 | 19.2031 | 18.7319 | 17.1591 | 16.2614
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.2011 | 20.2149 | 20.2316 | 20.2046 | 20.1808 | 20.1686 | 20.1725 | 20.1644 | 20.1536 | 20.141 | 20.128 | 20.1183 | 20.1111 | 20.1059 | 20.15 | 20.1711 | 20.0039
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.2011 | 20.2137 | 20.2201 | 20.0934 | 19.9655 | 19.8565 | 19.7852 | 19.6965 | 19.6183 | 19.5371 | 19.4505 | 19.3645 | 19.2813 | 19.1948 | 18.6634 | 17.0266 | 7.8875
Ratcliffe 132kV | ST ANNS 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.2011 | 20.2171 | 20.2308 | 20.1776 | 20.1172 | 20.0618 | 20.033 | 19.9877 | 19.9465 | 19.9028 | 19.8595 | 19.821 | 19.7893 | 19.7667 | 19.5856 | 19.1545 | 18.6831
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 24.0055 | 23.9884 | 23.7784 | 23.4596 | 23.1193 | 22.9258 | 22.5727 | 22.0526 | 21.2325 | 20.1654 | 18.7036 | 14.2194 | 7.5951 | 2.9024 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 24.0055 | 23.9652 | 23.7333 | 21.9411 | 21.5609 | 21.0028 | 20.301 | 19.2779 | 15.9589 | 8.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 24.0055 | 24.0881 | 23.9913 | 24.1697 | 24.2956 | 24.5121 | 24.6469 | 24.5881 | 24.2537 | 23.6107 | 22.6868 | 21.6617 | 18.9344 | 15.4491 | 11.526 | 3.2668 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 24.0055 | 23.9669 | 23.7105 | 21.935 | 21.559 | 21.2486 | 20.7963 | 20.3742 | 19.4117 | 16.7146 | 9.7362 | 0.93481 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | SYSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 24.0055 | 24.0407 | 23.923 | 23.9734 | 23.9651 | 23.8977 | 23.7153 | 23.1993 | 22.0086 | 20.3676 | 13.8695 | 6.5493 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.8471 | 22.7935 | 22.7288 | 22.6681 | 22.5737 | 22.5122 | 22.4762 | 22.4469 | 22.4221 | 22.3969 | 22.3792 | 22.3592 | 22.3482 | 22.3398 | 22.0485 | 21.4314 | 20.5952
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.8471 | 22.7955 | 22.7384 | 22.6736 | 22.5771 | 22.5107 | 22.4738 | 22.4322 | 22.4117 | 22.4055 | 22.3971 | 22.35 | 22.3441 | 22.3326 | 22.0758 | 21.4542 | 20.6094
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.8471 | 22.7983 | 22.749 | 22.7315 | 22.6879 | 22.6614 | 22.6402 | 22.6271 | 22.6079 | 22.5938 | 22.5899 | 22.5925 | 22.605 | 22.624 | 22.8409 | 23.0683 | 22.9866
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.8471 | 22.7925 | 22.7251 | 22.6648 | 22.5702 | 22.5043 | 22.4639 | 22.4378 | 22.4128 | 22.3843 | 22.3651 | 22.3536 | 22.3439 | 22.3251 | 21.9594 | 21.3093 | 7.8788
Ratcliffe 132kV | TALBOT ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.8471 | 22.796 | 22.7419 | 22.715 | 22.6494 | 22.6018 | 22.5691 | 22.54 | 22.5106 | 22.4927 | 22.4865 | 22.4921 | 22.5184 | 22.5543 | 22.6682 | 22.3882 | 21.8614
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.8636 | 22.8028 | 22.9421 | 22.7434 | 22.5311 | 22.3119 | 22.1556 | 21.9294 | 21.7698 | 21.6946 | 21.625 | 21.4469 | 21.1609 | 20.5364 | 16.6134 | 9.3731 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.8636 | 22.7065 | 22.6912 | 22.1575 | 21.65 | 21.1683 | 20.7673 | 20.3486 | 20.0353 | 19.4957 | 18.1205 | 16.0244 | 14.8445 | 13.471 | 4.5922 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.8636 | 22.8857 | 22.8934 | 22.8611 | 22.8116 | 22.7701 | 22.7334 | 22.672 | 22.5977 | 22.557 | 22.5377 | 22.5238 | 22.5266 | 22.5436 | 22.829 | 22.9716 | 22.1219
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.8636 | 22.7094 | 22.6604 | 22.1095 | 21.5928 | 21.101 | 20.6815 | 20.2841 | 19.9742 | 19.327 | 16.0463 | 15.9723 | 14.5065 | 12.9085 | 2.2821 | 0 | 0
Ratcliffe 132kV | TOTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.8636 | 22.7875 | 22.8789 | 22.7028 | 22.4791 | 22.2288 | 22.0147 | 21.7633 | 21.5203 | 21.3523 | 21.2205 | 21.0787 | 20.968 | 20.9038 | 19.0681 | 16.1693 | 12.2298
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 28.158 | 25.7399 | 24.5622 | 18.8196 | 12.1254 | 4.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 28.158 | 24.933 | 22.3098 | 11.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 28.158 | 27.2016 | 26.0111 | 24.948 | 23.692 | 22.3822 | 20.9656 | 19.2352 | 16.8864 | 14.2778 | 11.364 | 8.4435 | 5.1313 | 3.021 | 4.6838 | 3.8158 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 28.158 | 24.8331 | 21.7225 | 10.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | TOTON 3 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 28.158 | 25.9616 | 25.001 | 21.7125 | 17.2711 | 11.6179 | 5.6382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 41.7718 | 41.6285 | 41.4638 | 41.179 | 41.069 | 40.8325 | 40.7041 | 40.6455 | 40.6198 | 40.5482 | 40.5088 | 40.4641 | 40.648 | 40.5951 | 39.1076 | 36.4329 | 32.5778
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 41.7718 | 41.5056 | 41.174 | 40.3385 | 39.7217 | 38.9998 | 38.4049 | 37.7715 | 37.1715 | 36.6017 | 36.048 | 35.3639 | 34.2669 | 33.9213 | 29.9991 | 24.6896 | 17.8898
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 41.7718 | 41.674 | 41.585 | 41.4994 | 41.5359 | 41.507 | 41.4963 | 41.4868 | 41.4441 | 41.4203 | 41.4175 | 41.44 | 41.4981 | 41.5923 | 42.2151 | 42.3668 | 41.3002
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 41.7718 | 41.4848 | 41.1063 | 40.2256 | 39.5841 | 38.8558 | 38.2234 | 37.6167 | 36.9762 | 36.3529 | 35.7113 | 34.3155 | 34.064 | 33.5283 | 28.9652 | 22.7698 | 14.599
Ratcliffe 132kV | WEST BRIDGFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 41.7718 | 41.6108 | 41.421 | 41.1285 | 40.9666 | 40.64 | 40.3879 | 40.1519 | 39.8875 | 39.6488 | 39.4238 | 39.2069 | 39.0373 | 38.921 | 37.7629 | 35.3964 | 31.8597
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.4216 | 16.3688 | 16.32 | 16.1758 | 16.0302 | 16.6704 | 16.4633 | 16.1191 | 15.5387 | 14.6226 | 13.4264 | 12.129 | 7.6195 | 2.9118 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.4216 | 16.3553 | 16.2855 | 16.0934 | 15.9053 | 15.4349 | 14.8164 | 13.897 | 12.3964 | 8.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.4216 | 16.3991 | 16.3881 | 16.3708 | 16.3407 | 16.278 | 16.1727 | 15.9322 | 15.4415 | 14.6065 | 13.4962 | 12.3068 | 10.7606 | 9.7228 | 8.229 | 3.2773 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.4216 | 16.3562 | 16.2856 | 16.0957 | 15.9102 | 15.5611 | 15.1869 | 14.7805 | 13.9927 | 12.989 | 9.7675 | 0.93782 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.4216 | 16.3817 | 16.3482 | 16.2835 | 16.2018 | 16.0341 | 15.7545 | 15.1559 | 13.9525 | 12.2847 | 10.3271 | 6.5704 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 38.4459 | 32.629 | 28.6003 | 13.8111 | 5.0273 | 3.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 38.4459 | 31.3017 | 25.3051 | 0.044562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 38.4459 | 35.6117 | 32.7641 | 27.4981 | 28.1198 | 29.4539 | 28.3829 | 22.6117 | 9.3668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 38.4459 | 31.2473 | 24.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WILLOUGHBY 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 38.4459 | 33.3183 | 30.5202 | 28.1398 | 24.3139 | 17.7262 | 6.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.4545 | 15.3888 | 15.2054 | 14.7266 | 14.1644 | 13.6216 | 13.1084 | 12.5319 | 11.9645 | 11.4475 | 10.9244 | 10.3237 | 9.8236 | 9.3216 | 6.129 | 1.4025 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.4545 | 15.3734 | 15.1836 | 14.7233 | 14.1901 | 13.6785 | 13.1902 | 12.6709 | 12.1847 | 11.732 | 11.311 | 10.777 | 10.326 | 9.8609 | 6.7847 | 2.22 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.4545 | 15.4596 | 15.411 | 15.39 | 15.3085 | 15.2355 | 15.1648 | 15.0905 | 14.9929 | 14.9054 | 14.8269 | 14.7666 | 14.7275 | 14.7044 | 14.8308 | 14.8678 | 14.1083
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.4545 | 15.379 | 15.1704 | 14.6982 | 14.1402 | 13.6011 | 13.0813 | 12.5588 | 12.0314 | 11.5127 | 11.0144 | 10.5285 | 10.0498 | 9.5528 | 5.8383 | 0.86502 | 0
Ratcliffe 132kV | WOLLATON ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.4545 | 15.4285 | 15.3289 | 15.1926 | 14.9529 | 14.6975 | 14.4516 | 14.1982 | 13.9406 | 13.6944 | 13.4787 | 13.2946 | 13.1357 | 13.0154 | 12.0394 | 9.9521 | 7.3441
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.0928 | 11.1119 | 11.1323 | 11.1556 | 10.9244 | 10.7378 | 10.5091 | 10.2522 | 9.9062 | 9.5311 | 9.1479 | 8.7222 | 8.2823 | 7.8431 | 5.744 | 3.4524 | 4.3081
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.0928 | 11.1243 | 11.164 | 11.2188 | 11.0271 | 10.5641 | 10.2914 | 9.8486 | 9.3615 | 8.8755 | 8.3946 | 7.8855 | 7.3625 | 6.8541 | 4.4455 | 1.8864 | 2.55
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.0928 | 11.1174 | 11.1441 | 11.1739 | 11.1978 | 11.2207 | 11.2443 | 11.2686 | 11.2974 | 11.3306 | 11.3622 | 11.3904 | 11.4104 | 11.4207 | 11.6981 | 12.0837 | 10.7758
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.0928 | 11.1228 | 11.1618 | 11.2189 | 11.0085 | 10.5564 | 10.2482 | 9.81 | 9.2413 | 8.7758 | 8.3135 | 7.8816 | 7.4519 | 7.323 | 4.9166 | 4.8114 | 2.5327
Stalybridge 132kV | FLAGG 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.0928 | 11.1159 | 11.1418 | 11.1761 | 11.1209 | 11.0511 | 10.9943 | 11.008 | 10.6327 | 10.6167 | 10.5437 | 10.445 | 10.3263 | 10.2111 | 9.4819 | 8.6713 | 10.202
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.4691 | 13.3586 | 13.2449 | 13.0536 | 12.7118 | 12.4358 | 10.4923 | 10.2358 | 9.8904 | 9.5158 | 9.1332 | 8.7083 | 8.2691 | 7.8305 | 5.7348 | 3.4469 | 4.3012
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.4691 | 13.3372 | 13.1909 | 12.9536 | 12.5911 | 10.5472 | 10.2749 | 9.8329 | 9.3466 | 8.8613 | 8.3812 | 7.8729 | 7.3507 | 6.8432 | 4.4384 | 1.8834 | 2.5459
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.4691 | 13.3696 | 13.2851 | 13.1945 | 13.1111 | 13.0253 | 12.9398 | 12.8513 | 12.7543 | 12.658 | 12.5675 | 12.4843 | 12.4105 | 12.3473 | 12.1573 | 12.0644 | 10.7586
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.4691 | 13.3383 | 13.1898 | 12.9457 | 12.5728 | 10.5396 | 10.2318 | 9.7943 | 9.2265 | 8.7617 | 8.3002 | 7.869 | 7.44 | 7.3113 | 4.9087 | 4.8037 | 2.5287
Stalybridge 132kV | HINDLOW 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.4691 | 13.3625 | 13.262 | 13.1315 | 12.9213 | 12.7017 | 12.5209 | 12.4058 | 10.6157 | 10.5997 | 10.5269 | 10.4284 | 10.3098 | 10.1948 | 9.4667 | 8.6574 | 10.1857
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BEVERCOTES 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.2644 | 11.2477 | 11.2286 | 11.1795 | 11.1362 | 10.8936 | 9.8567 | 6.3351 | 0.43324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.2644 | 11.2127 | 11.1469 | 10.9982 | 10.856 | 9.8332 | 5.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.2644 | 11.247 | 11.2294 | 11.2189 | 11.2061 | 11.159 | 11.0818 | 10.9049 | 10.5537 | 9.8611 | 4.3566 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.2644 | 11.2108 | 11.1402 | 10.9899 | 10.8489 | 10.5737 | 7.7397 | 4.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | BOTTESFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.2644 | 11.2356 | 11.1997 | 11.1507 | 11.0957 | 10.9649 | 10.7515 | 10.1883 | 3.7112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CARLTON ON TRENT 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.4553 | 19.3003 | 19.1851 | 18.9861 | 14.0338 | 12.2047 | 9.6794 | 6.2212 | 0.42545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.4553 | 19.2875 | 19.1581 | 18.8994 | 12.7504 | 9.6564 | 5.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.4553 | 19.3439 | 19.3121 | 19.2797 | 17.0808 | 17.2867 | 17.0268 | 15.9605 | 13.6667 | 9.6837 | 4.2782 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.4553 | 19.2839 | 19.1446 | 18.877 | 12.6289 | 10.4458 | 7.6004 | 4.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CAYTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.4553 | 19.3217 | 19.2387 | 19.1416 | 16.0248 | 15.0739 | 13.3992 | 10.0051 | 3.6444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0.61636 | 0.90895 | 0.29512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | CHECKERHOUSE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 11.313 | 11.3934 | 11.4101 | 11.5996 | 11.8504 | 11.9392 | 9.6492 | 6.2017 | 0.42412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 11.313 | 11.3799 | 11.3913 | 11.5212 | 11.7437 | 9.6262 | 5.6007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 11.313 | 11.3888 | 11.4284 | 11.6844 | 11.9667 | 12.2192 | 12.4136 | 12.5056 | 12.5237 | 9.6535 | 4.2649 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 11.313 | 11.3875 | 11.3886 | 11.5516 | 11.7684 | 10.4131 | 7.5767 | 4.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | FERNWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 11.313 | 11.4025 | 11.4487 | 11.6897 | 12.0142 | 12.1393 | 12.2192 | 9.9738 | 3.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.49 | 25.3995 | 25.2851 | 25.0263 | 24.7703 | 24.3654 | 23.8778 | 23.2204 | 22.2346 | 21.0549 | 19.6886 | 18.2546 | 12.6376 | 6.1677 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.49 | 25.3988 | 25.2824 | 25.0235 | 24.7677 | 24.365 | 23.8791 | 23.2261 | 22.2459 | 21.0614 | 19.7102 | 18.2914 | 11.0633 | 4.7796 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.49 | 25.4472 | 25.4018 | 25.3505 | 25.3042 | 25.242 | 25.1565 | 25.0081 | 24.7459 | 24.3236 | 23.7719 | 23.1859 | 22.4513 | 21.9281 | 21.1322 | 19.8956 | 18.3279
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.49 | 25.3962 | 25.2699 | 24.9976 | 24.7367 | 24.3747 | 23.9721 | 23.5219 | 22.8335 | 20.1224 | 19.0541 | 17.7353 | 16.18 | 10.5506 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.49 | 25.4294 | 25.3576 | 25.2508 | 25.1287 | 24.952 | 24.7154 | 24.3167 | 23.5979 | 22.6686 | 21.5879 | 20.521 | 19.2693 | 18.3916 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 30.5342 | 30.3372 | 30.2183 | 29.8759 | 29.5871 | 29.1439 | 28.6258 | 27.9358 | 26.9814 | 25.9618 | 24.6167 | 23.1158 | 12.5533 | 6.1265 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 30.5342 | 30.3363 | 30.2139 | 29.8711 | 29.581 | 29.1384 | 28.6214 | 27.9362 | 26.9866 | 25.9633 | 24.6365 | 23.1563 | 10.9895 | 4.7477 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 30.5342 | 30.5247 | 30.3601 | 30.345 | 30.3545 | 30.3683 | 30.3499 | 30.2314 | 30.0259 | 29.7496 | 29.2865 | 28.8083 | 28.102 | 27.6331 | 26.9977 | 25.3721 | 18.737
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 30.5342 | 30.334 | 30.1962 | 29.8442 | 29.5423 | 29.1914 | 28.8001 | 28.3708 | 27.7581 | 27.2006 | 26.1045 | 24.7557 | 22.8916 | 10.4802 | 0 | 0 | 0
Staythorpe 132kV | GRANTHAM SOUTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 30.5342 | 30.3718 | 30.3158 | 30.2099 | 30.133 | 29.9889 | 29.8029 | 29.4325 | 28.777 | 28.0256 | 26.9972 | 25.9816 | 24.5294 | 23.4976 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HALLCROFT RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.8338 | 22.6942 | 22.5506 | 21.6991 | 13.3543 | 12.0503 | 9.557 | 6.1425 | 0.42007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.8338 | 22.5669 | 22.3223 | 20.8974 | 12.5891 | 9.5342 | 5.5472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.8338 | 22.7878 | 22.8241 | 22.7609 | 16.4174 | 16.3777 | 16.3461 | 13.4313 | 13.4154 | 9.5613 | 4.2241 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.8338 | 22.5695 | 22.1969 | 20.8132 | 12.4691 | 10.3137 | 7.5043 | 4.3157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.8338 | 22.7767 | 22.8295 | 22.6561 | 15.8221 | 13.4048 | 13.2298 | 9.8785 | 3.5983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 23.3849 | 19.7324 | 18.716 | 12.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 23.3849 | 18.8339 | 17.1046 | 7.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 23.3849 | 21.0106 | 22.5308 | 25.7931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 23.3849 | 18.8524 | 16.2195 | 6.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | HAWTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 23.3849 | 20.7302 | 21.8574 | 21.4716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.9389 | 16.2119 | 16.123 | 15.8278 | 15.4836 | 15.1164 | 14.7394 | 14.3156 | 13.9073 | 13.5594 | 13.3665 | 12.8964 | 12.4979 | 12.0926 | 9.4687 | 5.7119 | 4.4878
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.9389 | 16.2124 | 16.1235 | 15.8344 | 15.4987 | 15.1446 | 14.7816 | 14.3803 | 13.9925 | 13.6607 | 13.5158 | 13.1001 | 12.7557 | 12.3985 | 9.9129 | 6.3611 | 5.5813
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.9389 | 16.1875 | 16.1745 | 16.1584 | 16.131 | 16.0995 | 16.0666 | 16.0349 | 15.9915 | 15.9544 | 15.981 | 15.9758 | 15.9692 | 15.9742 | 16.1067 | 16.1743 | 15.6137
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.9389 | 16.2247 | 16.1254 | 15.8191 | 15.4582 | 15.0684 | 14.663 | 14.2556 | 13.8418 | 13.4617 | 13.2057 | 12.8302 | 12.4698 | 12.0889 | 9.0957 | 8.7402 | 3.3596
Staythorpe 132kV | KILTON RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.9389 | 16.2384 | 16.1956 | 16.1099 | 15.9906 | 15.8447 | 15.6894 | 15.517 | 15.3369 | 15.1786 | 15.2002 | 15.0767 | 14.9786 | 14.9057 | 14.2944 | 12.7104 | 14.202
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 35.6455 | 35.6426 | 35.6313 | 35.5817 | 35.5077 | 35.3583 | 35.1396 | 34.8162 | 34.3021 | 33.6415 | 32.8563 | 32.0178 | 29.3418 | 28.5024 | 25.4414 | 21.1007 | 17.5134
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 35.6455 | 35.642 | 35.6291 | 35.5755 | 35.4961 | 35.342 | 35.1232 | 34.8002 | 34.2826 | 33.6187 | 32.8397 | 32.0088 | 29.3408 | 28.5062 | 25.4471 | 21.1375 | 17.6532
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 35.6455 | 35.6546 | 35.6635 | 35.6661 | 35.6652 | 35.6587 | 35.6429 | 35.5988 | 35.4919 | 35.2712 | 34.9329 | 34.542 | 34.0197 | 33.6569 | 33.0546 | 32.174 | 31.0739
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 35.6455 | 35.6493 | 35.6467 | 35.5997 | 35.5216 | 35.383 | 35.205 | 34.9983 | 34.6576 | 34.2651 | 33.6729 | 32.923 | 30.2666 | 29.299 | 25.6824 | 21.4455 | 12.6089
Staythorpe 132kV | MANTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 35.6455 | 35.6454 | 35.6414 | 35.6296 | 35.6045 | 35.553 | 35.4653 | 35.2807 | 34.8892 | 34.3148 | 33.6115 | 32.9052 | 31.1964 | 30.6361 | 29.1206 | 26.7864 | 23.8892
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISSON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | MISTERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.5028 | 22.9787 | 22.8332 | 21.9711 | 14.03 | 12.2014 | 9.6768 | 6.2195 | 0.42533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.5028 | 22.8498 | 22.6021 | 21.1593 | 12.7469 | 9.6537 | 5.6168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.5028 | 23.1621 | 23.3805 | 23.8489 | 17.0761 | 17.282 | 17.0221 | 15.9562 | 13.663 | 9.6811 | 4.2771 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.5028 | 22.8524 | 22.4751 | 21.0741 | 12.6254 | 10.4429 | 7.5984 | 4.3698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NEWARK JUNCTION 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.5028 | 23.1219 | 23.2839 | 23.229 | 16.0204 | 15.0698 | 13.3956 | 10.0023 | 3.6434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | NORTH WHEATLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | ORDSALL RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.5253 | 6.4855 | 6.4677 | 6.4375 | 6.4182 | 6.0221 | 5.8236 | 5.4945 | 0.42673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.5253 | 6.4812 | 6.4583 | 6.4202 | 6.0691 | 5.9105 | 5.6116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.5253 | 6.4942 | 6.4882 | 6.4818 | 6.4754 | 6.455 | 6.4252 | 6.0685 | 5.8652 | 5.4113 | 4.2911 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.5253 | 6.4806 | 6.4569 | 6.4194 | 6.0673 | 5.9695 | 5.8223 | 4.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SIBTHORPE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.5253 | 6.4893 | 6.4766 | 6.4565 | 6.4357 | 6.0792 | 6.0194 | 5.728 | 3.6554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 8.6114 | 8.5671 | 8.5064 | 8.329 | 8.3581 | 8.1212 | 7.8894 | 6.2009 | 0.42406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 8.6114 | 8.5629 | 8.4998 | 8.2944 | 8.3007 | 7.97 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 8.6114 | 8.6023 | 8.5968 | 8.5882 | 8.7135 | 8.694 | 8.6614 | 8.5646 | 8.3716 | 8.0523 | 4.2643 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 8.6114 | 8.5616 | 8.4894 | 8.2783 | 8.2804 | 8.0094 | 7.5757 | 4.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SOUTHWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 8.6114 | 8.5902 | 8.5676 | 8.4928 | 8.6063 | 8.479 | 8.3209 | 8.0318 | 3.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | SWINDERBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | TUXFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WESTBOROUGH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WOODBECK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 53.4749 | 47.7596 | 47.1076 | 45.5625 | 43.9917 | 42.2607 | 40.4406 | 38.3411 | 35.9401 | 33.4631 | 31.0643 | 27.9507 | 21.3622 | 18.4879 | 4.9615 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 53.4749 | 47.7617 | 47.1044 | 45.5649 | 44.0056 | 42.3073 | 40.5348 | 38.5078 | 36.167 | 33.7316 | 31.4889 | 28.5495 | 22.1252 | 19.3889 | 6.1548 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 53.4749 | 47.8626 | 47.7173 | 47.4934 | 47.2114 | 46.8986 | 46.5535 | 46.114 | 45.4678 | 44.616 | 43.7532 | 42.763 | 41.5377 | 40.7092 | 39.6236 | 37.8329 | 39.9334
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 53.4749 | 47.8699 | 47.2177 | 45.6023 | 43.9558 | 42.193 | 40.4007 | 38.6104 | 36.5496 | 34.5293 | 32.3735 | 29.6623 | 23.1502 | 20.0351 | 10.9194 | 0 | 0
Staythorpe 132kV | WORKSOP 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 53.4749 | 47.9261 | 47.5274 | 46.9294 | 46.1975 | 45.3302 | 44.3895 | 43.2049 | 41.5909 | 39.7471 | 38.1333 | 36.231 | 32.3925 | 30.9705 | 25.8261 | 22.6298 | 18.1828
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.1519 | 9.8428 | 9.7565 | 9.5753 | 9.3934 | 9.2078 | 9.0206 | 8.8236 | 8.6307 | 8.4601 | 8.276 | 8.0653 | 7.8847 | 7.7096 | 6.6882 | 8.6205 | 13.8974
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.1519 | 9.8455 | 9.761 | 9.5814 | 9.4019 | 9.2217 | 9.0414 | 8.8552 | 8.6748 | 8.5119 | 8.3495 | 8.1631 | 8.0021 | 7.8432 | 6.8316 | 8.8246 | 14.2467
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.1519 | 9.8787 | 9.8426 | 9.8048 | 9.7626 | 9.7202 | 9.6776 | 9.6335 | 9.5835 | 9.5372 | 9.4934 | 9.4542 | 9.4197 | 9.3893 | 9.3493 | 9.3168 | 12.2097
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.1519 | 9.8437 | 9.7533 | 9.5654 | 9.3816 | 9.1935 | 9.0028 | 8.8121 | 8.6179 | 8.4395 | 8.2567 | 8.0674 | 7.8772 | 7.6866 | 9.8112 | 4.3951 | 2.4765
Staythorpe 132kV | WORKSOP WEST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.1519 | 9.8651 | 9.8106 | 9.7325 | 9.6432 | 9.5443 | 9.445 | 9.3438 | 9.2382 | 9.1414 | 9.0576 | 8.9812 | 8.9127 | 8.8544 | 8.4956 | 10.9122 | 10.0664
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.9329 | 16.7307 | 16.4488 | 15.8581 | 15.2666 | 14.6434 | 14.0482 | 13.3673 | 12.7227 | 12.0958 | 11.4274 | 10.6583 | 9.9537 | 9.3812 | 5.0736 | 1.9017 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.9329 | 16.7292 | 16.4412 | 15.7821 | 15.1171 | 14.4069 | 13.7084 | 12.9218 | 12.1514 | 11.427 | 10.6999 | 9.8689 | 9.0841 | 8.4035 | 3.1066 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.9329 | 16.8663 | 16.7932 | 16.7716 | 16.7189 | 16.6592 | 16.5909 | 16.4976 | 16.3716 | 16.2354 | 16.1003 | 15.992 | 15.8589 | 15.8074 | 16.1112 | 18.7576 | 17.5502
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.9329 | 16.7149 | 16.3914 | 15.6934 | 15.0116 | 14.2964 | 13.5939 | 12.8729 | 12.1243 | 11.4271 | 10.6696 | 9.9253 | 9.083 | 7.2713 | 1.6241 | 0 | 0
Stoke Bardolph 132kV | ARNOLD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.9329 | 16.8133 | 16.6519 | 16.4562 | 16.2031 | 15.8851 | 15.57 | 15.2134 | 14.8355 | 14.4727 | 14.1231 | 13.8363 | 13.5153 | 13.3407 | 11.561 | 11.0632 | 7.1409
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 36.5445 | 36.4933 | 36.305 | 35.829 | 35.3687 | 34.8988 | 34.5056 | 34.0638 | 33.6611 | 33.3119 | 32.9332 | 32.486 | 32.2099 | 31.4911 | 28.5446 | 23.8962 | 18.0313
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 36.5445 | 36.4831 | 36.2826 | 35.8148 | 35.3421 | 34.8872 | 34.4888 | 34.0662 | 33.6961 | 33.385 | 33.1031 | 32.7134 | 32.4184 | 32.2044 | 29.2953 | 25.0438 | 11.1925
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 36.5445 | 36.5463 | 36.4707 | 36.3926 | 36.3112 | 36.2268 | 36.1672 | 36.0987 | 36.0226 | 35.9663 | 35.9281 | 35.9108 | 35.9149 | 35.9411 | 36.131 | 36.2349 | 35.4394
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 36.5445 | 36.4825 | 36.2603 | 35.7724 | 35.2868 | 34.802 | 34.3857 | 33.9656 | 33.5606 | 33.1983 | 32.8402 | 32.5122 | 32.242 | 31.5088 | 28.2753 | 23.5582 | 0
Stoke Bardolph 132kV | BULWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 36.5445 | 36.5359 | 36.4108 | 36.226 | 36.0036 | 35.7614 | 35.569 | 35.3675 | 35.1834 | 35.023 | 34.9005 | 34.8092 | 34.7345 | 34.7022 | 33.9618 | 32.2058 | 29.3241
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.2404 | 20.1181 | 19.9646 | 19.5893 | 19.2378 | 18.9628 | 17.0225 | 16.5847 | 16.4467 | 16.2821 | 16.0426 | 15.7003 | 15.4259 | 15.1248 | 12.805 | 8.9282 | 3.7432
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.2404 | 20.0949 | 19.9106 | 19.4858 | 19.1102 | 18.8734 | 16.6053 | 16.454 | 16.2078 | 15.9566 | 15.671 | 15.2879 | 14.9721 | 14.6314 | 11.9431 | 7.859 | 2.7505
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.2404 | 20.1811 | 20.1146 | 20.0401 | 19.9533 | 19.8748 | 19.789 | 19.7172 | 19.6414 | 19.5799 | 19.5219 | 19.4784 | 19.4526 | 19.4407 | 19.5464 | 19.6761 | 18.9713
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.2404 | 20.0847 | 19.8772 | 19.4245 | 19.0462 | 18.8507 | 16.5542 | 16.3454 | 16.0539 | 15.75 | 15.3996 | 15.028 | 14.6476 | 14.2226 | 10.8772 | 6.21 | 0
Stoke Bardolph 132kV | CINDERHILL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.2404 | 20.146 | 20.0318 | 19.8531 | 19.6423 | 19.424 | 19.2015 | 19.0351 | 18.9059 | 18.8273 | 18.7808 | 16.6999 | 16.7075 | 16.7123 | 16.478 | 14.9577 | 12.5308
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.6361 | 2.5378 | 2.3056 | 2.064 | 1.5576 | 1.0626 | 0.61137 | 0.16991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.6361 | 2.5052 | 2.2129 | 1.803 | 1.1358 | 0.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.6361 | 2.6104 | 2.5319 | 2.6931 | 2.6038 | 2.5044 | 2.409 | 2.3203 | 2.2143 | 2.123 | 2.0547 | 2.014 | 1.998 | 1.9928 | 2.3276 | 2.5512 | 1.636
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.6361 | 2.4953 | 2.168 | 1.7579 | 1.0713 | 0.37329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stoke Bardolph 132kV | COLWICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.6361 | 2.5868 | 2.414 | 2.4321 | 2.1305 | 1.7836 | 1.4571 | 1.1431 | 0.84316 | 0.58152 | 0.3468 | 0.17918 | 0.053501 | 0 | 0 | 2.721 | 4.7157
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.4028 | 15.4025 | 15.3103 | 15.1709 | 15.0169 | 14.7735 | 14.173 | 13.4861 | 12.8357 | 12.2032 | 11.5289 | 10.753 | 10.0421 | 9.4645 | 5.1186 | 1.9186 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.4028 | 15.4018 | 15.3075 | 15.1425 | 14.9619 | 14.5349 | 13.8302 | 13.0366 | 12.2594 | 11.5285 | 10.795 | 9.9566 | 9.1648 | 8.4782 | 3.1342 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.4028 | 15.4134 | 15.4231 | 15.4635 | 15.4719 | 15.4815 | 15.4856 | 15.4674 | 15.4271 | 15.3649 | 15.2868 | 15.2137 | 15.0965 | 15.0358 | 15.0671 | 13.8552 | 13.7881
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.4028 | 15.3964 | 15.2903 | 15.1208 | 14.9342 | 14.4234 | 13.7147 | 12.9873 | 12.232 | 11.5287 | 10.7644 | 10.0135 | 9.1637 | 7.3359 | 1.6385 | 0 | 0
Stoke Bardolph 132kV | GEDLING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.4028 | 15.4156 | 15.3816 | 15.3675 | 15.318 | 15.2433 | 15.169 | 15.0597 | 14.917 | 14.6013 | 14.2486 | 13.9592 | 13.6354 | 13.4592 | 11.6637 | 11.1615 | 7.2044
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 37.7704 | 37.5879 | 37.4143 | 36.8938 | 36.4163 | 35.9638 | 35.5649 | 35.1449 | 35.2781 | 35.3076 | 35.3154 | 35.3093 | 35.4182 | 35.5482 | 34.3612 | 28.1213 | 11.7859
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 37.7704 | 37.5883 | 37.4151 | 36.9048 | 36.4302 | 35.9804 | 35.5778 | 35.1684 | 35.3906 | 35.5063 | 35.7636 | 35.9076 | 35.9471 | 35.955 | 32.1611 | 24.0049 | 4.6724
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 37.7704 | 37.6931 | 37.6476 | 37.5979 | 37.5301 | 37.4558 | 37.3865 | 37.3192 | 37.5856 | 37.8385 | 38.1657 | 38.5726 | 39.061 | 39.6294 | 41.9739 | 42.412 | 41.4395
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 37.7704 | 37.5741 | 37.3663 | 36.8349 | 36.3482 | 35.8833 | 35.4594 | 35.0742 | 35.2075 | 35.2194 | 35.2439 | 35.3414 | 35.4562 | 35.5699 | 34.0573 | 23.7828 | 0
Stoke Bardolph 132kV | MAPPERLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 37.7704 | 37.6468 | 37.5533 | 37.3687 | 37.1579 | 36.9179 | 36.6932 | 36.4752 | 36.9316 | 37.2428 | 37.7216 | 38.2068 | 38.5068 | 38.8318 | 39.1145 | 37.4526 | 34.8127
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.3628 | 22.1787 | 21.9696 | 21.4355 | 20.9551 | 20.585 | 18.9103 | 18.7411 | 18.453 | 18.1508 | 17.7995 | 17.3404 | 16.9715 | 16.5865 | 13.8243 | 9.4389 | 3.8696
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.3628 | 22.1789 | 21.9555 | 21.4051 | 20.9083 | 20.5537 | 18.8893 | 18.6662 | 18.3345 | 18.0005 | 17.6593 | 17.2169 | 16.8583 | 16.4751 | 13.4048 | 8.8812 | 3.2741
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.3628 | 22.2992 | 22.2496 | 22.1976 | 22.1268 | 22.052 | 21.9707 | 21.8994 | 21.8194 | 21.7568 | 21.7168 | 21.7008 | 21.7067 | 21.7367 | 22.1564 | 22.4378 | 21.6736
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.3628 | 22.1655 | 21.9149 | 21.3358 | 20.8358 | 20.524 | 18.837 | 18.5628 | 18.1874 | 17.7996 | 17.3911 | 16.9736 | 16.5385 | 16.0534 | 12.2354 | 7.0972 | 0
Stoke Bardolph 132kV | MARLBOROUGH RD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.3628 | 22.2487 | 22.1217 | 21.9238 | 21.692 | 21.4316 | 21.1797 | 20.9537 | 20.753 | 20.6086 | 20.5102 | 20.4613 | 20.4414 | 19.571 | 18.8127 | 17.1221 | 14.4331
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 60.9852 | 60.5912 | 60.0284 | 58.6722 | 57.0753 | 55.4829 | 54.064 | 52.4639 | 51.6523 | 50.7166 | 49.683 | 48.463 | 47.4824 | 46.6891 | 36.5424 | 29.2035 | 11.8114
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 60.9852 | 60.5463 | 59.8928 | 58.3489 | 56.5581 | 54.7476 | 53.0759 | 51.234 | 50.2636 | 49.2188 | 48.3285 | 47.061 | 45.7796 | 44.5925 | 32.3509 | 24.1466 | 4.6825
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 60.9852 | 60.8735 | 60.7463 | 60.8544 | 60.6628 | 60.476 | 60.3196 | 60.1155 | 60.2122 | 60.2736 | 60.4137 | 60.6809 | 60.9982 | 61.4976 | 64.4775 | 65.8588 | 62.8629
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 60.9852 | 60.5204 | 59.7904 | 58.1936 | 56.3463 | 54.5107 | 52.8023 | 51.1078 | 50.0443 | 48.8982 | 47.673 | 46.519 | 45.2586 | 42.5719 | 35.8172 | 23.9231 | 0
Stoke Bardolph 132kV | NOTTINGHAM EAST 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 60.9852 | 60.7665 | 60.4343 | 60.0983 | 59.3514 | 58.4885 | 57.7122 | 56.8686 | 56.7498 | 56.4762 | 56.3986 | 56.4299 | 56.2208 | 56.262 | 52.9011 | 53.1591 | 48.3658
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 48.5831 | 51.4705 | 48.5227 | 48.3184 | 47.89 | 44.5949 | 44.0132 | 43.375 | 42.7755 | 42.2408 | 41.6597 | 40.988 | 40.4405 | 39.8976 | 36.3677 | 31.0208 | 24.1845
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 48.5831 | 48.5627 | 48.5159 | 48.3145 | 47.9172 | 47.453 | 46.9717 | 46.4413 | 45.9446 | 45.4962 | 45.0514 | 44.4572 | 43.963 | 43.4578 | 40.0755 | 34.6141 | 28.697
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 48.5831 | 51.4771 | 48.534 | 48.5098 | 48.4735 | 46.2804 | 46.1997 | 46.1196 | 46.0138 | 45.9213 | 45.8386 | 45.7765 | 45.7173 | 45.6747 | 45.7492 | 45.7731 | 44.8968
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 48.5831 | 51.4705 | 48.5159 | 48.3027 | 47.8709 | 47.3666 | 46.8439 | 46.3118 | 45.789 | 45.2706 | 44.7339 | 44.2178 | 43.7026 | 43.1691 | 38.5571 | 32.8842 | 25.8702
Stoke Bardolph 132kV | NOTTINGHAM NORTH 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 48.5831 | 51.4709 | 48.5359 | 48.493 | 48.3907 | 48.2398 | 48.0641 | 47.8592 | 47.6337 | 47.4111 | 47.1968 | 47.0083 | 46.8523 | 46.7342 | 45.7364 | 43.1703 | 40.1724
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 100.069 | 99.5833 | 98.8574 | 97.0173 | 95.2681 | 93.6783 | 92.4319 | 87.843 | 86.9559 | 85.8058 | 84.4013 | 82.6102 | 81.1569 | 79.6425 | 68.7269 | 52.4616 | 28.2695
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 100.069 | 99.5464 | 98.7566 | 96.8484 | 95.006 | 93.3807 | 92.2253 | 87.6729 | 86.5408 | 85.3002 | 84.0209 | 82.3428 | 80.9739 | 79.5505 | 68.4672 | 52.4096 | 11.207
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 100.069 | 99.9117 | 99.68 | 99.4371 | 99.1472 | 98.8873 | 98.6045 | 98.3403 | 98.0476 | 97.8194 | 97.6479 | 97.5546 | 97.5402 | 97.6012 | 98.5555 | 99.7664 | 96.9957
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 100.069 | 99.5129 | 98.6283 | 96.6099 | 94.717 | 93.0525 | 92.0734 | 87.3745 | 85.995 | 84.5304 | 82.9735 | 81.4132 | 79.824 | 78.0695 | 64.2668 | 46.1018 | 0
Stoke Bardolph 132kV | NOTTINGHAM NORTH 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 100.069 | 99.7793 | 99.3166 | 98.5988 | 97.7458 | 96.8402 | 95.9494 | 95.1359 | 94.3978 | 93.8195 | 93.3569 | 93.0411 | 92.8368 | 92.748 | 87.0882 | 81.0102 | 71.0882
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 6.8342 | 0.077047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 6.8342 | 0.048089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 6.8342 | 6.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 6.8342 | 0.042614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOSTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 6.8342 | 0.6279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.3631 | 20.2207 | 20.0383 | 19.6048 | 19.179 | 18.5579 | 17.5999 | 16.6341 | 14.9517 | 12.8444 | 10.394 | 7.8364 | 4.865 | 2.3974 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.3631 | 20.2195 | 20.0337 | 19.6 | 19.1746 | 18.5568 | 17.601 | 16.6444 | 14.9724 | 12.8592 | 10.4324 | 7.9015 | 4.939 | 2.4732 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.3631 | 20.3092 | 20.2539 | 20.1951 | 20.1338 | 20.05 | 19.9436 | 19.7273 | 19.2969 | 18.6125 | 17.5306 | 16.5917 | 15.3361 | 14.4494 | 13.1175 | 10.8201 | 7.82
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.3631 | 20.215 | 20.0156 | 19.5641 | 19.1352 | 18.5889 | 17.7173 | 17.2639 | 16.3782 | 15.1738 | 13.3278 | 11.0388 | 8.123 | 5.1793 | 0 | 0 | 0
Walpole 132kV | BOURNE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.3631 | 20.2765 | 20.1761 | 20.0171 | 19.8273 | 19.5649 | 19.2287 | 18.6442 | 17.2814 | 15.6424 | 13.6962 | 11.7806 | 9.4403 | 7.8281 | 3.5549 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 88.9006 | 88.4589 | 87.6608 | 85.4762 | 80.3766 | 74.3926 | 68.2149 | 62.6246 | 40.1378 | 15.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 88.9006 | 88.4382 | 87.5945 | 85.3533 | 80.2573 | 74.3372 | 68.1986 | 60.5396 | 34.7079 | 7.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 88.9006 | 88.7763 | 88.5947 | 88.3603 | 88.0693 | 87.6474 | 87.1921 | 86.2862 | 84.6527 | 81.8346 | 78.0736 | 74.0841 | 68.9468 | 65.4646 | 60.5576 | 54.0615 | 37.5383
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 88.9006 | 88.4089 | 87.4826 | 85.1383 | 79.8085 | 73.5808 | 67.6325 | 58.3595 | 34.5792 | 5.8177 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | BOURNE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 88.9006 | 88.6578 | 88.2513 | 87.4766 | 85.5064 | 82.9157 | 80.1977 | 77.1015 | 72.1362 | 65.4403 | 57.7344 | 50.3236 | 41.2847 | 28.5265 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.41731 | 0.35087 | 0.2908 | 0.068001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.41731 | 0.3391 | 0.26483 | 0.02036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.41731 | 0.39305 | 0.3891 | 0.37616 | 0.36459 | 0.32874 | 0.29028 | 0.22483 | 0.071176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.41731 | 0.34383 | 0.26532 | 0.015093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | CROWLAND 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.41731 | 0.37902 | 0.36019 | 0.28653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DONINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.607 | 7.6063 | 7.5998 | 7.5592 | 7.1685 | 6.6475 | 6.1038 | 5.7397 | 5.3606 | 4.9614 | 4.5657 | 4.2069 | 3.8191 | 3.5405 | 3.2352 | 2.0145 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.607 | 7.6063 | 7.5994 | 7.5586 | 7.1839 | 6.6996 | 6.1921 | 5.8444 | 5.4774 | 5.0819 | 4.7006 | 4.3621 | 3.9884 | 3.7202 | 3.4071 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.607 | 7.6095 | 7.6116 | 7.6134 | 7.6139 | 7.6117 | 7.6051 | 7.5867 | 7.539 | 7.4398 | 7.2872 | 7.1112 | 6.8721 | 6.723 | 6.5682 | 6.9882 | 6.6322
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.607 | 7.6057 | 7.597 | 7.5516 | 7.1423 | 6.5878 | 6.0337 | 5.7279 | 5.4077 | 5.1051 | 4.7735 | 4.4367 | 4.0312 | 3.6739 | 3.0192 | 0 | 0
Walpole 132kV | DOWSBY FEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.607 | 7.6084 | 7.6079 | 7.6014 | 7.5139 | 7.34 | 7.13 | 6.9498 | 6.7151 | 6.4295 | 6.1234 | 5.8479 | 5.5189 | 5.3472 | 5.5337 | 4.8259 | 3.9116
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 9.1586 | 8.8267 | 8.6717 | 8.3126 | 7.2661 | 6.1717 | 5.0136 | 4.2387 | 3.61 | 3.0088 | 2.4829 | 1.9813 | 1.5317 | 1.1215 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 9.1586 | 8.8258 | 8.6678 | 8.3077 | 7.2597 | 6.1658 | 5.0077 | 4.2353 | 3.61 | 3.0012 | 2.4956 | 2.0125 | 1.5671 | 1.1541 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 9.1586 | 8.8972 | 8.8457 | 8.7996 | 8.808 | 8.8411 | 8.7892 | 8.7378 | 8.7151 | 8.6789 | 8.6504 | 8.6329 | 8.6237 | 8.6103 | 8.6362 | 8.651 | 8.1097
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 9.1586 | 8.8189 | 8.6439 | 8.2632 | 7.1415 | 5.9207 | 4.5952 | 3.7608 | 3.0443 | 2.3522 | 1.728 | 1.1729 | 0.63362 | 0.16762 | 0 | 0 | 0
Walpole 132kV | HOLBEACH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 9.1586 | 8.8716 | 8.7809 | 8.6506 | 8.2913 | 7.849 | 7.3478 | 7.0135 | 6.7895 | 6.5512 | 6.3642 | 6.2331 | 6.0985 | 5.9961 | 5.2134 | 3.8201 | 2.0693
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.104 | 4.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.104 | 4.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.104 | 4.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.104 | 4.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | KIRTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.104 | 4.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.7978 | 4.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.7978 | 4.6359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.7978 | 6.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.7978 | 4.6341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LANGRICK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.7978 | 4.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.2024 | 5.0229 | 4.9208 | 4.6669 | 3.6599 | 2.4396 | 1.2919 | 0.38199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.2024 | 5.0221 | 4.9173 | 4.6624 | 3.6533 | 2.4318 | 1.2825 | 0.37206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.2024 | 5.2136 | 5.0562 | 5.0778 | 5.0513 | 5.0452 | 5.104 | 5.0343 | 4.8631 | 4.6141 | 4.331 | 4.0556 | 3.838 | 3.6143 | 2.4677 | 1.4649 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.2024 | 5.0251 | 4.9101 | 4.6559 | 3.5859 | 2.2819 | 1.0722 | 0.16102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | LONG SUTTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.2024 | 5.0629 | 5.0193 | 4.9639 | 4.5919 | 4.1613 | 3.8527 | 3.4878 | 3.0417 | 2.6938 | 2.4083 | 2.1654 | 1.8558 | 1.6142 | 0 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.5559 | 19.4733 | 19.3761 | 19.1476 | 18.856 | 17.2063 | 16.9964 | 16.7354 | 16.5523 | 16.3792 | 16.2357 | 16.015 | 15.7565 | 15.4712 | 7.8598 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.5559 | 19.4686 | 19.3637 | 19.1261 | 18.8395 | 17.1936 | 16.9529 | 16.6768 | 16.4873 | 16.2954 | 16.1541 | 15.9368 | 15.6656 | 14.4107 | 3.336 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.5559 | 19.521 | 19.4877 | 19.4518 | 19.4102 | 19.3728 | 19.3357 | 19.3122 | 19.3282 | 19.3464 | 19.3809 | 19.4199 | 19.4395 | 19.4609 | 19.618 | 19.627 | 19.2368
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.5559 | 19.4626 | 19.3464 | 19.1003 | 18.8167 | 17.1514 | 16.8277 | 16.5213 | 16.2844 | 16.0415 | 15.8016 | 15.551 | 15.2316 | 14.891 | 4.3781 | 0 | 0
Walpole 132kV | MARKET DEEPING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.5559 | 19.5008 | 19.4383 | 19.3424 | 19.1734 | 19.0006 | 18.8692 | 18.8013 | 18.7833 | 18.7647 | 18.7584 | 18.7476 | 18.7239 | 17.2817 | 16.5867 | 9.2965 | 0.069743
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MARSH LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.83 | 4.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.83 | 4.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.83 | 6.5736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.83 | 4.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.83 | 4.7681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 6.809 | 4.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 6.809 | 4.5618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 6.809 | 6.5534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 6.809 | 4.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 6.809 | 4.7534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 48.3453 | 46.812 | 45.9152 | 43.1664 | 34.949 | 25.6519 | 16.4963 | 9.6628 | 3.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 48.3453 | 46.7969 | 45.8668 | 43.097 | 34.8534 | 25.5473 | 16.3765 | 9.5495 | 3.8686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 48.3453 | 47.7129 | 47.1403 | 47.0654 | 46.9527 | 46.9799 | 47.0083 | 46.5523 | 45.7453 | 44.6154 | 43.3131 | 42.0915 | 41.178 | 40.2002 | 35.4486 | 31.0802 | 21.2195
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 48.3453 | 46.7979 | 45.7348 | 42.8944 | 34.1494 | 24.0673 | 14.0564 | 7.0171 | 0.45783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SOUTH HOLLAND 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 48.3453 | 47.1911 | 46.8443 | 46.034 | 43.093 | 39.5369 | 36.3171 | 33.5119 | 30.7054 | 28.3561 | 26.2775 | 24.5757 | 22.6579 | 18.322 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 91.6901 | 90.8486 | 90.126 | 86.6999 | 78.8625 | 70.2103 | 46.0261 | 26.96 | 11.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 91.6901 | 90.8282 | 90.0627 | 86.6106 | 78.7443 | 70.0882 | 45.692 | 26.6438 | 10.7937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 91.6901 | 91.5029 | 91.3795 | 91.301 | 91.1227 | 91.0568 | 91.0687 | 90.69 | 90.0013 | 89.1809 | 88.1776 | 87.2873 | 86.6763 | 85.9638 | 78.0948 | 60.7152 | 27.7101
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 91.6901 | 90.8472 | 89.8868 | 86.3663 | 78.085 | 67.15 | 39.2185 | 19.5783 | 1.2774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 91.6901 | 91.3141 | 91.2673 | 90.2637 | 87.4335 | 83.9659 | 80.9238 | 78.2848 | 75.6265 | 73.488 | 62.9627 | 49.6912 | 33.7537 | 23.0264 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1445 | 20.292 | 20.194 | 19.9999 | 19.7813 | 19.5927 | 19.4595 | 19.2785 | 19.126 | 19.0519 | 18.9921 | 18.9257 | 18.8881 | 17.1237 | 16.3711 | 2.4028 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1445 | 20.2914 | 20.1917 | 19.9975 | 19.7792 | 19.5925 | 19.4599 | 19.2817 | 19.1314 | 19.055 | 19.0008 | 18.9362 | 18.8943 | 17.1258 | 16.3586 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1445 | 20.2785 | 20.2452 | 20.2409 | 20.2008 | 20.1778 | 20.1826 | 20.1486 | 20.1059 | 20.1016 | 20.1116 | 20.1377 | 20.1708 | 20.1846 | 20.2768 | 20.2387 | 19.8365
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1445 | 20.3011 | 20.1928 | 19.9924 | 19.7652 | 19.5729 | 19.4325 | 19.2603 | 19.1075 | 19.0203 | 18.951 | 18.905 | 18.8809 | 17.1061 | 15.9406 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1445 | 20.3187 | 20.258 | 20.1988 | 20.0929 | 19.9974 | 19.9445 | 19.8391 | 19.7346 | 19.7026 | 19.6959 | 19.6975 | 19.6843 | 19.6478 | 19.2771 | 18.7903 | 16.5702
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 91.6901 | 90.8486 | 90.126 | 86.6999 | 78.8625 | 70.2103 | 46.0261 | 26.96 | 11.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 91.6901 | 90.8282 | 90.0627 | 86.6106 | 78.7443 | 70.0882 | 45.692 | 26.6438 | 10.7937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 91.6901 | 91.5029 | 91.3795 | 91.301 | 91.1227 | 91.0568 | 91.0687 | 90.69 | 90.0013 | 89.1809 | 88.1776 | 87.2873 | 86.6763 | 85.9638 | 78.0948 | 60.7152 | 27.7101
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 91.6901 | 90.8472 | 89.8868 | 86.3663 | 78.085 | 67.15 | 39.2185 | 19.5783 | 1.2774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | SPALDING CLAY LAKE 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 91.6901 | 91.3141 | 91.2673 | 90.2637 | 87.4335 | 83.9659 | 80.9238 | 78.2848 | 75.6265 | 73.488 | 62.9627 | 49.6912 | 33.7537 | 23.0264 | 0 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 35.7606 | 35.6146 | 35.5589 | 35.2001 | 34.6554 | 34.0651 | 33.5036 | 33.0854 | 32.7065 | 32.4625 | 30.7057 | 30.4433 | 30.1161 | 29.7628 | 26.9076 | 2.3985 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 35.7606 | 35.6134 | 35.5539 | 35.1947 | 34.6493 | 34.0614 | 33.5022 | 33.0902 | 32.716 | 32.4642 | 30.714 | 30.479 | 30.1672 | 29.8198 | 26.8787 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 35.7606 | 35.6977 | 35.7268 | 35.7631 | 35.7933 | 35.8226 | 35.8415 | 35.8801 | 35.8989 | 35.9232 | 35.9145 | 35.9146 | 35.9243 | 35.9305 | 35.8922 | 35.8135 | 35.0012
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 35.7606 | 35.6058 | 35.5201 | 35.1571 | 34.5916 | 33.9919 | 33.3793 | 32.9553 | 32.554 | 30.733 | 30.5358 | 30.1369 | 29.6763 | 29.2299 | 25.8544 | 0 | 0
Walpole 132kV | SPALDING PARK ROAD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 35.7606 | 35.6691 | 35.6932 | 35.6264 | 35.475 | 35.2356 | 35.0145 | 34.8925 | 34.7542 | 34.6179 | 34.402 | 34.2111 | 34.0492 | 33.9282 | 32.8378 | 30.4439 | 28.4017
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.5495 | 22.0818 | 21.8982 | 21.445 | 21.0209 | 20.5364 | 20.0782 | 19.7376 | 16.3121 | 15.7034 | 14.5232 | 12.9729 | 11.0706 | 9.475 | 3.5576 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.5495 | 22.0632 | 21.8529 | 21.3507 | 20.8824 | 20.3364 | 19.8594 | 16.3626 | 15.9906 | 14.9475 | 13.5271 | 11.878 | 9.9246 | 8.325 | 2.0962 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.5495 | 22.3053 | 22.0977 | 22.0362 | 21.9568 | 21.8544 | 21.7219 | 21.5809 | 21.2709 | 20.7836 | 20.2027 | 19.7381 | 16.4109 | 16.176 | 15.7735 | 14.6881 | 12.7486
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.5495 | 22.0522 | 21.8171 | 21.2937 | 20.8177 | 20.3204 | 19.907 | 19.6886 | 16.307 | 15.8533 | 14.8154 | 13.3602 | 11.4261 | 9.5098 | 1.9188 | 0 | 0
Walpole 132kV | STAMFORD 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.5495 | 22.1207 | 21.9965 | 21.8055 | 21.5818 | 21.2858 | 20.9364 | 20.5494 | 19.9399 | 16.3898 | 15.835 | 14.7903 | 13.2813 | 12.3141 | 9.4618 | 5.0664 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 64.9733 | 63.4233 | 62.7177 | 58.3695 | 57.3683 | 54.8578 | 51.886 | 48.5362 | 43.2717 | 25.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 64.9733 | 63.3027 | 62.4672 | 58.2069 | 56.3742 | 53.0381 | 49.1019 | 44.4598 | 38.0465 | 12.7714 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 64.9733 | 64.1556 | 63.458 | 63.1846 | 62.875 | 62.446 | 61.9156 | 61.4299 | 57.928 | 55.0753 | 50.9859 | 46.6072 | 40.7825 | 37.0512 | 32.8141 | 25.0814 | 11.8974
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 64.9733 | 63.2658 | 62.3536 | 58.0794 | 56.0716 | 53.073 | 49.9159 | 47.1256 | 42.5504 | 9.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STAMFORD 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 64.9733 | 63.5599 | 63.038 | 62.2979 | 61.6676 | 58.1593 | 56.6437 | 54.1114 | 49.3765 | 42.9611 | 35.5147 | 28.2081 | 17.7715 | 10.7863 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.7976 | 4.6975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.7976 | 4.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.7976 | 5.7928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.7976 | 4.6858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | STICKNEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.7976 | 4.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.403 | 12.3843 | 12.3602 | 12.3081 | 12.2762 | 11.7411 | 11.6867 | 11.5174 | 11.1691 | 10.7011 | 10.0699 | 9.3554 | 8.469 | 7.8233 | 5.7869 | 3.4284 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.403 | 12.3734 | 12.3381 | 12.2719 | 11.7391 | 11.6604 | 11.4639 | 11.1442 | 10.6587 | 10.0322 | 9.3079 | 8.5507 | 7.6669 | 7.0272 | 4.8973 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.403 | 12.3937 | 12.3837 | 12.3726 | 12.3668 | 12.3477 | 12.3193 | 12.274 | 11.7473 | 11.622 | 11.3343 | 10.9986 | 10.5505 | 10.2507 | 9.8915 | 9.3016 | 8.5904
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.403 | 12.373 | 12.3341 | 12.2685 | 11.7383 | 11.6801 | 11.56 | 11.4068 | 11.1285 | 10.7957 | 10.2667 | 9.5972 | 8.7349 | 7.9545 | 5.2716 | 0 | 0
Walpole 132kV | TINWELL ROAD KETTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.403 | 12.386 | 12.3646 | 12.3336 | 12.3089 | 12.2691 | 11.7441 | 11.6613 | 11.3495 | 10.8645 | 10.2825 | 9.7064 | 9.0051 | 8.5594 | 7.4789 | 5.8956 | 3.9398
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 15.0989 | 15.068 | 15.0287 | 14.9495 | 14.4552 | 13.9587 | 13.5108 | 13.2882 | 13.1765 | 13.0076 | 12.8573 | 12.7539 | 12.6596 | 12.5602 | 11.0566 | 3.2668 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 15.0989 | 15.0679 | 15.0281 | 14.9488 | 14.4546 | 13.9587 | 13.5113 | 13.2901 | 13.1793 | 13.0092 | 12.8615 | 12.7608 | 12.6679 | 12.569 | 11.0534 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 15.0989 | 15.0795 | 15.0604 | 15.041 | 15.0191 | 14.9953 | 15.0031 | 15.0051 | 15.0442 | 15.0558 | 15.0556 | 15.057 | 15.0593 | 15.0632 | 15.0196 | 14.9516 | 14.7948
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 15.0989 | 15.0661 | 15.0243 | 14.943 | 14.4278 | 13.8468 | 13.3296 | 13.0806 | 12.9318 | 12.7401 | 12.5665 | 10.475 | 10.35 | 10.2233 | 9.9722 | 0 | 0
Walpole 132kV | TUNNEL BANK BOURNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 15.0989 | 15.0743 | 15.0463 | 15.0093 | 14.8237 | 14.6009 | 14.4312 | 14.3584 | 14.3775 | 14.3315 | 14.2768 | 14.248 | 14.2256 | 14.1985 | 12.9852 | 13.1885 | 12.7979
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.35 | 4.4011 | 4.5039 | 4.4175 | 4.3319 | 4.2486 | 4.2085 | 4.1343 | 4.0704 | 4.0146 | 3.961 | 3.8879 | 3.8182 | 3.7475 | 3.3182 | 2.3975 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.35 | 4.4009 | 4.5032 | 4.4166 | 4.3304 | 4.2466 | 4.2062 | 4.1317 | 4.0673 | 4.0099 | 3.9579 | 3.8858 | 3.8162 | 3.7445 | 3.3042 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.35 | 4.3911 | 4.4679 | 4.4423 | 4.4146 | 4.3867 | 4.3922 | 4.3712 | 4.3492 | 4.3291 | 4.3124 | 4.2983 | 4.2837 | 4.269 | 4.1961 | 4.0802 | 3.8952
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.35 | 4.4047 | 4.4966 | 4.4134 | 4.3302 | 4.2425 | 4.2086 | 4.1392 | 4.0716 | 4.0056 | 3.9382 | 3.8724 | 3.8064 | 3.7355 | 3.2074 | 0 | 0
Walpole 132kV | WARDENTREE PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.35 | 4.4073 | 4.5209 | 4.4742 | 4.4229 | 4.3683 | 4.3582 | 4.3129 | 4.2705 | 4.2291 | 4.1927 | 4.1585 | 4.1228 | 4.0912 | 3.8631 | 3.5086 | 3.1254
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.7103 | 16.6789 | 16.6364 | 16.5184 | 16.4091 | 16.288 | 16.1581 | 16.0161 | 15.2031 | 14.4679 | 13.3415 | 11.9871 | 10.2934 | 8.8781 | 4.5411 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.7103 | 16.6641 | 16.6003 | 16.4438 | 16.2997 | 16.1425 | 16.0066 | 15.1301 | 14.2076 | 12.9484 | 11.4787 | 9.963 | 8.1735 | 6.864 | 2.6588 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.7103 | 16.6959 | 16.6786 | 16.6605 | 16.6383 | 16.5997 | 16.5368 | 16.4103 | 16.187 | 15.3922 | 14.9105 | 14.0473 | 12.8833 | 12.1306 | 11.1635 | 9.7434 | 8.0885
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.7103 | 16.6621 | 16.591 | 16.4271 | 16.2796 | 16.1459 | 16.0428 | 15.8989 | 15.0701 | 14.4425 | 13.3784 | 12.0148 | 10.228 | 8.5955 | 3.1985 | 0 | 0
Walpole 132kV | WEST DEEPING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.7103 | 16.6841 | 16.6494 | 16.5921 | 16.5254 | 16.4155 | 16.2589 | 16.0301 | 15.1589 | 14.0454 | 12.6651 | 11.3033 | 9.639 | 8.6631 | 6.3747 | 3.1053 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0.43088 | 0.36228 | 0.30026 | 0.070212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0.43088 | 0.35012 | 0.27344 | 0.021022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0.43088 | 0.40583 | 0.40175 | 0.38839 | 0.37644 | 0.33943 | 0.29972 | 0.23214 | 0.07349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0.43088 | 0.35501 | 0.27394 | 0.015583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WHAPLODE DROVE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0.43088 | 0.39134 | 0.3719 | 0.29584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.6013 | 16.5819 | 16.5588 | 16.4981 | 16.4429 | 16.2919 | 16.1241 | 15.9126 | 15.3719 | 14.5942 | 13.5144 | 12.1734 | 10.5011 | 8.985 | 3.7069 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.6013 | 16.5663 | 16.5227 | 16.4221 | 16.3219 | 16.0639 | 15.7456 | 15.2728 | 14.2516 | 12.9701 | 11.5327 | 10.0095 | 8.215 | 6.7964 | 1.5733 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.6013 | 16.5859 | 16.5703 | 16.5532 | 16.5357 | 16.5071 | 16.4614 | 16.3611 | 16.1714 | 15.8517 | 15.4316 | 14.9817 | 14.403 | 13.9468 | 13.1609 | 11.8996 | 10.2247
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.6013 | 16.5666 | 16.5208 | 16.4201 | 16.3224 | 16.1287 | 15.9221 | 15.6774 | 14.9689 | 14.1996 | 13.0786 | 11.6991 | 9.9215 | 8.2377 | 2.0648 | 0 | 0
Walpole 132kV | WITTERING 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.6013 | 16.5808 | 16.5544 | 16.516 | 16.4704 | 16.3908 | 16.2734 | 16.0301 | 15.5744 | 14.9581 | 13.8454 | 12.6635 | 11.1896 | 10.2872 | 7.8925 | 4.3844 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.1187 | 21.0497 | 20.9854 | 20.7792 | 20.5525 | 20.2549 | 19.9701 | 19.6408 | 19.3141 | 19.0855 | 17.4323 | 14.9276 | 11.8843 | 9.0762 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.1187 | 20.9767 | 20.7878 | 20.3604 | 19.909 | 19.387 | 18.8707 | 18.3217 | 16.255 | 13.6399 | 10.6889 | 7.5714 | 4.0518 | 1.2756 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.1187 | 21.045 | 20.994 | 20.9372 | 20.8773 | 20.8083 | 20.7378 | 20.6717 | 20.5955 | 20.5305 | 20.479 | 19.6754 | 18.1255 | 17.0668 | 15.6781 | 13.4692 | 10.1547
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.1187 | 20.9696 | 20.7638 | 20.3141 | 19.8446 | 19.321 | 18.8005 | 18.2777 | 17.6657 | 16.0355 | 13.7478 | 10.943 | 7.4859 | 4.2514 | 0 | 0 | 0
West Burton 132kV | ANDERSON LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.1187 | 21.0286 | 20.9131 | 20.7584 | 20.5529 | 20.3174 | 20.0923 | 19.8624 | 19.6424 | 18.2282 | 16.0181 | 13.8677 | 11.3039 | 9.5841 | 4.6285 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 23.0245 | 23.0051 | 22.9226 | 22.7683 | 22.6211 | 22.5131 | 22.4052 | 22.2898 | 22.1934 | 22.1117 | 22.0261 | 21.9252 | 21.8546 | 21.7935 | 21.2488 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 23.0245 | 22.9851 | 22.874 | 22.6788 | 22.4891 | 22.3426 | 22.2015 | 22.0533 | 21.922 | 21.8005 | 21.6839 | 21.5472 | 21.4395 | 21.3347 | 16.8466 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 23.0245 | 22.9939 | 22.9299 | 22.8595 | 22.8007 | 22.7517 | 22.6953 | 22.6537 | 22.5993 | 22.5481 | 22.5027 | 22.4643 | 22.4314 | 22.4047 | 22.3783 | 22.3479 | 22.0393
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 23.0245 | 22.983 | 22.8596 | 22.6655 | 22.4829 | 22.3298 | 22.1736 | 22.0261 | 21.8891 | 21.7566 | 21.628 | 21.5096 | 21.3977 | 21.2915 | 18.2816 | 0 | 0
West Burton 132kV | BEEVOR STREET 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 23.0245 | 22.9977 | 22.9114 | 22.8071 | 22.6955 | 22.5979 | 22.5025 | 22.4099 | 22.3191 | 22.2364 | 22.1624 | 22.0981 | 22.0459 | 22.0076 | 21.7397 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 1.3719 | 0.89957 | 0.80615 | 0.55891 | 0.094046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 1.3719 | 0.85809 | 0.70349 | 0.32422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 1.3719 | 1.1284 | 0.88877 | 0.83849 | 0.77374 | 0.69884 | 0.60503 | 0.46697 | 0.23944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 1.3719 | 0.85234 | 0.68311 | 0.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | DODDINGTON PARK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 1.3719 | 0.90399 | 0.81622 | 0.67294 | 0.42734 | 0.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | FISKERTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 99.4653 | 96.388 | 95.1962 | 92.3673 | 88.941 | 84.8371 | 80.7001 | 76.3635 | 70.6491 | 64.6699 | 55.598 | 43.8111 | 29.7023 | 9.8083 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 99.4653 | 95.9301 | 93.9887 | 89.646 | 84.7393 | 78.6607 | 71.8755 | 63.6229 | 53.4209 | 41.4106 | 28.1371 | 9.9294 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 99.4653 | 98.0304 | 96.0366 | 95.3061 | 94.5273 | 93.6356 | 92.5028 | 90.7744 | 88.0031 | 83.7809 | 78.4271 | 72.8304 | 65.7503 | 61.0395 | 55.3947 | 51.1186 | 35.0963
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 99.4653 | 95.8632 | 93.7367 | 89.1773 | 84.0526 | 78.3038 | 72.3127 | 66.4627 | 58.8925 | 51.0008 | 40.1494 | 27.1834 | 6.4398 | 0 | 0 | 0 | 0
West Burton 132kV | LINCOLN MAIN 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 99.4653 | 96.4331 | 95.2329 | 93.5069 | 91.2269 | 88.3803 | 85.0217 | 80.2573 | 73.2678 | 64.4549 | 54.5523 | 44.9432 | 33.3105 | 25.683 | 0 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 29.5841 | 28.9834 | 28.9661 | 28.9195 | 28.8619 | 28.8348 | 28.7767 | 28.6857 | 28.5972 | 28.5134 | 28.4046 | 28.8761 | 29.2382 | 29.0992 | 28.4694 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 29.5841 | 28.9735 | 28.9407 | 28.8656 | 28.7793 | 28.6948 | 28.5961 | 28.4678 | 28.3613 | 28.2451 | 28.1065 | 28.554 | 28.8871 | 28.7146 | 27.8358 | 27.0382 | 26.2764
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 29.5841 | 29.5741 | 29.4883 | 29.4814 | 29.468 | 28.973 | 28.9816 | 28.9791 | 28.9851 | 28.9863 | 28.9788 | 29.5679 | 29.5571 | 29.5443 | 29.4917 | 29.4936 | 29.3486
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 29.5841 | 28.9729 | 28.9387 | 28.8622 | 28.7719 | 28.7102 | 28.6084 | 28.4771 | 28.3423 | 28.21 | 28.0546 | 28.4907 | 28.8054 | 28.6202 | 27.7492 | 0 | 0
West Burton 132kV | LINCOLN No 2 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 29.5841 | 29.4975 | 29.4782 | 28.9385 | 28.9 | 28.8822 | 28.8555 | 28.8102 | 28.7801 | 28.743 | 28.6872 | 29.2391 | 29.6695 | 29.6064 | 29.2571 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 7.8815 | 7.617 | 7.5619 | 7.4383 | 7.0845 | 6.631 | 6.177 | 5.8291 | 5.3555 | 4.8402 | 4.1314 | 3.2662 | 2.1983 | 1.2068 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 7.8815 | 7.6149 | 7.5571 | 7.4166 | 7.0566 | 6.5796 | 6.051 | 5.5262 | 4.8116 | 3.9481 | 3.0056 | 2.0542 | 0.9522 | 0.079054 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 7.8815 | 7.8065 | 7.6283 | 7.6119 | 7.5907 | 7.5587 | 7.5117 | 7.4235 | 7.2593 | 6.9928 | 6.6431 | 6.2724 | 5.7987 | 5.4687 | 4.9904 | 4.2504 | 3.3218
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 7.8815 | 7.6141 | 7.5515 | 7.4055 | 7.0321 | 6.5546 | 6.0714 | 5.7038 | 5.2007 | 4.66 | 3.9326 | 3.0668 | 1.9804 | 0.9561 | 0 | 0 | 0
West Burton 132kV | METHERINGHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 7.8815 | 7.633 | 7.6008 | 7.5497 | 7.4113 | 7.2261 | 7.0104 | 6.7403 | 6.2776 | 5.68 | 5.0026 | 4.3507 | 3.5636 | 3.0195 | 1.6124 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 35.3971 | 34.8688 | 34.6782 | 32.833 | 32.6881 | 32.419 | 32.0518 | 31.5897 | 30.9288 | 30.1808 | 29.1617 | 27.9045 | 26.4327 | 25.2571 | 21.047 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 35.3971 | 34.8638 | 34.6589 | 32.8176 | 32.6147 | 32.2389 | 31.7054 | 30.9437 | 29.9125 | 28.6913 | 27.3678 | 25.9509 | 24.3813 | 23.2716 | 16.9606 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 35.3971 | 35.2331 | 34.8615 | 34.7683 | 34.6797 | 34.6011 | 32.8447 | 32.8263 | 32.7392 | 32.5162 | 32.1367 | 31.667 | 31.0213 | 30.5583 | 29.9763 | 31.0153 | 29.5906
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 35.3971 | 34.8496 | 34.63 | 32.7986 | 32.5516 | 32.1522 | 31.6258 | 31.026 | 30.1836 | 29.277 | 28.1156 | 26.7915 | 25.1897 | 23.8741 | 18.4053 | 0 | 0
West Burton 132kV | NORTH HYKEHAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 35.3971 | 34.9152 | 34.7702 | 34.6077 | 32.8417 | 32.7734 | 32.5982 | 32.2472 | 31.6173 | 30.751 | 29.7543 | 28.7753 | 27.6203 | 26.8665 | 24.6217 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.2234 | 17.9027 | 17.8137 | 17.5461 | 17.2359 | 16.9607 | 16.6746 | 16.3603 | 16.2792 | 16.2822 | 16.2342 | 16.1012 | 16.015 | 15.8988 | 14.2538 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.2234 | 17.8447 | 17.6654 | 17.2265 | 16.7161 | 16.2427 | 15.7624 | 15.2632 | 15.0333 | 14.4857 | 14.4446 | 14.2915 | 13.9909 | 13.6094 | 10.5919 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.2234 | 18.1068 | 17.8559 | 17.7701 | 17.6833 | 17.6359 | 17.5867 | 17.5405 | 17.6191 | 17.7345 | 17.885 | 18.0697 | 18.2683 | 18.4896 | 19.3472 | 19.6187 | 18.8963
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.2234 | 17.835 | 17.633 | 17.1604 | 16.5949 | 16.1076 | 15.5583 | 15.0375 | 14.4123 | 14.1983 | 13.8999 | 13.5608 | 13.1792 | 12.7995 | 9.7744 | 0 | 0
West Burton 132kV | ROOKERY LANE LINCOLN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.2234 | 17.8915 | 17.7819 | 17.5989 | 17.3509 | 17.1113 | 16.8703 | 16.6346 | 16.6449 | 16.7126 | 16.8625 | 16.9899 | 16.9547 | 16.9132 | 15.9725 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Best View | Headroom (MW) | 14.999 | 14.9898 | 14.9792 | 14.9671 | 14.9551 | 14.9431 | 14.9313 | 14.9195 | 14.9082 | 14.8953 | 14.8814 | 14.8676 | 14.8539 | 14.8395 | 14.7591 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Consumer Transformation | Headroom (MW) | 14.999 | 14.9898 | 14.9792 | 14.9671 | 14.9551 | 14.9431 | 14.9303 | 14.9185 | 14.9075 | 14.8966 | 14.8857 | 14.8709 | 14.8552 | 14.8388 | 14.7706 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Falling Short | Headroom (MW) | 14.999 | 14.9898 | 14.9807 | 14.9716 | 14.9627 | 14.9538 | 14.9442 | 14.9338 | 14.9234 | 14.9131 | 14.9029 | 14.8927 | 14.8817 | 14.8707 | 14.8267 | 14.7765 | 14.7339
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | Leading the Way | Headroom (MW) | 14.999 | 14.9898 | 14.9792 | 14.9671 | 14.9551 | 14.9431 | 14.9313 | 14.9199 | 14.9085 | 14.8956 | 14.8818 | 14.868 | 14.8543 | 14.8398 | 14.7594 | 0 | 0
West Burton 132kV | RUSTON HORNSBY 33 6 6kV S STN | Primary Substation | 6.6 | System Transformation | Headroom (MW) | 14.999 | 14.9898 | 14.9807 | 14.9709 | 14.9611 | 14.9507 | 14.9404 | 14.9292 | 14.9181 | 14.906 | 14.8933 | 14.881 | 14.8688 | 14.8566 | 14.7922 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.2983 | 4.0837 | 4.0209 | 3.88 | 3.7364 | 3.4552 | 3.1588 | 2.8017 | 2.0577 | 1.1694 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.2983 | 4.0328 | 3.8803 | 3.5668 | 3.2653 | 2.7232 | 2.0363 | 1.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.2983 | 4.093 | 4.0589 | 4.0215 | 3.9771 | 3.902 | 3.7856 | 3.5469 | 3.0832 | 2.3234 | 1.3214 | 0.2507 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.2983 | 4.0313 | 3.8687 | 3.5456 | 3.2421 | 2.7971 | 2.3243 | 1.8192 | 0.89949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | SOUTH CARLTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.2983 | 4.0729 | 3.9797 | 3.8655 | 3.7337 | 3.5132 | 3.1867 | 2.5703 | 1.4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 18.6288 | 18.2812 | 18.1455 | 17.8063 | 17.5079 | 17.1062 | 16.7109 | 16.2925 | 15.7574 | 15.0852 | 14.1004 | 12.8489 | 11.3424 | 9.9866 | 5.3303 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 18.6288 | 18.2769 | 18.1382 | 17.7671 | 17.4253 | 16.9035 | 16.3093 | 15.5488 | 14.5811 | 13.3837 | 12.0317 | 10.6104 | 9.0055 | 7.7681 | 3.2126 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 18.6288 | 18.5776 | 18.3129 | 18.2659 | 18.2115 | 18.1443 | 18.0632 | 17.8739 | 17.6521 | 17.2544 | 16.7366 | 16.191 | 15.5043 | 15.0575 | 14.5131 | 13.836 | 12.4322
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 18.6288 | 18.2747 | 18.1231 | 17.7391 | 17.3883 | 16.9329 | 16.4725 | 16.0147 | 15.415 | 14.6885 | 13.6582 | 12.4104 | 10.8574 | 9.4292 | 4.0939 | 0 | 0
West Burton 132kV | WADDINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 18.6288 | 18.3247 | 18.2504 | 18.1213 | 17.8919 | 17.7487 | 17.5142 | 17.1226 | 16.5124 | 15.6971 | 14.7636 | 13.8564 | 12.781 | 12.0771 | 10.3948 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | WRAGBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 42.015 | 41.7691 | 41.4964 | 40.9436 | 40.4082 | 39.8941 | 39.4769 | 39.0531 | 38.695 | 38.3987 | 38.1206 | 37.8364 | 37.6837 | 33.4422 | 32.0273 | 27.849 | 22.8042
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 42.015 | 41.7754 | 41.507 | 40.9094 | 40.3268 | 39.7602 | 39.2816 | 38.8077 | 38.4064 | 38.1044 | 37.8677 | 37.6851 | 33.412 | 33.3315 | 30.9446 | 26.1271 | 20.2541
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 42.015 | 41.8856 | 41.7758 | 41.6586 | 41.5427 | 41.425 | 41.321 | 41.2187 | 41.0949 | 40.988 | 40.8977 | 40.8199 | 40.7615 | 40.725 | 40.7916 | 40.7941 | 39.8691
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 42.015 | 41.7601 | 41.4644 | 40.8359 | 40.2396 | 39.6483 | 39.1591 | 38.7057 | 38.3038 | 37.9971 | 37.7704 | 37.6646 | 33.3697 | 32.9532 | 29.896 | 24.4914 | 0
Willington 132kV | ALLENTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 42.015 | 41.844 | 41.6733 | 41.4229 | 41.1348 | 40.8167 | 40.5447 | 40.2719 | 40.0054 | 39.7757 | 39.5637 | 39.3793 | 39.2268 | 39.114 | 38.2424 | 33.5716 | 31.5386
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.5749 | 16.4479 | 16.332 | 16.0163 | 15.5502 | 14.8233 | 14.002 | 13.1945 | 11.9569 | 10.4297 | 8.6863 | 6.7695 | 4.5483 | 2.7068 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.5749 | 16.4456 | 16.326 | 16.0001 | 15.525 | 14.7944 | 13.976 | 13.1777 | 11.9464 | 10.4237 | 8.7073 | 6.8157 | 4.6074 | 2.7667 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.5749 | 16.4975 | 16.4687 | 16.4397 | 16.4303 | 16.4015 | 16.3444 | 16.2696 | 16.0438 | 15.6344 | 15.064 | 14.4236 | 13.5695 | 12.9788 | 12.032 | 10.4935 | 8.4796
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.5749 | 16.4417 | 16.3072 | 15.9718 | 15.4738 | 14.793 | 14.0747 | 13.5567 | 12.6965 | 11.7321 | 10.3426 | 8.5997 | 6.3968 | 4.2819 | 0 | 0 | 0
Willington 132kV | ASHBOURNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.5749 | 16.4793 | 16.4185 | 16.308 | 16.1512 | 15.8777 | 15.5562 | 15.2021 | 14.4253 | 13.3657 | 12.1322 | 10.8396 | 9.2351 | 8.0943 | 4.707 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.7424 | 12.5744 | 12.5175 | 12.3962 | 12.3422 | 11.594 | 11.4977 | 11.3641 | 11.2273 | 11.0938 | 10.9491 | 10.7646 | 10.6011 | 6.8175 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.7424 | 12.5741 | 12.5173 | 12.3963 | 12.3423 | 11.5959 | 11.502 | 11.3729 | 11.2386 | 11.106 | 10.972 | 10.8006 | 10.6499 | 6.8826 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.7424 | 12.7275 | 12.5822 | 12.5671 | 12.5446 | 12.5207 | 12.4988 | 12.4766 | 12.4507 | 12.4288 | 12.4099 | 12.3955 | 12.3868 | 12.3816 | 12.4015 | 12.3876 | 12.2723
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.7424 | 12.5722 | 12.5095 | 12.3889 | 11.6269 | 11.5842 | 11.4802 | 11.3502 | 11.2095 | 11.0613 | 10.9067 | 10.7504 | 10.5941 | 10.4349 | 0 | 0 | 0
Willington 132kV | BAKEWELL 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.7424 | 12.587 | 12.5555 | 12.5043 | 12.4486 | 12.3946 | 12.3551 | 12.3337 | 11.6376 | 11.6208 | 11.5911 | 11.5554 | 11.5182 | 11.4863 | 11.203 | 0.19518 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 21.3429 | 21.1803 | 21.5586 | 21.3494 | 20.9059 | 20.463 | 20.0748 | 19.7063 | 19.4116 | 16.5953 | 16.4127 | 15.9201 | 15.241 | 14.5167 | 10.8258 | 5.6172 | 0.85313
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 21.3429 | 21.1748 | 21.5764 | 21.2557 | 20.7391 | 20.2245 | 19.7707 | 19.4075 | 16.5143 | 16.2101 | 15.6235 | 14.8235 | 13.9761 | 13.1943 | 8.8567 | 2.8167 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 21.3429 | 21.2864 | 21.6666 | 21.8508 | 21.7985 | 21.7384 | 21.672 | 21.5934 | 21.4657 | 21.3032 | 21.1189 | 20.9468 | 20.7513 | 20.6107 | 20.6518 | 20.4005 | 19.4074
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 21.3429 | 21.1639 | 21.5061 | 21.2078 | 20.6996 | 20.1874 | 19.749 | 19.4324 | 16.5317 | 16.3651 | 15.897 | 15.2083 | 14.3335 | 13.4094 | 8.2325 | 1.7327 | 0
Willington 132kV | BELPER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 21.3429 | 21.2415 | 21.7433 | 21.7837 | 21.5489 | 21.2795 | 21.0043 | 20.6941 | 20.3146 | 19.924 | 19.5723 | 19.3434 | 16.5833 | 16.5373 | 15.6398 | 12.9384 | 9.1696
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 13.1476 | 13.1235 | 13.0508 | 12.8689 | 12.6825 | 12.4281 | 12.14 | 11.8325 | 11.4831 | 11.0185 | 10.196 | 8.9851 | 7.5217 | 5.7675 | 1.736 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 13.1476 | 13.1218 | 13.0477 | 12.8722 | 12.6909 | 12.4044 | 12.0631 | 11.6363 | 11.0715 | 9.9146 | 8.6335 | 7.2984 | 5.768 | 4.6536 | 0 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 13.1476 | 13.1406 | 13.1133 | 13.0823 | 13.0528 | 13.0161 | 12.97 | 12.8994 | 12.8 | 12.6262 | 12.3995 | 12.1634 | 11.8649 | 11.5486 | 10.8932 | 12.0246 | 10.8542
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 13.1476 | 13.1207 | 13.0429 | 12.8625 | 12.6772 | 12.4239 | 12.1353 | 11.8389 | 11.4966 | 11.0337 | 10.1451 | 8.9671 | 7.5043 | 5.7424 | 1.5293 | 0 | 0
Willington 132kV | CASTLE DONINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 13.1476 | 13.1381 | 13.0956 | 13.0268 | 12.9444 | 12.8309 | 12.6901 | 12.4832 | 12.2047 | 11.7868 | 11.2888 | 10.4933 | 9.5489 | 8.875 | 8.0069 | 5.3655 | 2.124
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 30.6276 | 30.4642 | 30.3718 | 30.1983 | 27.0639 | 26.9813 | 26.8355 | 26.6245 | 26.3937 | 26.1638 | 25.9069 | 25.5567 | 25.2698 | 24.9769 | 20.3523 | 16.7032 | 12.3494
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 30.6276 | 30.4642 | 30.3662 | 30.1895 | 27.048 | 26.9239 | 26.7203 | 26.4427 | 26.1312 | 25.8444 | 25.5546 | 25.1722 | 24.8668 | 24.5399 | 19.3948 | 15.2619 | 10.1545
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 30.6276 | 30.5236 | 30.4922 | 30.4335 | 30.3661 | 30.3018 | 30.2453 | 30.1973 | 30.147 | 30.1075 | 30.0759 | 30.0506 | 30.0297 | 30.0114 | 29.9593 | 27.2358 | 26.8236
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 30.6276 | 30.4582 | 30.3481 | 30.1835 | 27.0329 | 26.8778 | 26.6369 | 26.3451 | 26.0061 | 25.6741 | 25.3275 | 24.9717 | 24.5992 | 24.1715 | 18.393 | 13.6992 | 7.5494
Willington 132kV | CHADDESDEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 30.6276 | 30.4989 | 30.4413 | 30.3239 | 30.2171 | 30.1483 | 27.1113 | 27.1037 | 27.0687 | 27.0216 | 26.9682 | 26.9199 | 26.8833 | 26.8637 | 25.4376 | 23.6666 | 21.1869
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.7016 | 16.682 | 16.6684 | 16.5954 | 16.3895 | 16.0241 | 15.6293 | 15.2341 | 13.4313 | 10.4541 | 5.7665 | 1.0165 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.7016 | 16.6654 | 16.6192 | 16.4278 | 16.0429 | 15.4893 | 14.9148 | 14.3373 | 11.4557 | 8.1472 | 3.17 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.7016 | 16.688 | 16.6856 | 16.6746 | 16.6808 | 16.6787 | 16.6863 | 16.673 | 16.6389 | 16.8071 | 16.786 | 16.7548 | 15.0915 | 13.382 | 11.6852 | 7.162 | 1.8845
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.7016 | 16.6622 | 16.6089 | 16.4005 | 15.9801 | 15.407 | 14.8518 | 14.3993 | 13.8777 | 12.5405 | 8.8144 | 4.2392 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CHURCH ST 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.7016 | 16.6805 | 16.6666 | 16.6178 | 16.523 | 16.3576 | 16.1948 | 15.9903 | 15.6751 | 15.7521 | 12.087 | 8.506 | 4.0768 | 1.0897 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.4541 | 5.3193 | 5.1939 | 4.9004 | 4.5982 | 4.0902 | 3.5916 | 2.7551 | 1.5415 | 0.0081201 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.4541 | 5.3194 | 5.1936 | 4.9017 | 4.6036 | 4.0806 | 3.5575 | 2.6759 | 1.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.4541 | 5.3752 | 5.3409 | 5.3151 | 5.2696 | 5.2501 | 5.2923 | 5.1462 | 4.8071 | 4.2152 | 3.4221 | 2.5739 | 1.469 | 0.73619 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.4541 | 5.3183 | 5.185 | 4.8859 | 4.581 | 4.2002 | 3.9035 | 3.4216 | 2.6081 | 1.6613 | 0.23521 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | CROMFORD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.4541 | 5.3549 | 5.2867 | 5.1867 | 5.0576 | 4.9042 | 4.8012 | 4.3566 | 3.4898 | 2.296 | 0.89476 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 22.4507 | 22.2785 | 22.0846 | 21.6488 | 21.2236 | 20.8233 | 20.461 | 20.0776 | 19.7492 | 19.4456 | 19.1372 | 18.77 | 18.5073 | 16.8044 | 15.5111 | 12.4436 | 8.612
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 22.4507 | 22.2791 | 22.0768 | 21.5918 | 21.117 | 20.666 | 20.2407 | 19.7989 | 19.4007 | 19.0563 | 18.7442 | 18.4199 | 16.7714 | 16.6867 | 14.5982 | 11.0505 | 6.5615
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 22.4507 | 22.3805 | 22.3181 | 22.2566 | 22.1762 | 22.0953 | 22.0145 | 21.9414 | 21.8613 | 21.7959 | 21.7464 | 21.717 | 21.7123 | 21.7267 | 22.0364 | 22.1724 | 21.4936
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 22.4507 | 22.266 | 22.0358 | 21.5196 | 21.0262 | 20.5443 | 20.0838 | 19.6497 | 19.2387 | 18.8663 | 18.5305 | 16.7901 | 16.7028 | 16.4878 | 13.6864 | 9.6239 | 4.2025
Willington 132kV | DARLEY ABBEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 22.4507 | 22.3364 | 22.2116 | 22.0266 | 21.8144 | 21.5839 | 21.3586 | 21.1422 | 20.9327 | 20.7542 | 20.6027 | 20.4792 | 20.3853 | 20.3286 | 19.6381 | 16.8311 | 15.2879
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1292 | 19.432 | 19.3442 | 19.1502 | 18.9843 | 18.9536 | 18.8325 | 18.6009 | 18.359 | 18.083 | 17.4861 | 17.0166 | 16.4267 | 15.8462 | 13.5487 | 10.7202 | 3.3241
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1292 | 19.4295 | 19.3383 | 19.1204 | 18.9298 | 18.7861 | 18.5832 | 18.2525 | 17.6168 | 17.2504 | 16.7392 | 16.1645 | 15.526 | 14.9809 | 12.5818 | 8.3187 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1292 | 20.0998 | 19.4429 | 19.4113 | 19.3902 | 19.4729 | 19.4957 | 19.4417 | 19.3733 | 19.2374 | 19.0605 | 18.8787 | 18.6532 | 18.5005 | 18.3027 | 17.6668 | 17.1534
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1292 | 19.4255 | 19.3236 | 19.0942 | 18.8981 | 18.8282 | 18.6578 | 18.3928 | 18.1289 | 17.5432 | 17.171 | 16.654 | 16.008 | 15.368 | 12.6054 | 0 | 0
Willington 132kV | DENBY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1292 | 19.456 | 19.4021 | 19.3179 | 19.2416 | 19.243 | 19.1933 | 19.0153 | 18.7903 | 18.4443 | 18.1092 | 17.5537 | 17.2102 | 16.9311 | 15.9579 | 14.3255 | 12.2613
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 106.457 | 105.6522 | 105.4631 | 104.9337 | 104.3931 | 103.8922 | 103.4847 | 103.0949 | 102.772 | 102.4902 | 102.2009 | 101.8104 | 101.5249 | 101.2654 | 100.1125 | 82.6423 | 79.3108
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 106.457 | 105.6592 | 105.4744 | 104.9125 | 104.3318 | 103.7843 | 103.3224 | 102.8774 | 102.4965 | 102.1748 | 101.8703 | 101.4747 | 101.18 | 100.9095 | 99.9518 | 81.9635 | 77.6774
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 106.457 | 106.1745 | 105.701 | 105.6132 | 105.5023 | 105.3945 | 105.3062 | 105.2209 | 105.1197 | 105.0331 | 104.9604 | 104.9057 | 104.875 | 104.8578 | 105.115 | 105.2532 | 104.5555
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 106.457 | 105.644 | 105.451 | 104.8705 | 104.2688 | 103.6955 | 103.2156 | 102.7904 | 102.3965 | 102.0256 | 101.6697 | 101.3543 | 101.0752 | 100.8112 | 83.3144 | 81.0006 | 75.2764
Willington 132kV | DERBY 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 106.457 | 105.7122 | 105.621 | 105.4035 | 105.1139 | 104.8043 | 104.5416 | 104.2914 | 104.0515 | 103.8262 | 103.6224 | 103.4502 | 103.314 | 103.2186 | 102.4385 | 101.0437 | 100.2372
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 100.1183 | 97.2883 | 94.8247 | 91.0368 | 85.1243 | 79.2108 | 73.7463 | 67.7355 | 61.8233 | 55.9042 | 48.9773 | 40.2582 | 31.65 | 23.562 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 100.1183 | 97.2871 | 94.6981 | 90.1427 | 83.2505 | 76.2767 | 69.3062 | 61.4479 | 53.2817 | 45.0683 | 36.6463 | 27.106 | 17.891 | 9.4679 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 100.1183 | 98.7009 | 98.0574 | 99.0099 | 98.0137 | 96.9359 | 95.817 | 94.6094 | 92.9682 | 91.1052 | 88.813 | 86.9749 | 84.8963 | 83.5906 | 84.635 | 78.7379 | 65.8931
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 100.1183 | 97.1615 | 94.2617 | 89.2327 | 82.6693 | 75.6593 | 68.8814 | 62.0827 | 54.8395 | 47.689 | 39.7118 | 31.133 | 21.5511 | 11.8936 | 0 | 0 | 0
Willington 132kV | DERBY 132kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 100.1183 | 98.1468 | 96.7137 | 96.1399 | 93.1738 | 89.8839 | 86.4794 | 82.7596 | 78.3759 | 73.7911 | 69.1846 | 65.0042 | 60.6049 | 57.8027 | 38.6938 | 7.1823 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 67.7204 | 65.5704 | 63.2979 | 58.3667 | 53.592 | 48.9501 | 44.8633 | 40.4079 | 36.3675 | 32.7419 | 29.0237 | 24.3719 | 6.3633 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 67.7204 | 65.617 | 63.2962 | 57.9124 | 52.6672 | 47.4519 | 42.6962 | 37.539 | 32.6676 | 28.4718 | 24.4843 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 67.7204 | 66.6424 | 65.8585 | 65.0013 | 64.2148 | 63.49 | 62.8718 | 62.2357 | 61.4231 | 60.7377 | 60.1842 | 59.7347 | 59.4828 | 59.4414 | 61.4963 | 62.8254 | 55.1186
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 67.7204 | 65.4787 | 62.87 | 57.1674 | 51.7204 | 46.2717 | 41.1585 | 35.9976 | 30.837 | 26.1426 | 21.4859 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | DERBY SOUTH 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 67.7204 | 66.2391 | 64.7946 | 62.6759 | 60.3118 | 57.674 | 55.3224 | 52.8958 | 50.4626 | 48.4074 | 46.5335 | 44.9325 | 43.6474 | 42.7516 | 21.78 | 0 | 0
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.8911 | 20.8602 | 20.8197 | 20.6808 | 20.5358 | 20.4049 | 20.299 | 20.188 | 20.0839 | 19.9985 | 19.8955 | 19.7726 | 19.6696 | 19.5735 | 18.9393 | 17.1941 | 16.6555
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.8911 | 20.8631 | 20.8255 | 20.6848 | 20.5344 | 20.3966 | 20.2781 | 20.153 | 20.0359 | 19.9377 | 19.8262 | 19.6941 | 19.5796 | 19.4698 | 18.7722 | 17.1653 | 16.4381
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.8911 | 20.8718 | 20.8594 | 20.8202 | 20.785 | 20.7523 | 20.7228 | 20.6919 | 20.6541 | 20.6272 | 20.596 | 20.5675 | 20.5436 | 20.5212 | 20.4667 | 20.419 | 20.1901
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.8911 | 20.8644 | 20.8244 | 20.6823 | 20.5318 | 20.3922 | 20.2736 | 20.1522 | 20.0229 | 19.9127 | 19.7881 | 19.6717 | 19.5619 | 19.4436 | 18.6208 | 17.0912 | 16.1059
Willington 132kV | EAGLE CENTRE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.8911 | 20.871 | 20.8535 | 20.7874 | 20.708 | 20.6299 | 20.5619 | 20.4923 | 20.4182 | 20.3584 | 20.2885 | 20.2294 | 20.1738 | 20.1294 | 19.861 | 19.3392 | 18.6991
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 30.5616 | 30.172 | 29.9927 | 29.5751 | 29.1396 | 28.7205 | 28.3246 | 27.9034 | 27.4687 | 27.0199 | 26.5019 | 25.8588 | 25.2353 | 24.6618 | 21.6702 | 13.5566 | 3.3341
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 30.5616 | 30.1712 | 29.9904 | 29.5291 | 29.047 | 28.5613 | 28.0682 | 27.5166 | 26.9253 | 26.2932 | 25.6732 | 24.9435 | 24.2444 | 23.6328 | 20.242 | 8.3437 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 30.5616 | 30.5017 | 30.189 | 30.128 | 30.046 | 29.9572 | 29.8592 | 29.7464 | 29.5961 | 29.4255 | 29.2309 | 29.0405 | 28.8237 | 28.6739 | 28.598 | 28.3619 | 27.2748
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 30.5616 | 30.1617 | 29.9594 | 29.4704 | 28.972 | 28.4637 | 27.9634 | 27.474 | 26.9401 | 26.3546 | 25.7423 | 25.0827 | 24.3297 | 23.5728 | 19.2203 | 0 | 0
Willington 132kV | HEANOR 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 30.5616 | 30.2167 | 30.1085 | 29.9367 | 29.7251 | 29.4755 | 29.2129 | 28.9133 | 28.5487 | 28.132 | 27.7108 | 27.3185 | 26.9061 | 26.6215 | 25.3272 | 22.682 | 19.3806
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 85.7616 | 77.9912 | 75.5598 | 69.878 | 64.3652 | 58.8995 | 53.2099 | 46.338 | 38.5339 | 30.1975 | 19.9174 | 7.3776 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 85.7616 | 77.3254 | 73.9455 | 65.5955 | 57.5285 | 49.0761 | 40.1425 | 29.4568 | 17.3548 | 3.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 85.7616 | 82.8174 | 77.8656 | 76.8197 | 75.5962 | 74.5525 | 73.0777 | 70.9453 | 67.8226 | 63.6185 | 58.5166 | 53.4127 | 47.2397 | 43.1361 | 39.8628 | 32.528 | 11.6588
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 85.7616 | 77.1676 | 73.3887 | 64.6228 | 56.3156 | 48.0609 | 39.5626 | 30.7789 | 20.5895 | 9.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HEANOR 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 85.7616 | 78.3094 | 76.3665 | 73.231 | 69.7268 | 65.8039 | 61.3442 | 55.3433 | 47.4432 | 37.9628 | 27.7251 | 18.0533 | 7.2615 | 0.12956 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 5.5179 | 5.3815 | 5.2546 | 4.9577 | 4.652 | 4.138 | 3.6336 | 2.7873 | 1.5596 | 0.008215 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 5.5179 | 5.3816 | 5.2543 | 4.959 | 4.6575 | 4.1283 | 3.5991 | 2.7072 | 1.4112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 5.5179 | 5.438 | 5.4033 | 5.3772 | 5.3312 | 5.3115 | 5.3542 | 5.2063 | 4.8633 | 4.2645 | 3.4621 | 2.604 | 1.4862 | 0.74479 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 5.5179 | 5.3805 | 5.2456 | 4.943 | 4.6346 | 4.2493 | 3.9491 | 3.4616 | 2.6386 | 1.6807 | 0.23796 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | HOPTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 5.5179 | 5.4175 | 5.3485 | 5.2473 | 5.1168 | 4.9616 | 4.8574 | 4.4076 | 3.5306 | 2.3228 | 0.90522 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 2.9528 | 2.0466 | 1.9033 | 1.4551 | 1.0364 | 0.63691 | 0.23466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61897 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 2.9528 | 2.0429 | 1.8953 | 1.388 | 0.90823 | 0.43225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 2.9528 | 2.8827 | 2.132 | 2.0919 | 2.0582 | 2.015 | 1.9645 | 1.8985 | 1.7686 | 1.6012 | 1.3949 | 1.1879 | 0.94069 | 0.78564 | 0.79371 | 0.66277 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 2.9528 | 2.0317 | 1.8571 | 1.3264 | 0.84378 | 0.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ILKESTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 2.9528 | 2.1067 | 2.0511 | 1.8803 | 1.6936 | 1.4639 | 1.2241 | 0.93002 | 0.52453 | 0.097177 | 0 | 0 | 0 | 0 | 4.2215 | 1.7867 | 0
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.7541 | 16.5068 | 16.4317 | 16.2934 | 16.1594 | 16.0311 | 15.9219 | 15.8137 | 15.3258 | 15.178 | 14.7807 | 14.2017 | 13.4612 | 12.8887 | 11.0928 | 9.1492 | 7.8013
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.7541 | 16.5073 | 16.4312 | 16.2775 | 16.1296 | 15.965 | 15.7914 | 15.2951 | 14.943 | 14.4243 | 13.806 | 13.1705 | 12.4349 | 11.9844 | 10.4835 | 8.5567 | 6.1267
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.7541 | 16.5405 | 16.5182 | 16.4948 | 16.4683 | 16.4338 | 16.387 | 16.3076 | 16.1635 | 15.9436 | 15.72 | 15.2119 | 14.8486 | 14.5905 | 14.328 | 13.9365 | 13.3137
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.7541 | 16.5035 | 16.42 | 16.2583 | 16.1065 | 15.9565 | 15.8265 | 15.732 | 15.2471 | 15.0177 | 14.5806 | 13.9991 | 13.2308 | 12.6223 | 10.5116 | 8.2673 | 6.4242
Willington 132kV | INFINITY PARK 33 11 kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.7541 | 16.5274 | 16.4768 | 16.4161 | 16.3455 | 16.2484 | 16.125 | 15.9294 | 15.333 | 15.0696 | 14.6004 | 14.1271 | 13.5483 | 13.1885 | 12.3402 | 11.0271 | 9.3059
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 32.8727 | 32.7521 | 32.6098 | 32.2785 | 31.964 | 31.6979 | 31.4321 | 31.1427 | 30.8803 | 30.6656 | 30.4792 | 30.3401 | 27.5084 | 27.3681 | 25.5088 | 22.084 | 18.0579
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 32.8727 | 32.7364 | 32.5624 | 32.1502 | 31.7627 | 31.4262 | 31.099 | 30.7703 | 30.5094 | 30.3725 | 27.4989 | 27.3371 | 26.9842 | 26.568 | 23.4994 | 19.2584 | 14.2907
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 32.8727 | 32.8085 | 32.7496 | 32.6862 | 32.6127 | 32.5583 | 32.4732 | 32.3674 | 32.2238 | 32.0472 | 31.8455 | 31.6464 | 31.4103 | 31.2537 | 31.1101 | 30.9198 | 30.2748
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 32.8727 | 32.7296 | 32.538 | 32.1105 | 31.723 | 31.3994 | 31.0722 | 30.773 | 30.5131 | 30.3776 | 27.4965 | 27.2794 | 26.8291 | 26.2447 | 22.4732 | 5.1868 | 0
Willington 132kV | LITTLE HALLAM 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 32.8727 | 32.7807 | 32.6717 | 32.5134 | 32.3259 | 32.1359 | 31.9212 | 31.6691 | 31.365 | 31.0671 | 30.7881 | 30.5667 | 30.3781 | 30.3104 | 27.131 | 25.2994 | 22.6409
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.0503 | 18.9186 | 18.885 | 18.837 | 17.025 | 16.8208 | 16.3588 | 15.9144 | 15.343 | 14.647 | 13.8964 | 13.1719 | 11.435 | 6.1889 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.0503 | 18.9185 | 18.8848 | 18.8369 | 17.0249 | 16.8207 | 16.3597 | 15.9162 | 15.3465 | 14.6504 | 13.9019 | 13.1804 | 11.4159 | 6.2307 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.0503 | 19.0234 | 18.9001 | 18.8758 | 18.8514 | 18.822 | 18.7883 | 18.7413 | 18.6899 | 17.0632 | 16.9638 | 16.7604 | 16.4078 | 16.1457 | 15.6918 | 15.1223 | 14.5087
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.0503 | 18.919 | 18.8853 | 18.8382 | 17.0226 | 16.7876 | 16.3297 | 16.0052 | 15.595 | 15.1498 | 14.5748 | 13.9152 | 13.0854 | 11.4585 | 0 | 0 | 0
Willington 132kV | LONGCLIFFE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.0503 | 18.9223 | 18.8945 | 18.8636 | 18.7688 | 18.7099 | 17.0168 | 16.9296 | 16.7054 | 16.324 | 15.8457 | 15.3712 | 14.7787 | 14.41 | 12.5478 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.1467 | 24.8761 | 24.6215 | 24.5815 | 24.0552 | 23.4836 | 22.9581 | 22.3943 | 21.8866 | 21.5929 | 17.8753 | 17.0653 | 15.8342 | 14.5925 | 8.803 | 1.4481 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.1467 | 24.8753 | 24.6104 | 24.434 | 23.829 | 23.1266 | 22.4362 | 21.7928 | 17.9921 | 17.4091 | 16.3492 | 15.0145 | 13.5056 | 12.2793 | 6.1735 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.1467 | 25.0105 | 24.9397 | 25.2855 | 25.2126 | 25.1221 | 25.0147 | 24.8683 | 24.6436 | 24.33 | 23.9513 | 23.5764 | 23.1323 | 22.8392 | 22.6478 | 22.1277 | 18.3777
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.1467 | 24.8688 | 24.5847 | 24.4515 | 23.851 | 23.1936 | 22.5845 | 22.0253 | 21.6321 | 17.9476 | 17.3489 | 16.316 | 14.911 | 13.4954 | 6.3009 | 0 | 0
Willington 132kV | MACKWORTH 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.1467 | 24.9631 | 24.8127 | 25.0392 | 24.7696 | 24.4537 | 24.1099 | 23.6602 | 23.0794 | 22.4447 | 21.8785 | 21.5686 | 18.0036 | 17.767 | 16.2178 | 12.6516 | 7.6977
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.3837 | 4.2233 | 4.2643 | 4.1719 | 3.8676 | 3.2648 | 2.5207 | 1.6117 | 0.18344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.3837 | 4.2121 | 4.2307 | 4.0931 | 3.747 | 3.1073 | 2.3233 | 1.3752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.3837 | 4.3661 | 4.2715 | 4.2487 | 4.2208 | 4.1664 | 4.076 | 3.8729 | 3.479 | 2.8101 | 1.9186 | 0.95992 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.3837 | 4.2165 | 4.2293 | 4.0973 | 3.7524 | 3.1881 | 2.5986 | 2.0773 | 1.2699 | 0.22888 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MARCHINGTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.3837 | 4.2299 | 4.2736 | 4.2145 | 4.0742 | 3.8521 | 3.5407 | 2.9973 | 1.9531 | 0.47183 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.5414 | 19.4097 | 19.2313 | 18.8111 | 18.4114 | 17.5534 | 17.1452 | 16.5504 | 15.8596 | 15.0958 | 14.2288 | 13.3074 | 11.3542 | 6.1451 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.5414 | 19.4141 | 19.2403 | 18.8285 | 18.4359 | 17.5638 | 17.1935 | 16.6155 | 15.9438 | 15.1855 | 14.35 | 13.4567 | 11.3352 | 6.1867 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.5414 | 19.4864 | 19.4285 | 19.3581 | 19.2916 | 19.255 | 19.2044 | 19.1341 | 19.0072 | 18.7963 | 18.5326 | 18.2671 | 17.5727 | 17.4902 | 17.4106 | 17.2436 | 16.5494
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.5414 | 19.4067 | 19.2118 | 18.7762 | 18.3732 | 17.564 | 17.2566 | 16.845 | 16.2785 | 15.7131 | 15.0107 | 14.2404 | 13.3661 | 11.3776 | 0 | 0 | 0
Willington 132kV | MATLOCK 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.5414 | 19.4598 | 19.3575 | 19.1917 | 19.0078 | 18.814 | 18.5957 | 18.3403 | 17.5777 | 17.3715 | 16.9643 | 16.5494 | 16.0619 | 15.7718 | 12.4592 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 14.351 | 14.2861 | 14.1677 | 13.8936 | 13.6144 | 13.2353 | 12.821 | 12.3622 | 11.7992 | 11.0911 | 10.1241 | 8.9218 | 7.4687 | 5.7268 | 1.7237 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 14.351 | 14.2839 | 14.1633 | 13.8883 | 13.6077 | 13.1535 | 12.6101 | 11.8998 | 10.9935 | 9.8447 | 8.5727 | 7.247 | 5.7273 | 4.6208 | 0 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 14.351 | 14.3167 | 14.2663 | 14.2124 | 14.1564 | 14.0888 | 14.0043 | 13.872 | 13.6724 | 13.341 | 12.9092 | 12.455 | 11.8768 | 11.4672 | 10.8164 | 11.9398 | 10.7777
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 14.351 | 14.2819 | 14.1547 | 13.8729 | 13.588 | 13.2013 | 12.775 | 12.3197 | 11.7543 | 11.0383 | 10.0736 | 8.9039 | 7.4513 | 5.7019 | 1.5186 | 0 | 0
Willington 132kV | MELBOURNE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 14.351 | 14.3098 | 14.2362 | 14.1252 | 13.9944 | 13.8153 | 13.5877 | 13.2308 | 12.7287 | 12.0166 | 11.2092 | 10.4193 | 9.4816 | 8.8124 | 7.9505 | 5.3277 | 2.109
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.9145 | 19.8522 | 19.7664 | 19.5567 | 19.3548 | 19.1591 | 18.986 | 18.8103 | 18.6644 | 18.5469 | 18.4542 | 17.5222 | 11.3576 | 6.147 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.9145 | 19.8523 | 19.7662 | 19.558 | 19.3569 | 19.164 | 18.991 | 18.8185 | 18.6743 | 18.5556 | 18.4659 | 17.8548 | 11.3386 | 6.1885 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.9145 | 19.8867 | 19.8578 | 19.8262 | 19.7854 | 19.7466 | 19.708 | 19.6725 | 19.632 | 19.5958 | 19.5656 | 19.5424 | 19.5252 | 19.5156 | 19.564 | 19.5724 | 19.2949
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.9145 | 19.8489 | 19.7534 | 19.5356 | 19.3302 | 19.1303 | 18.9519 | 18.7863 | 18.6395 | 18.5189 | 18.4357 | 17.4787 | 17.252 | 11.381 | 0 | 0 | 0
Willington 132kV | MILLCLOSE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.9145 | 19.8735 | 19.8213 | 19.7374 | 19.6392 | 19.5329 | 19.4356 | 19.3411 | 19.2533 | 19.1693 | 19.0914 | 19.0245 | 18.9694 | 18.9282 | 12.4629 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.9085 | 19.5638 | 19.5113 | 19.4249 | 19.3524 | 19.3011 | 16.6555 | 16.6366 | 16.5593 | 16.4272 | 16.2219 | 15.9313 | 15.6235 | 15.4091 | 12.2807 | 10.1924 | 3.3274
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.9085 | 19.5325 | 19.4446 | 19.3249 | 16.6054 | 16.4819 | 16.2626 | 15.9324 | 15.5143 | 15.0524 | 14.5382 | 13.9428 | 13.3365 | 12.8456 | 8.0435 | 4.3498 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.9085 | 19.5725 | 19.5335 | 19.4962 | 19.4523 | 19.4079 | 19.3633 | 19.3179 | 19.2714 | 16.6922 | 16.6809 | 16.6271 | 16.5096 | 16.4172 | 16.3884 | 16.2819 | 15.5891
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.9085 | 19.5285 | 19.4345 | 19.3205 | 16.5943 | 16.4533 | 16.232 | 15.9626 | 15.6104 | 15.2483 | 14.7835 | 14.2445 | 13.6005 | 12.983 | 7.4201 | 0 | 0
Willington 132kV | MOORGREEN 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.9085 | 19.5564 | 19.4962 | 19.4191 | 19.3485 | 19.2975 | 16.6512 | 16.6097 | 16.4803 | 16.2573 | 15.9573 | 15.6415 | 15.268 | 15.0428 | 13.0615 | 11.1524 | 8.654
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.5116 | 12.485 | 12.4573 | 12.4001 | 12.3477 | 12.28 | 12.2245 | 10.9527 | 10.9048 | 10.7739 | 10.5288 | 10.1922 | 9.7551 | 9.345 | 7.8487 | 5.9455 | 2.6927
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.5116 | 12.4838 | 12.4553 | 12.3926 | 12.335 | 12.2584 | 12.2085 | 10.9349 | 10.8198 | 10.5814 | 10.2439 | 9.8554 | 9.3864 | 8.9858 | 7.4811 | 5.4337 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.5116 | 12.4975 | 12.4887 | 12.4792 | 12.4688 | 12.4535 | 12.4328 | 12.3947 | 12.3268 | 12.2374 | 10.9457 | 10.9037 | 10.7839 | 10.6726 | 10.4884 | 10.1523 | 9.7062
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.5116 | 12.4831 | 12.452 | 12.3862 | 12.3283 | 12.2608 | 12.2153 | 10.9523 | 10.9139 | 10.8225 | 10.6214 | 10.3119 | 9.8733 | 9.419 | 7.6741 | 0 | 0
Willington 132kV | MORLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.5116 | 12.4923 | 12.4752 | 12.4501 | 12.4221 | 12.3817 | 12.3307 | 12.2527 | 10.9495 | 10.8665 | 10.6598 | 10.3942 | 10.034 | 9.7846 | 9.0964 | 8.0342 | 6.6969
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 36.9117 | 36.6257 | 36.3418 | 35.7221 | 35.1432 | 34.6012 | 34.1179 | 33.6221 | 33.2436 | 33.0274 | 29.7984 | 29.6981 | 29.5224 | 29.2935 | 26.9441 | 22.5618 | 17.0735
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 36.9117 | 36.6304 | 36.3303 | 35.6504 | 35.0149 | 34.4083 | 33.8681 | 33.3524 | 33.0446 | 29.7747 | 29.6812 | 29.4169 | 29.1223 | 28.7605 | 25.4049 | 20.3556 | 13.9229
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 36.9117 | 36.7642 | 36.6688 | 36.5643 | 36.4766 | 36.4064 | 36.3485 | 36.2849 | 36.2022 | 36.1341 | 36.0811 | 36.0402 | 36.0269 | 36.0416 | 36.4092 | 36.684 | 35.7335
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 36.9117 | 36.6129 | 36.2723 | 35.5515 | 34.8889 | 34.2671 | 33.688 | 33.215 | 30.767 | 29.7103 | 29.4952 | 29.1717 | 28.7797 | 28.3175 | 24.2627 | 18.4728 | 0
Willington 132kV | NORMANTON 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 36.9117 | 36.7097 | 36.5181 | 36.2495 | 35.9651 | 35.6516 | 35.3629 | 35.0629 | 34.7621 | 34.5163 | 34.2988 | 34.1185 | 33.9781 | 33.8825 | 33.064 | 29.4692 | 26.8103
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 12.935 | 12.9143 | 12.9042 | 12.8227 | 12.7437 | 12.6444 | 12.533 | 12.3971 | 12.2954 | 11.564 | 11.1937 | 10.7431 | 10.1691 | 9.7815 | 8.7873 | 7.8199 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 12.935 | 12.9061 | 12.8844 | 12.7762 | 12.6626 | 12.5116 | 12.3508 | 11.6622 | 11.2936 | 10.7361 | 10.068 | 9.3597 | 8.521 | 8.0397 | 4.5872 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 12.935 | 12.9229 | 12.9233 | 12.8985 | 12.8917 | 12.8752 | 12.8443 | 12.7779 | 12.6574 | 12.4637 | 12.2937 | 11.5911 | 11.2025 | 10.9025 | 10.4729 | 10.0717 | 9.5722
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 12.935 | 12.9059 | 12.8796 | 12.7646 | 12.6432 | 12.507 | 12.3585 | 11.6976 | 11.4673 | 11.0992 | 10.5192 | 9.7791 | 8.8862 | 8.3384 | 2.2796 | 0 | 0
Willington 132kV | RATCLIFFE ON SOAR 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 12.935 | 12.9213 | 12.9233 | 12.8827 | 12.8297 | 12.7364 | 12.6078 | 12.4173 | 11.6958 | 11.3889 | 10.8747 | 10.3337 | 9.6678 | 9.2905 | 8.2843 | 7.3303 | 6.1697
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 4.8411 | 4.7214 | 4.5642 | 4.2029 | 3.8451 | 3.5091 | 3.1944 | 2.8658 | 2.4941 | 2.0986 | 1.5959 | 0.96592 | 0.29334 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 4.8411 | 4.7156 | 4.5533 | 4.1539 | 3.7589 | 3.3644 | 2.9604 | 2.4892 | 1.9424 | 1.3088 | 0.66443 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 4.8411 | 4.7915 | 4.7445 | 4.6962 | 4.6321 | 4.5614 | 4.4818 | 4.3826 | 4.2352 | 4.0453 | 3.8157 | 3.5861 | 3.3104 | 3.1233 | 3.0212 | 2.702 | 1.7765
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 4.8411 | 4.7072 | 4.5273 | 4.1069 | 3.7011 | 3.2956 | 2.904 | 2.5232 | 2.0749 | 1.5827 | 1.022 | 0.38547 | 0 | 0 | 0 | 0 | 0
Willington 132kV | RIPLEY 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 4.8411 | 4.7636 | 4.6718 | 4.5233 | 4.3471 | 4.1356 | 3.9121 | 3.6377 | 3.2618 | 2.8025 | 2.3193 | 1.8646 | 1.3546 | 1.0055 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 16.8214 | 16.8322 | 16.837 | 16.8145 | 16.5575 | 15.9902 | 15.2132 | 14.334 | 13.0777 | 10.45 | 5.7642 | 1.0161 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 16.8214 | 16.8284 | 16.8218 | 16.751 | 16.3872 | 15.7113 | 14.8335 | 13.8598 | 11.4512 | 8.144 | 3.1687 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 16.8214 | 16.8343 | 16.8444 | 16.847 | 16.8459 | 16.8306 | 16.785 | 16.6605 | 16.3641 | 15.7959 | 14.9775 | 14.064 | 12.856 | 12.0291 | 10.775 | 7.1591 | 1.8837
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 16.8214 | 16.8279 | 16.82 | 16.7439 | 16.3626 | 15.719 | 14.9926 | 14.4433 | 13.5989 | 12.5355 | 8.8109 | 4.2375 | 0 | 0 | 0 | 0 | 0
Willington 132kV | ROCESTER 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 16.8214 | 16.8326 | 16.8377 | 16.825 | 16.7357 | 16.5348 | 16.2087 | 15.6914 | 14.7771 | 13.5126 | 12.0189 | 8.5026 | 4.0752 | 1.0892 | 0 | 0 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.1782 | 20.0622 | 19.9362 | 19.6454 | 19.367 | 19.1388 | 18.9472 | 18.7482 | 18.6032 | 18.4985 | 18.4093 | 18.2662 | 18.191 | 17.1278 | 16.4687 | 14.2814 | 11.5165
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.1782 | 20.0454 | 19.8819 | 19.5017 | 19.141 | 18.8318 | 18.5563 | 18.3028 | 17.7103 | 17.0709 | 17.0224 | 16.8993 | 16.7662 | 16.572 | 14.6617 | 11.6158 | 7.8807
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.1782 | 20.1219 | 20.0821 | 20.0425 | 19.9931 | 19.9788 | 19.9627 | 19.9407 | 19.9171 | 19.911 | 19.9234 | 19.9621 | 20.0226 | 20.074 | 20.3722 | 20.4977 | 19.9446
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.1782 | 20.0368 | 19.8549 | 19.4549 | 19.0844 | 18.7783 | 18.4902 | 18.2573 | 17.0797 | 17.0291 | 16.9189 | 16.7709 | 16.5912 | 16.3241 | 13.9075 | 5.1837 | 0
Willington 132kV | SANDIACRE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.1782 | 20.0895 | 19.9905 | 19.8523 | 19.6954 | 19.5575 | 19.4354 | 19.3167 | 19.2134 | 19.1418 | 19.103 | 19.0814 | 19.059 | 19.0264 | 18.5031 | 16.8292 | 15.1538
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 25.0748 | 23.9182 | 23.3579 | 23.3333 | 23.3285 | 23.3164 | 23.3142 | 23.294 | 23.3009 | 23.337 | 23.2788 | 23.1438 | 22.9634 | 22.7752 | 21.4163 | 19.0483 | 16.3615
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 25.0748 | 23.9182 | 23.35 | 23.2741 | 23.24 | 23.1483 | 23.0985 | 23.044 | 23.0414 | 23.0819 | 23.0254 | 22.8985 | 22.7205 | 22.5214 | 20.8277 | 18.1914 | 15.1153
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 25.0748 | 24.1228 | 25.0602 | 25.0866 | 25.1526 | 25.2411 | 25.3407 | 23.9058 | 23.9483 | 25.0156 | 25.0259 | 25.0752 | 25.1372 | 25.2097 | 25.3035 | 25.2456 | 24.0752
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 25.0748 | 23.9178 | 23.3286 | 23.2664 | 23.2287 | 23.2064 | 23.1646 | 23.1106 | 23.0507 | 23.0195 | 22.8712 | 22.7243 | 22.4951 | 22.2494 | 20.2478 | 17.3674 | 13.7087
Willington 132kV | SINFIN LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 25.0748 | 23.9199 | 25.0595 | 25.0632 | 25.1006 | 23.6338 | 23.6928 | 23.7542 | 23.8288 | 23.9063 | 23.928 | 23.9507 | 23.9467 | 23.9454 | 23.6155 | 22.4235 | 20.8209
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 40.5074 | 40.1447 | 39.79 | 39.049 | 38.349 | 37.6462 | 36.9774 | 36.3307 | 35.6802 | 35.3636 | 28.0451 | 26.9143 | 25.2556 | 23.6962 | 16.7233 | 7.0357 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 40.5074 | 40.1442 | 39.7705 | 38.9505 | 38.1809 | 37.388 | 36.6241 | 35.904 | 35.4174 | 28.0972 | 27.0819 | 25.4872 | 23.5634 | 21.9118 | 14.1256 | 3.6749 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 40.5074 | 40.3851 | 40.1949 | 40.0729 | 39.9392 | 39.7848 | 39.6002 | 39.3754 | 39.0095 | 38.508 | 37.9063 | 37.3018 | 36.6154 | 36.1927 | 35.7246 | 35.1441 | 28.4957
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 40.5074 | 40.1388 | 39.7328 | 38.8709 | 38.0846 | 37.3007 | 36.5753 | 35.9986 | 35.4948 | 28.3412 | 27.8169 | 26.5726 | 24.721 | 22.7791 | 13.4055 | 2.2388 | 0
Willington 132kV | SPONDON 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 40.5074 | 40.2465 | 40.0179 | 39.698 | 39.3277 | 38.8823 | 38.3884 | 37.8065 | 36.986 | 36.1477 | 35.5059 | 28.4133 | 27.9846 | 27.4155 | 24.7416 | 19.5222 | 12.4852
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 91.3963 | 88.6179 | 87.977 | 94.1528 | 87.9837 | 81.0331 | 73.9362 | 66.0377 | 55.2742 | 43.3979 | 28.4839 | 10.3879 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 91.3963 | 88.575 | 87.9353 | 91.7048 | 84.4975 | 75.875 | 66.5791 | 55.4054 | 41.4934 | 25.5804 | 8.2181 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 91.3963 | 90.4194 | 91.022 | 100.7958 | 100.3612 | 99.6959 | 98.7481 | 97.2336 | 94.4165 | 90.0575 | 84.5058 | 78.6691 | 71.3299 | 65.8566 | 59.318 | 55.9899 | 33.0507
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 91.3963 | 88.4845 | 87.3862 | 92.5225 | 85.5083 | 77.5631 | 69.3717 | 61.2856 | 50.1272 | 38.4472 | 23.3563 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | SPONDON B 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 91.3963 | 89.5246 | 90.3046 | 99.0713 | 96.1527 | 92.3353 | 87.9651 | 82.17 | 73.6237 | 62.9709 | 51.1513 | 39.4519 | 25.9953 | 16.8561 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 53.5878 | 49.3078 | 47.6976 | 43.3936 | 39.2457 | 35.5453 | 31.9371 | 27.8183 | 23.6865 | 19.8452 | 15.7957 | 10.5648 | 3.138 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 53.5878 | 49.1601 | 47.2429 | 41.9754 | 36.8776 | 32.1458 | 27.4252 | 22.1136 | 16.6087 | 11.5933 | 6.6438 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 53.5878 | 52.9202 | 49.7546 | 49.2244 | 48.6309 | 48.2202 | 47.6371 | 46.8755 | 45.6879 | 44.2668 | 42.6279 | 41.0874 | 39.2782 | 38.1521 | 38.8818 | 38.1067 | 28.3578
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 53.5878 | 49.0538 | 46.8818 | 41.3668 | 36.2029 | 31.5254 | 26.7204 | 21.7668 | 16.2126 | 11.2155 | 5.6886 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | STANTON 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 53.5878 | 49.7673 | 48.7477 | 46.9028 | 44.7758 | 42.5295 | 40.1595 | 37.3907 | 33.951 | 30.4952 | 27.0074 | 23.8083 | 20.2104 | 17.8637 | 10.7406 | 0 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 20.0369 | 19.993 | 19.9366 | 22.8913 | 22.9959 | 23.0993 | 23.1964 | 23.2834 | 23.1879 | 23.1029 | 23.0151 | 22.8761 | 22.749 | 22.6166 | 22.2558 | 21.3261 | 2.6865
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 20.0369 | 19.9928 | 19.9357 | 22.5115 | 22.5463 | 22.5651 | 22.5923 | 22.6166 | 22.6534 | 22.6953 | 22.7486 | 22.7358 | 22.7297 | 22.7175 | 22.0024 | 12.1273 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 20.0369 | 20.0068 | 19.9784 | 22.4058 | 22.5387 | 22.667 | 22.7922 | 22.9087 | 23.0261 | 23.1469 | 23.272 | 23.3805 | 23.4875 | 23.4556 | 23.2345 | 22.9671 | 22.6042
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 20.0369 | 19.9916 | 19.9319 | 22.8878 | 22.9929 | 23.0973 | 23.1944 | 23.2884 | 23.1979 | 23.1138 | 23.0313 | 22.9079 | 22.7856 | 22.6562 | 22.2649 | 12.2529 | 0
Willington 132kV | TRENT LANE 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 20.0369 | 20.0015 | 19.9625 | 22.5966 | 22.6786 | 22.738 | 22.8048 | 22.8711 | 22.9438 | 23.0182 | 23.1082 | 23.1439 | 23.1824 | 23.2211 | 22.818 | 22.6457 | 22.0448
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 24.5868 | 23.0572 | 22.6151 | 20.9721 | 16.3235 | 9.0545 | 0.77244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 24.5868 | 22.7314 | 21.7924 | 18.9052 | 13.0359 | 4.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 24.5868 | 23.7162 | 22.9636 | 22.3671 | 21.9667 | 21.2998 | 20.4142 | 18.508 | 14.9964 | 11.3128 | 3.9062 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 24.5868 | 22.7036 | 21.6744 | 18.6922 | 12.6131 | 4.6105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | UTTOXETER 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 24.5868 | 23.0737 | 22.6435 | 21.4349 | 19.1422 | 15.8268 | 11.9567 | 6.3546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.8569 | 19.8783 | 19.8385 | 19.7543 | 19.6839 | 19.5668 | 19.4543 | 19.3331 | 19.2294 | 19.1413 | 19.047 | 18.9218 | 18.8279 | 18.7385 | 17.6846 | 16.7766 | 3.3231
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.8569 | 19.8501 | 19.7702 | 19.5788 | 19.4077 | 19.2028 | 18.9985 | 18.7874 | 18.595 | 18.4376 | 18.3192 | 17.3132 | 17.2619 | 17.1589 | 15.9875 | 8.3162 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.8569 | 19.8736 | 19.8477 | 19.8204 | 19.8024 | 19.7688 | 19.7364 | 19.7031 | 19.6659 | 19.6322 | 19.6044 | 19.5853 | 19.5685 | 19.558 | 19.5958 | 19.5852 | 19.2943
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.8569 | 19.8502 | 19.7633 | 19.5638 | 19.3876 | 19.1842 | 18.9861 | 18.7906 | 18.584 | 18.4252 | 18.3096 | 17.3141 | 17.2682 | 17.1607 | 15.8137 | 0 | 0
Willington 132kV | WATNALL 33 11KV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.8569 | 19.8725 | 19.8243 | 19.7485 | 19.6777 | 19.5857 | 19.4951 | 19.4008 | 19.3059 | 19.2203 | 19.1386 | 19.0678 | 19.0081 | 18.9615 | 18.5837 | 17.3586 | 16.7398
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Best View | Headroom (MW) | 19.5436 | 19.5136 | 19.5204 | 19.4435 | 19.3776 | 19.2546 | 19.1115 | 18.9186 | 18.6565 | 18.4189 | 18.1196 | 17.183 | 17.0368 | 16.8182 | 15.5417 | 13.0753 | 3.3254
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Consumer Transformation | Headroom (MW) | 19.5436 | 19.4502 | 19.3638 | 19.0908 | 18.8383 | 18.5365 | 18.2252 | 17.1709 | 17.0223 | 16.7092 | 16.2748 | 15.7519 | 15.1947 | 14.68 | 12.0619 | 8.2879 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Falling Short | Headroom (MW) | 19.5436 | 19.511 | 19.5011 | 19.4912 | 19.4743 | 19.4358 | 19.3802 | 19.3037 | 19.185 | 19.0371 | 18.8449 | 18.6503 | 18.4116 | 18.2571 | 18.1547 | 17.3131 | 16.9303
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | Leading the Way | Headroom (MW) | 19.5436 | 19.4439 | 19.3384 | 19.052 | 18.7893 | 18.4886 | 18.1939 | 17.1732 | 17.0743 | 16.8662 | 16.5039 | 16.047 | 15.4734 | 14.8581 | 11.6746 | 0 | 0
Willington 132kV | WESTWOOD 33 11kV S STN | Primary Substation | 11 | System Transformation | Headroom (MW) | 19.5436 | 19.4862 | 19.4519 | 19.367 | 19.2727 | 19.1282 | 18.9616 | 18.7453 | 18.4422 | 18.1314 | 17.1722 | 17.0154 | 16.7123 | 16.4948 | 15.6201 | 13.807 | 11.4087
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Best View | Headroom (MW) | 51.3898 | 48.4146 | 46.0445 | 40.2937 | 32.1754 | 21.1546 | 9.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Consumer Transformation | Headroom (MW) | 51.3898 | 48.4221 | 46.05 | 40.3033 | 32.1997 | 21.1807 | 9.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Falling Short | Headroom (MW) | 51.3898 | 50.3009 | 48.6437 | 47.8647 | 47.0415 | 46.3115 | 45.6011 | 43.8386 | 40.1386 | 33.98 | 25.8817 | 17.2358 | 6.0946 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | Leading the Way | Headroom (MW) | 51.3898 | 48.3563 | 45.7514 | 39.7952 | 31.3575 | 21.1536 | 11.0431 | 2.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | WINSTER 33kV S STN | Bulk Supply Point | 33 | System Transformation | Headroom (MW) | 51.3898 | 49.0303 | 47.6776 | 45.5079 | 42.2581 | 38.11 | 33.7895 | 27.8643 | 17.7544 | 4.4618 | 0 | 0 | 0 | 0 | 0 | 0 | 0