## Appendix G Mk1
Appendix G Information | [15 empty] | Site Specific Technical Conditions
Licence Area | GSP | Part 1 [MW] | Part 2 [MW] | Part 3 [MW] | Part 4 [MW] | Part 5 [MW] | Total Aggregated Developer Capacity [MW] | Fault Level Headroom [kA] | Connection Asset Reverse Power Limits [MVA] | Approved Copy of Appendix G | Last Reviewed | Subject to Project Progression | Capacity in Project Progression | Technology Restriction | Materiality Headroom Subject to Completion of Transmission Works | Power Factor Range | Emergency Disconnection | SGT ANM
East Midlands | Drakelow | 45 | 116.45 | 0 | 318.5 | 0 | 479.95 | 1.46 | N/A | 2024-06-03 | 2024-06-18 | Yes | 54.9 | BESS subject to Project Progression/Modification Application | Installation of a new SGT. Expected Completion Date October 2029. | Yes | Yes | No
East Midlands | East Claydon | 187.23 | 215.63 | 0 | 297.19 | 0 | 700.05 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 326.79 | BESS subject to Project Progression/Modification Application | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2031. | Yes | Yes | No
East Midlands | Grendon | 662.98 | 450 | 0 | 605.8 | 0 | 1718.78 | 2.461 | N/A | 2024-06-03 | 2024-06-18 | Yes | 728.75 | BESS subject to Project Progression/Modification Application | New GSP Proposed. Expected Completion Date October 2031. | Yes | Yes | No
East Midlands | Lea Marston | 21.65 | 212.254 | 0 | 71.2 | 0 | 305.104 | 1.72 | N/A | 2024-06-03 | 2024-06-18 | Yes | 69.9 | BESS subject to Project Progression/Modification Application | Installation of an additional SGT and Wider transmission reinforcement works. Expected Completion Date June 2033. | Yes | Yes | No
East Midlands | Ratcliffe | 196.915 | 144.31 | 0 | 1318.95 | 0 | 1660.175 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 476.9 | N/A | New GSP Proposed. Expected Completion Date October 2033. | Yes | Yes | No
East Midlands | Walpole | 198.4 | 141.6 | 0 | 332.7 | 0 | 672.7 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 349.6 | BESS subject to Project Progression/Modification Application | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2030. | Yes | Yes | No
East Midlands | West Burton | 29.51 | 236.36 | 0 | 250.9 | 0 | 516.77 | 0 | 480 | 2024-06-03 | 2024-06-18 | Yes | 289.88 | BESS subject to Project Progression/Modification Application | Wider transmission reinforcement works. Expected Completion Date May 2033. | Yes | Yes | Yes
East Midlands | Willington | 386.617 | 114.948 | 0 | 388.2 | 0 | 901.465 | 0.173 | N/A | 2024-06-03 | 2024-06-18 | Yes | 675.49 | N/A | Installation of a new SGT and Wider transmission reinforcement works. Expected Completion Date October 2034. | Yes | Yes | No
West Midlands | Cellarhead | 135.49 | 175.69 | 0 | 562.2 | 0 | 873.38 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 256.1 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date November 2033. | Yes | Yes | No
West Midlands | East Claydon | 12.26 | 13.05 | 0 | 95.4 | 0 | 120.71 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 152.2 | BESS subject to Project Progression/Modification Application | N/A | Yes | Yes | No
West Midlands | Iron Acton | 64.5 | 172.3 | 0 | 1019.482 | 0 | 1256.3 | 0 | N/A | 2034-06-03 | 2024-06-18 | Yes | 309.3 | BESS subject to Project Progression/Modification Application | New GSP Proposed. Expected Completion Date December 2036. | Yes | Yes | No
West Midlands | Ironbridge | 57.521 | 133 | 0 | 572.6 | 0 | 763.12 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 104.9 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2033. | Yes | Yes | No
West Midlands | Lea Marston | 22.095 | 45.1 | 0 | 395.8 | 0 | 462.995 | 1.47 | N/A | 2024-06-03 | 2024-06-18 | Yes | 516.3 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date June 2033. | Yes | Yes | No
West Midlands | Ocker Hill | 4 | 63.2 | 0 | 199.3 | 0 | 266.5 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 117.9 | BESS subject to Project Progression/Modification Application | Substaion rebuild, subject to further assessment. Expected Completion Date October 2027. | Yes | Yes | No
West Midlands | Oldbury | 38.506 | 60 | 0 | 0 | 0 | 108.506 | 1.623 | 240 | 2024-06-03 | 2024-06-18 | Yes | 148.9 | N/A | N/A | Yes | Yes | No
West Midlands | Rugeley | 18 | 52 | 0 | 555.4 | 0 | 625.4 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 299.2 | N/A | New GSP Proposed. Expected Completion Date June 2034. | Yes | Yes | No
West Midlands | Shrewsbury | 53.07 | 55.08 | 0 | 55 | 0 | 163.15 | 0 | N/A | 2024-06-03 | 2024-06-18 | Yes | 399.7 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2032. | Yes | Yes | No
South West | Iron Acton | 86 | 190.77 | 0 | 1019.482 | 0 | 1256.3 | 1.1917 | N/A | 2024-05-27 | 2024-06-18 | Yes | 221.2 | BESS subject to Project Progression/Modification Application | New GSP Proposed. Expected Completion Date December 2036. | Yes | Yes | No
South West | Melksham | 0 | 0 | 0 | 149.3 | 0 | 149.3 | 0 | N/A | 2024-05-29 | 2024-06-18 | No | 0 | BESS subject to Project Progression/Modification Application | New GSP Proposed. Expected Completion Date November 2037. | Yes | Yes | No
South West | Seabank | 84.121 | 308.23 | 0 | 83.66 | 0 | 476.011 | 3 | 240 | 2024-05-30 | 2024-06-18 | Yes | 212 | BESS subject to Project Progression/Modification Application | Attributable and Wider transmission reinforcement works. Expected Completion Date December 2036. | Yes | Yes | No
South Wales | Aberthaw | 23.98 | 106.3768 | 0 | 247.38 | 0 | 377.7368 | 3 | N/A | 2023-11-27 | 2024-06-18 | Yes | 69.9 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | No
South Wales | Pembroke | 164.1775 | 237.99 | 0 | 0 | 0 | 402.1475 | 1.506 | N/A | 2024-03-04 | 2024-06-18 | Yes | 72.37 | BESS subject to Project Progression/Modification Application | N/A | Yes | Yes | No
South Wales | Swansea North | 438.728 | 758.1054 | 0 | 49.9 | 0 | 1246.1 | 0.232 | 480 | 2024-02-16 | 2024-06-18 | Yes | 315.649 | BESS subject to Project Progression/Modification Application | N/A | Yes | Yes | Yes
South Wales | Uskmouth | 29.9 | 421.915 | 0 | 183.04 | 0 | 634.855 | 0 | N/A | 2023-11-20 | 2024-06-18 | Yes | 45.8 | N/A | SGT replacement works and Wider transmission reinforecement works. Expected Completion Date October 2029. | Yes | Yes | No
[16 empty] | In order to allow NGED to contain voltage within acceptable limits at the National Electricity Transmission System (NETS)/ Distribution System interface, the Customer must ensure that the generators (≥1MW) have the capability to operate between 0.95 leading and 0.95 lagging power factor. Customers will be advised of the target Power Factor within this range. | National Grid Electricity Transmission (NGET) has instructed that NGED shall maintain a facility such that under emergency conditions on the National Electricity Transmission System (NETS), NGED shall have the ability to de-energise embedded generation (≥1MW) upon instruction from NGET. | The Customer’s generation will be included in the SGT Active Network Management Scheme (ANM) .The SGT ANM will automatically curtail the output of the Customer’s generation in order to control power flow in reverse direction through the Supergrid Transformers (SGTs) at this Grid Supply Point

## Appendix G Mk2
Appendix G Information | [12 empty] | Site Specific Technical Conditions
Licence Area | GSP | Total MW Table 1 | Total Developer Capacity [MW] | Materiality Trigger [MW] | Fault Level Headroom [kA] | Connection Asset Reverse Power Limits [MVA] | Approved Copy of Appendix G | Last Reviewed | Subject to Materiality Trigger Study | Capacity in Materiality Trigger Study | Technology Restriction | Materiality Headroom Subject to Completion of Transmission Works | Power Factor Range | Emergency Disconnection | SGT ANM | SWOT | Connect & Manage | Operational Visibility and Commercial Control | Technical Limits
East Midlands | Berkswell | 677.1 | 408 | 689.1 | 3 | 240 | 2024-06-03 | 2024-06-18 | Yes | 587.1 | BESS subject to Project Progression/Modification Application | Installation of a new SGT and Wider transmission reinforcement works. Expected Completion Date June 2033. | Yes | Yes | No | No | No | Yes | Yes
East Midlands | Bicker Fen | 559.38 | 0 | 559.38 | 2.616 | 240 | 2024-06-03 | 2024-06-18 | Yes | 827.1 | N/A | Installation of a new SGT and Wider transmission reinforcement works. Expected Completion Date October 2033. | Yes | Yes | Yes | No | No | Yes | Yes
East Midlands | Chesterfield | 1046.93 | 160.7 | 1046.93 | 3 | 480 | 2024-06-03 | 2024-06-18 | Yes | 622.9 | BESS subject to Project Progression/Modification Application | Uprating of connection assets. Expected Completion Date October 2032. | Yes | Yes | Yes | No | No | Yes | Yes
East Midlands | Coventry | 679.96 | 143.6 | 679.96 | 3 | 180 | 2024-06-03 | 2024-06-18 | Yes | 823 | N/A | Installation of a new SGT and Wider transmission reinforcement works. Expected Completion Date October 2028. | Yes | Yes | No | No | No | Yes | Yes
East Midlands | Enderby | 368.88 | 48 | 368.88 | 3 | 480 | 2024-06-03 | 2024-06-18 | Yes | 337.3 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2032. | Yes | Yes | No | No | No | Yes | Yes
East Midlands | Staythorpe | 978.55 | 64.5 | 978.55 | 3 | 240 | 2024-06-03 | 2024-06-18 | Yes | 216.35 | N/A | Installation of an additional SGT and Wider transmission reinforcement works. Expected Completion Date October 2030. | Yes | Yes | Yes | No | No | Yes | Yes
East Midlands | Stoke Bardolph | 146.186 | 49.9 | 146.186 | 2.852 | 240 | 2024-06-03 | 2024-06-18 | Yes | 194.4 | N/A | Wider transmission reinforcement works. Expected Completion Date October 2032. | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Bishops Wood | 909.11 | 239.6 | 909.11 | 3 | 480 | 2024-12-18 | 2024-06-18 | Yes | 707.2 | N/A | SGT replacements, substation extension works and Wider transmission reinforcement works. Expected Completion Date June 2033. | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Bushbury | 372.3 | 75 | 372.3 | 3 | 480 | 2024-06-03 | 2024-06-18 | Yes | 547.9 | BESS subject to Project Progression/Modification Application | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2032. | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Bustleholm | 142.1 | 40.6 | 142.1 | 3 | 480 | 2024-06-03 | 2024-06-18 | Yes | 49.9 | N/A | Wider transmission reinforcement works. Expected Completion Date June 2033. | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Feckenham | 779.551 | 211.8 | 779.551 | 1.59 | 300 | 2024-06-03 | 2024-06-18 | Yes | 429.2 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2033. | Yes | Yes | Yes | No | No | Yes | Yes
West Midlands | Kitwell | 327.1 | 219.7 | 327.1 | 3 | 480 | 2024-06-03 | 2024-06-18 | Yes | 518.9 | N/A | Attributable and Wider transmission reinforcement works. Expected Completion Date October 2033. | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Nechells East | 226.4 | 0 | 302.8 | 5.463 | 480 | 2024-06-03 | 2024-06-18 | Yes | 72.6 | BESS subject to Project Progression/Modification Application | N/A | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Penn | 453.45 | 199.9 | 453.45 | 3.256 | 480 | 2024-06-03 | 2024-06-18 | Yes | 779.7 | N/A | SGT replacement works and Wider transmission reinforecement works. Expected Completion Date October 2033. | Yes | Yes | No | No | No | Yes | Yes
West Midlands | Port Ham | 1279.425 | 464 | 1314.425 | 2.83 | 480 | 2024-06-03 | 2024-06-18 | Yes | 515.5 | BESS subject to Project Progression/Modification Application | Attributable and Wider transmission reinforcement works. Expected Completion Date November 2033. | Yes | Yes | Yes | No | No | Yes | Yes
West Midlands | Willenhall | 87.85 | 49.9 | 87.85 | 3.601 | 240 | 2024-06-03 | 2024-06-18 | Yes | 199.8 | BESS subject to Project Progression/Modification Application | New GSP Proposed. Expected Completion Date October 2034. | Yes | Yes | No | No | No | Yes | Yes
South Wales | Cardiff East | 153.35 | 49.9 | 153.35 | 3.2 | 240 | 2023-12-18 | 2024-06-18 | Yes | 63 | N/A | Wider transmission reinforecement works. Expected Completion Date October 2028. | Yes | Yes | No | No | No | Yes | Yes
South Wales | Grange | 123.9 | 0 | 123.9 | 2.674 | 180 | 2023-12-18 | 2024-06-18 | Yes | 19 | N/A | N/A | Yes | Yes | No | No | No | Yes | Yes
South Wales | Pyle | 532.934 | 130.7 | 532.934 | 3 | 180 | 2023-12-18 | 2024-06-18 | Yes | 125 | N/A | Wider transmission reinforecement works. Expected Completion Date October 2028. | Yes | Yes | Yes | No | No | Yes | Yes
South Wales | Rassau | 505.987 | 76.6 | 505.987 | 2.5 | 240 | 2024-01-08 | 2024-06-18 | Yes | 255.9 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | Yes | No | No | Yes | Yes
South Wales | Upper Boat 33 | 214.7876 | 0 | 214.7876 | 2.791 | 100 | 2023-12-18 | 2024-06-18 | No | N/A | N/A | N/A | Yes | Yes | Yes | No | No | Yes | Yes
South Wales | Upper Boat 132 | 382.571 | 107.5 | 382.571 | N/A | 240 | 2023-12-18 | 2024-06-18 | Yes | 387.94 | N/A | Wider transmission reinforecement works. Expected Completion Date October 2033. | Yes | Yes | No | No | No | Yes | Yes
South West | Abham | 363.3 | 185.5 | 363.3 | 3 | 240 | 2024-05-29 | 2024-06-18 | Yes | 499.9 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | Yes | Yes | Yes | Yes | Yes
South West | Alverdiscott | 813.9964 | 464.8 | 813.9964 | 1.21 | 240 | 2024-05-29 | 2024-06-18 | Yes | 463.4 | BESS subject to Project Progression/Modification Application | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | Yes | Yes | Yes | Yes | Yes
South West | Axminster | 165.1 | 98.5 | 165.1 | 2.42 | N/A | 2024-05-29 | 2024-06-18 | Yes | 99.9 | BESS subject to Project Progression/Modification Application | New GSP Proposed. Expected Completion Date December 2036. | Yes | Yes | No | Yes | Yes | No | No
South West | Bridgwater | 430.4612 | 289.1 | 430.4612 | 3 | 240 | 2024-05-29 | 2024-06-18 | Yes | 296.4 | N/A | Attributable and wider transmission reinforecement works. Expected Completion Date May 2037. | Yes | Yes | Yes | Yes | Yes | Yes | Yes
South West | Exeter | 704.8402 | 493.98 | 704.8402 | 3 | 240 | 2024-05-29 | 2024-06-18 | Yes | 150.7 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | Yes | Yes | Yes | Yes | Yes
South West | Indian Queens | 1096.6272 | 591.3 | 1096.6272 | 0.99 | 480 | 2024-05-29 | 2024-06-18 | Yes | 643 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | Yes | Yes | Yes | Yes | Yes
South West | Landulph | 421.8 | 207.8 | 421.8 | 3 | 240 | 2024-05-29 | 2024-06-18 | Yes | 209.9 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | No | Yes | Yes | Yes | Yes
South West | Sandford | 308.524 | 157.1 | 308.524 | 3 | 240 | 2024-05-29 | 2024-06-18 | Yes | 655.2 | N/A | Wider transmission reinforecement works. Expected Completion Date December 2036. | Yes | Yes | No | No | No | Yes | Yes
South West | Taunton | 284.0001 | 165.5 | 284.001 | 3 | 240 | 2024-05-29 | 2024-06-18 | Yes | 79.8 | N/A | Attributable and wider transmission reinforecement works. Expected Completion Date May 2037. | Yes | Yes | Yes | Yes | Yes | Yes | Yes
[13 empty] | In order to allow NGED to contain voltage within acceptable limits at the National Electricity Transmission System (NETS)/ Distribution System interface, the Customer must ensure that the generators (≥1MW) have the capability to operate between 0.95 leading and 0.95 lagging power factor. Customers will be advised of the target Power Factor within this range. | National Grid Electricity Transmission (NGET) has instructed that NGED shall maintain a facility such that under emergency conditions on the National Electricity Transmission System (NETS), NGED shall have the ability to de-energise embedded generation (≥1MW) upon instruction from NGET. | The Customer’s generation will be included in the SGT Active Network Management Scheme (ANM) .The SGT ANM will automatically curtail the output of the Customer’s generation in order to control power flow in reverse direction through the Supergrid Transformers (SGTs) at this Grid Supply Point | The Customer’s generation will be included in the South West Operational Tripping Scheme (the SWOTS) required by National Grid Electricity Transmission (NGET). The SWOTS will automatically constrain the Customer’s generation output to zero during N-3 outage conditions on the National Electricity Transmission System (NETS). | The Customer’s generation will be included in Connect & Manage arrangement to address transmission system constraints in the South West through NGET having better management, visibility and control of Distributed Energy Resources (DER). | The Customer's connection will be required to provide visibility of the actions and/or output of the DER and a means to satisfy coordinated control between NGED ESO and NGET, such that NGED can discharge its obligations to develop, maintain, and operate an efficient, coordinated and economical system for the distribution of electricity. | The Customer's connection can participate in Technical Limit scheme, which allows for earlier energissation of connections on an interim basis, subject to 'Technical Limit' curtailment ('Interim Network Access Rights'), ahead of the completion of enabling transmission reinforcement works.